## DBH-Upgrade
Selectiontool DBH-upgrade
|  |  |  | Taal/Language/Sprache/Langue/Språk/Lengua/Jazyk |  |  |  | Nederlands
|  |  |  | Statisch toestel |  |  |  | Tempo
|  |  |  | Uitvoering [centimeter] |  |  |  | 70 | 80 | 15 | 16.5
[8 empty] | Hoogte | Lengte | Type | Diepte
|  |  |  | DBH set |  |  |  |  | 80 |  | 15
[8 empty] | Lengte | Lengte [cm] |  | Unit
Temperaturen
Verwarmen: |  |  |  |  | Koelen:
Water aanvoer | 0 | 0 | 35 | °C | Water aanvoer | 0 | 0 | 17 | °C | Eenheidsstelsel
Water retour | 0 | 0 | 18.3333 | °C | Water retour | 0 | 0 | 21 | °C
Ruimte (droge bol) | 0 | 0 | 15 | °C | Ruimte (droge bol) | 0 | 0 | 27 | °C
[5 empty] | rel. vocht. |  |  | 50%
Ventilatorsnelheid | Stuurspanning [v] | Verwarmvermogen [W] | Waterdebiet [kg/h] | Waterzijdig drukverlies [kPa] | Koelvermogen [W]** | Waterdebiet [kg/h] | Waterzijdig drukverlies [kPa] | Geluidsdrukniveau [dB(A)]**** | Geluidsvermogen [dB(A)]**** | Elektrisch verbruik [W] | Watervolume [l]
Tempo Hybrid, Lengte 80cm, Hoogte 70cm, Type 15 + DBH set, Unit 15 Lengte 80cm. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0* | 0 | 102 | 5 | 0.00015609 |  |  |  | 0 | 0 | 0 | 0.8
1 | 11.8 | 228 | 12 | 0.00084598 | 149 | 32 | 0.0056883 | 26 | 34 | 6 | 0.8
2 | 13.7 | 244 | 13 | 0.00098787 | 160 | 34 | 0.0064018 | 30 | 38 | 6.7 | 0.8
3 | 21.85 | 328 | 17 | 0.0016621 | 215 | 46 | 0.011547 | 42.4 | 50.4 | 9 | 0.8
v2021-04-26
* | Indien de ventilatoren uitgeschakeld zijn, is de afgifte een indicatieve waarde.
** | Koelvermogen is berekend volgens EN16430 met de ventilatoren naar boven blazend voor alle types.
*** | Wanneer het watervolume in gallons wordt gegeven, zijn dit imperial gallons.
**** | Geluidsvermogen volgens ISO 3741:2010, Voor het geluidsdrukniveau is er een aangenomen kamerdemping van 8 dB(A).
SI-eenheden
Imperiale-eenheden
Kopieer alle data
DBH

## data (hidden)
[12 empty] | heating | Ti |  |  |  | 35 | 35 | [17 empty] | cooling | Ti |  |  |  | RH |  |  | 17 | 17 | RH | 50% | [16 empty] | DBH-unit is te lang! | [6 empty] | DBH rail | GEEN | 10 | 15 |  |  | Imperial/SI |  | toestel | taal | lengte | hoogte | type |  | Built_in Hybrid |  |  | Strada Hybrid |  |  | Linea Hybrid |  |  | Tempo Hybrid |  |  | DBH-upgrade
[13 empty] | Tr |  |  |  | 18.3333 | 18.3333 | [18 empty] | Tr | [6 empty] | 21 | 21 | [18 empty] | Een DBH-unit kan niet geplaatst worden op een Tempo hoogte 20, type 11. | Een DBH-unit kan niet geplaatst worden op een Tempo hoogte 20, type 16. | Een DBH-unit kan niet geplaatst worden op een Tempo hoogte 20, type 21. |  |  |  |  | 1 | 15 | 15 |  |  |  | 1 |  | Geselecteerd | [5 empty] | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type
Tempo_L | [12 empty] | Ta |  |  |  | 15 | 15 | [18 empty] | Ta | [6 empty] | 27 | 27 | [31 empty] | 1 | Strada | Strada Hybrid | Nederlands | 50 | 0 | 10 |  | 20 | 60 | 10 | 35 | 50 | 10 | 20 | 50 | 10 | 20 | 50 | 10 |  | 50 | 10
kolomindex | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 |  | Linea | Linea Hybrid | English | 60 | 0 | 11 |  | 30 | 70 | 11 | 50 | 60 | 11 | 35 | 60 | 11 | 30 | 60 | 11 |  | 60 | 11
370801515 | 80 | 15 | 3 | 70 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1262.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 102 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 | 0 | 1578 | 0 | 0.8 | 0 | 0 | 0 | 11.8 | 13.7 | 21.85 | 0 | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 | 0 | 0 | 0 | 0 | 1 |  | Tempo | Tempo Hybrid | Français | 70 | 0 | 15 |  | 40 | 80 | 15 | 65 | 70 | 15 | 50 | 70 | 15 | 40 | 70 | 15 |  | 70 | 15
8015 | [77 empty] | Built_in | Built_in Hybrid | Deutsch | 80 | 0 | 16 |  | 50 | 90 | 16 | 95 | 80 | 16 | 65 | 80 | 16 | 50 | 80 | 16 |  | 80 | 16
[78 empty] | 3 |  | Norsk | 90 |  | 20 |  | 60 | 100 | 20 |  | 90 | 20 | 95 | 90 | 20 | 60 | 90 | 20 |  | 90 | 20
[8 empty] | soundpressure level |  |  |  | power | 75/65/20 |  |  | n |  |  |  | result | power |  |  | result | flow |  |  | static pressure loss | [7 empty] | power | 16/18/27 |  | n |  |  | result | power |  | result | flow |  | static pressure loss |  |  |  | electrical power nominal |  |  |  | oude cataloog |  | Statisch met rail / statisch cataloog |  |  |  |  | BMS-stuurspanning |  |  | Sensible heat factor |  |  | Total cooling capacity |  |  |  | Diff. Total and sensible |  |  | Show or not |  |  |  | Español | 100 |  | 21 |  | 70 | 110 | 21 |  | 100 | 21 |  | 100 | 21 | 70 | 100 | 21 |  | 100 | 21
lookup code | L,rail | T,rail | toestel | height | length | type | depth | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | k1 | n | t | k2 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | watervolume | 1 | 2 | 3 |  | Static,H | Static,C |  |  |  | 0 | 1 | 2 | 3 |  | SHF 1 | SHF 2 | SHF 3 | Q,t 1 | Q,t 2 | Q,t 3 |  | ΔQ,t,s 1 | ΔQ,t,s 2 | ΔQ,t,s 3 | OK/NOTOK |  | W/m,beript dyn heat |  | Svenska | 110 |  |  |  | 90 | 120 |  |  | 110 |  |  | 110 |  | 90 | 110 |  |  | 110
13550100 |  | 0 | 1 | 35 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 449 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 449 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  | W/m,beript dyn cool | Čeština | 120 |  |  |  |  | 140 |  |  | 120 |  |  | 120 |  |  | 120 |  |  | 120
13550110 |  | 0 | 1 | 35 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 598 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  | ExtraTaal1 | 140 |  |  |  |  | 160 |  |  | 140 |  |  | 140 |  |  | 140 |  |  | 140
13560100 |  | 0 | 1 | 35 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 539 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 539 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  | OFF |  | ExtraTaal2 | 160 |  |  |  |  | 180 |  |  | 160 |  |  | 160 |  |  | 160 |  |  | 160
13560110 |  | 0 | 1 | 35 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 64 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 718 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  | 26dB(A) |  | ExtraTaal3 | 180 |  | Kopieer alle data |  |  | 200 |  |  | 180 |  |  | 180 |  |  | 180 |  |  | 180
13560150 |  | 0 | 1 | 35 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 882 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 882 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  | 30dB(A) |  |  | 200 |  | SI-eenheden |  |  | 220 |  |  | 200 |  |  | 200 |  |  | 200 |  |  | 200
13560160 |  | 0 | 1 | 35 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 956 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 956 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  | MAX |  |  | 220 |  | Imperiale-eenheden |  |  | 240 |  |  | 220 |  |  | 220 |  |  | 220 |  |  | 220
13560200 |  | 0 | 1 | 35 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1236 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1236 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  |  | 240 |  |  |  |  | 260 |  |  | 240 |  |  | 240 |  |  | 240 |  |  | 240
13560210 |  | 0 | 1 | 35 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1268 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1268 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  |  | 260 |  |  |  |  | 280 |  |  | 260 |  |  | 260 |  |  | 260 |  |  | 260
13570100 |  | 0 | 1 | 35 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 629 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 629 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  | 1 | 280 | [7 empty] | 280 |  |  | 280 |  |  | 280 |  |  | 280
13570110 |  | 0 | 1 | 35 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 75 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 837 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  |  | 300 | [13 empty] | 300 |  |  | 300
13570150 |  | 0 | 1 | 35 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1029 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00014954 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1029 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 |  |  |  |  | 0 | 0 | [8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
13570160 |  | 0 | 1 | 35 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00041403 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1115 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | [5 empty] | 0 | [11 empty] | 11.8 | 13.7 | 21.85 | 6 | 6.7 | 9
13570200 |  | 0 | 1 | 35 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1442 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00022051 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1442 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | [5 empty] | 0 | [9 empty] | Raillengte | Railtype | BMS-stuurspanningen |  |  | Opgenomen elektrisch vermogen
13570210 |  | 0 | 1 | 35 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1480 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024224 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1480 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | H |  |  | C | [10 empty] | 5010 | 50 | 10 | 14.2 | 16.2 | 21.85 | 3.6 | 4.1 | 5.1
13580100 |  | 0 | 1 | 35 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 718 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 5015 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0
13580110 |  | 0 | 1 | 35 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 957 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 957 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 6010 | 60 | 10 | 13.6 | 15.6 | 21.85 | 4.8 | 5.4 | 6.8
13580150 |  | 0 | 1 | 35 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1176 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00022173 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1176 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 6015 | 60 | 15 | 12.3 | 14.4 | 21.85 | 4.8 | 5.5 | 7.2
13580160 |  | 0 | 1 | 35 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1274 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00060898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1274 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 7010 | 70 | 10 | 13.2 | 15.1 | 21.85 | 5.5 | 5.9 | 7.9
13580200 |  | 0 | 1 | 35 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1648 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0002951 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1648 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 7015 | 70 | 15 | 12.3 | 14.4 | 21.85 | 5.1 | 5.6 | 7.2
13580210 |  | 0 | 1 | 35 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1691 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034051 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1691 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 8010 | 80 | 10 | 12.8 | 14.7 | 21.85 | 6.3 | 6.8 | 9.1
13590100 |  | 0 | 1 | 35 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 808 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 808 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 8015 | 80 | 15 | 11.8 | 13.7 | 21.85 | 6 | 6.7 | 9
13590110 |  | 0 | 1 | 35 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00033253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1076 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 9010 | 90 | 10 | 12.5 | 14.7 | 21.85 | 6.7 | 7.4 | 10.3
13590150 |  | 0 | 1 | 35 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1323 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031016 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1323 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 9015 | 90 | 15 | 11.3 | 13.2 | 21.85 | 7 | 7.7 | 10.7
13590160 |  | 0 | 1 | 35 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1434 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00062691 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1434 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 10010 | 100 | 10 | 12.3 | 14.1 | 21.85 | 7.8 | 8.7 | 12.2
13590200 |  | 0 | 1 | 35 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1854 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00038208 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1854 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 10015 | 100 | 15 | 10.9 | 12.8 | 21.85 | 7 | 7.7 | 10.7
13590210 |  | 0 | 1 | 35 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1903 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 161 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00045824 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1903 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 11010 | 110 | 10 | 12 | 13.9 | 21.85 | 8.4 | 9.3 | 14
135100100 |  | 0 | 1 | 35 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 898 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 11015 | 110 | 15 | 10.9 | 12.8 | 21.85 | 7.9 | 8.8 | 12.5
135100110 |  | 0 | 1 | 35 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1196 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00050061 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1196 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 12010 | 120 | 10 | 11.8 | 13.7 | 21.85 | 8.9 | 9.9 | 14.8
135100150 |  | 0 | 1 | 35 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1470 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00032186 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1470 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 12015 | 120 | 15 | 10.6 | 12.5 | 21.85 | 8.7 | 9.8 | 14.3
135100160 |  | 0 | 1 | 35 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1593 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00086899 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1593 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 14010 | 140 | 10 | 11.5 | 13.3 | 21.85 | 10.1 | 11.2 | 17.5
135100200 |  | 0 | 1 | 35 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2060 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00048192 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2060 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 14015 | 140 | 15 | 10.4 | 12.2 | 21.85 | 9.6 | 10.5 | 16.1
135100210 |  | 0 | 1 | 35 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2114 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00059642 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2114 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 16010 | 160 | 10 | 11.2 | 13 | 21.85 | 11 | 12.4 | 19.2
135110100 |  | 0 | 1 | 35 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 988 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 988 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 16015 | 160 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6
135110110 |  | 0 | 1 | 35 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1316 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00053543 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1316 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 18010 | 180 | 10 | 10.9 | 12.7 | 21.85 | 12.2 | 13.7 | 22
135110150 |  | 0 | 1 | 35 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1617 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00043037 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1617 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 18015 | 180 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6
135110160 |  | 0 | 1 | 35 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1752 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.001155 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 1752 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 20010 | 200 | 10 | 10.7 | 12.5 | 21.85 | 13.4 | 14.8 | 24
135110200 |  | 0 | 1 | 35 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2266 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00059509 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2266 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 20015 | 200 | 15 | 10 | 11.4 | 21.85 | 13.2 | 14.7 | 23.5
135110210 |  | 0 | 1 | 35 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2325 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 197 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00075597 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2325 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 22010 | 220 | 10 | 10.5 | 12.3 | 21.85 | 13.4 | 14.8 | 24
135120100 |  | 0 | 1 | 35 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1078 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 22015 | 220 | 15 | 10 | 11.1 | 21.85 | 15.5 | 16.8 | 27.5
135120110 |  | 0 | 1 | 35 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1435 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.0007561 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1435 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 24010 | 240 | 10 | 10.4 | 12.2 | 21.85 | 14.8 | 16.6 | 28
135120150 |  | 0 | 1 | 35 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1764 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055702 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1764 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 24015 | 240 | 15 | 10 | 10.9 | 21.85 | 16.4 | 17.7 | 29.7
135120160 |  | 0 | 1 | 35 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1912 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 165 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014865 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1912 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 26010 | 260 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4
135120200 |  | 0 | 1 | 35 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2472 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 240 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00072203 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2472 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 26015 | 260 | 15 | 10 | 10.9 | 21.85 | 16.2 | 18.6 | 31.4
135120210 |  | 0 | 1 | 35 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2537 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 214 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00093782 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2537 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 28010 | 280 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4
135140100 |  | 0 | 1 | 35 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1257 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1257 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 28015 | 280 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5
135140110 |  | 0 | 1 | 35 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1674 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1674 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 30010 | 300 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4
135140150 |  | 0 | 1 | 35 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2058 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0007242 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2058 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 30015 | 300 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5
135140160 |  | 0 | 1 | 35 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2230 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 193 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0019081 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2230 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135140200 |  | 0 | 1 | 35 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2884 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 280 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0010189 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2884 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135140210 |  | 0 | 1 | 35 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2960 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 250 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0013719 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 2960 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135160100 |  | 0 | 1 | 35 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1437 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 137 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00050754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1437 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | L,rail/L,tot | T10 | T11 | T15 | T16 | T20 | T21 | ALS
135160110 |  | 0 | 1 | 35 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1914 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00148 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1914 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 90% | 68% | 80% | 68% | 80% | 80% | 90% | T10
135160150 |  | 0 | 1 | 35 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2352 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010829 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2352 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 0.8 | 92% | 74.4% | 84% | 74.4% | 84% | 84% | 68% | T11
135160160 |  | 0 | 1 | 35 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2549 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0023937 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2549 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 0.6 | 94% | 80.8% | 88% | 80.8% | 88% | 88% | 80% | T15
135160200 |  | 0 | 1 | 35 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3296 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 320 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0015452 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3296 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 0.4 | 96% | 87.2% | 92% | 87.2% | 92% | 92% | 68% | T16
135160210 |  | 0 | 1 | 35 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3382 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 286 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0019054 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 3382 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 0.2 | 98% | 93.6% | 96% | 93.6% | 96% | 96% | 80% | T20
135180100 |  | 0 | 1 | 35 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1616 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00070519 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1616 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 100% | 100% | 100% | 100% | 100% | 100% | 80% | T21
135180110 |  | 0 | 1 | 35 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2153 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0019612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2153 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135180150 |  | 0 | 1 | 35 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2646 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 257 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0013278 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2646 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135180160 |  | 0 | 1 | 35 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2867 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 248 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0034326 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 2867 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135180200 |  | 0 | 1 | 35 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3708 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 360 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0019916 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3708 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | Lengths | Calculation factors for lower fan settings
135180210 |  | 0 | 1 | 35 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3805 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 322 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.002545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3805 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [11 empty] | T10 |  | T11 |  | T15 |  | T16 |  | T20 |  | T21
135200100 |  | 0 | 1 | 35 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1796 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00094435 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1796 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [11 empty] | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1
135200110 |  | 0 | 1 | 35 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2392 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2392 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 50 | 0.85519 | 0.79918 | 0.85519 | 0.79918
135200150 |  | 0 | 1 | 35 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2940 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 285 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0018258 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2940 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 60 | 0.84525 | 0.7893 | 0.84525 | 0.7893 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.84525 | 0.7893 | 0.75556 | 0.70384
135200160 |  | 0 | 1 | 35 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3186 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 276 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.004109 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3186 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 70 | 0.8364 | 0.77994 | 0.8364 | 0.77994 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.8364 | 0.77994 | 0.75556 | 0.70384
135200200 |  | 0 | 1 | 35 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4120 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 400 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0025055 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4120 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 80 | 0.82846 | 0.77134 | 0.82846 | 0.77134 | 0.74531 | 0.69504 | 0.74531 | 0.69504 | 0.82846 | 0.77134 | 0.74531 | 0.69504
135200210 |  | 0 | 1 | 35 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4228 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 357 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0029791 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 4228 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 90 | 0.82124 | 0.76344 | 0.82124 | 0.76344 | 0.7343 | 0.6854 | 0.7343 | 0.6854 | 0.82124 | 0.76344 | 0.7343 | 0.6854
135220100 |  | 0 | 1 | 35 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1842.6812 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 176 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0010147 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1842.6812 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 100 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746
135220110 |  | 0 | 1 | 35 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2454.058 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0027293 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2454.058 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 110 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746
135220150 |  | 0 | 1 | 35 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3016.6957 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 293 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0019128 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3016.6957 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 120 | 0.80301 | 0.7433 | 0.80301 | 0.7433 | 0.71879 | 0.67123 | 0.71879 | 0.67123 | 0.80301 | 0.7433 | 0.71879 | 0.67123
135220160 |  | 0 | 1 | 35 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3268.942 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 283 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.00486 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 3268.942 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 140 | 0.79292 | 0.73212 | 0.79292 | 0.73212 | 0.71271 | 0.66551 | 0.71271 | 0.66551 | 0.79292 | 0.73212 | 0.71271 | 0.66551
135220200 |  | 0 | 1 | 35 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4227.4783 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 410 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0026001 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4227.4783 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 160 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707
135220210 |  | 0 | 1 | 35 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4338.6377 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 367 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0034561 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 4338.6377 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 180 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707
135240100 |  | 0 | 1 | 35 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2155 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 206 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0015594 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2155 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 200 | 0.76886 | 0.70539 | 0.76886 | 0.70539 | 0.69292 | 0.65762 | 0.69292 | 0.65762 | 0.76886 | 0.70539 | 0.69292 | 0.65762
135240110 |  | 0 | 1 | 35 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2870 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0039541 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2870 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 220 | 0.75856 | 0.69426 | 0.75856 | 0.69426 | 0.68521 | 0.65781 | 0.68521 | 0.65781 | 0.75856 | 0.69426 | 0.68521 | 0.65781
135240150 |  | 0 | 1 | 35 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3528 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 342 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0028103 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3528 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 240 | 0.75028 | 0.68489 | 0.75028 | 0.68489 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75028 | 0.68489 | 0.6819 | 0.65797
135240160 |  | 0 | 1 | 35 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3823 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 331 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0063803 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3823 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 260 | 0.75 | 0.68 | 0.75 | 0.68 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75 | 0.68 | 0.6819 | 0.65797
135240200 |  | 0 | 1 | 35 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4944 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 480 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0037474 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4944 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 280 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821
135240210 |  | 0 | 1 | 35 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5074 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 429 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.004751 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 5074 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 300 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821
135260100 |  | 0 | 1 | 35 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2231.5281 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.001659 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2231.5281 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135260110 |  | 0 | 1 | 35 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2972.7079 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 265 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0048207 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 2972.7079 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | Type,ww | L/cm
135260150 |  | 0 | 1 | 35 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3653.5281 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 354 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0029295 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 3653.5281 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 10 | 0.0066667
135260160 |  | 0 | 1 | 35 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3958.8764 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 343 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0073485 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 3958.8764 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 11 | 0.013333
135260200 |  | 0 | 1 | 35 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5119.9101 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0041729 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 5119.9101 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 15 | 0.01
135260210 |  | 0 | 1 | 35 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5253.9438 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 444 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0053829 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 5253.9438 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 16 | 0.02
135280100 |  | 0 | 1 | 35 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2514 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 240 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002057 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2514 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 20 | 0.013333
135280110 |  | 0 | 1 | 35 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3349 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 299 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0057978 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3349 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 21 | 0.026667
135280150 |  | 0 | 1 | 35 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4116 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 399 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0040598 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4116 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
135280160 |  | 0 | 1 | 35 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4460 | 0 | 0 | 0 | 1.458 | 1.1 | 1.1 | 1.1 | 386 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0092545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 4460 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 2 | 3 | 4 | 5 | 6
135280200 |  | 0 | 1 | 35 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5768 | 0 | 0 | 0 | 1.39 | 1.08 | 1.08 | 1.08 | 559 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0052939 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5768 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | Niveaus | Type | k1 | n | t | k2
135280210 |  | 0 | 1 | 35 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5919 | 0 | 0 | 0 | 1.472 | 1.05 | 1.05 | 1.05 | 500 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0070356 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 5919 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15050100 |  | 0 | 1 | 50 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 538 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 538 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 row | [5 empty] | 1 | 2 | 3 | 4 | 5 |  | 50
15050110 |  | 0 | 1 | 50 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 693 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 693 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 4 | 0.0013823 | 1.7232 | 1 | 0.00033291 | 4 | 0.0013823 | 1.7232 | 1 | 0.00033291 |  | 60
15060100 |  | 0 | 1 | 50 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 646 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 646 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 2 | 5 | 0.000937 | 1.789 | 2 | 0.000446 | 5 | 0.000937 | 1.789 | 2 | 0.000446 |  | 70
15060110 |  | 0 | 1 | 50 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 832 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 | 6 | 0.000937 | 1.789 | 4 | 0.00139 | 6 | 0.000937 | 1.789 | 4 | 0.00139 |  | 80
15060150 |  | 0 | 1 | 50 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.000143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1040 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 2 rows | [5 empty] | 7 | 0.0025582 | 1.4943 | 3 | 0.00056162 |  | 90
15060160 |  | 0 | 1 | 50 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1139 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1139 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 9 | 0.00080534 | 1.8139 | 2 | 0.00039795 | 8 | 0.000937 | 1.789 | 4 | 0.00139 |  | 100
15060200 |  | 0 | 1 | 50 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 145 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00021338 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1455 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 2 | 10 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 9 | 0.00080534 | 1.8139 | 2 | 0.00039795 |  | 110
15060210 |  | 0 | 1 | 50 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1549 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031197 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1549 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 | 11 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 10 | 0.0003969 | 1.7346 | 2 | 0.00036735 |  | 120
15070100 |  | 0 | 1 | 50 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 753 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 3 rows | [5 empty] | 11 | 0.0003969 | 1.7346 | 4 | 0.00057429 |  | 140
15070110 |  | 0 | 1 | 50 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 970 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 14 | 0.0025582 | 1.4943 | 3 | 0.00056162 | 14 | 0.0025582 | 1.4943 | 3 | 0.00056162 |  | 150
15070150 |  | 0 | 1 | 50 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00021277 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1214 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 2 | 15 | 0.0002083 | 1.724 | 2 | 0.00046183 | 15 | 0.0002083 | 1.724 | 2 | 0.00046183 |  | 160
15070160 |  | 0 | 1 | 50 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1329 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00059105 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1329 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 | 16 | 0.0002083 | 1.724 | 4 | 0.0013928 | 16 | 0.0002083 | 1.724 | 4 | 0.0013928 |  | 180
15070200 |  | 0 | 1 | 50 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1698 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00036009 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1698 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 rows | [5 empty] | 19 | 0.011616 | 1.5869 | 1 | 0.0016553 |  | 200
15070210 |  | 0 | 1 | 50 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1807 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00042233 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1807 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 19 | 0.011616 | 1.5869 | 1 | 0.0016553 | 20 | 0.0001276 | 1.7219 | 2 | 0.00037661 |  | 220
15080100 |  | 0 | 1 | 50 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 861 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 861 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 2 | 20 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 21 | 0.0001276 | 1.7219 | 4 | 0.0005142 |  | 240
15080110 |  | 0 | 1 | 50 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00030716 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1109 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 | 21 | 0.0001276 | 1.7219 | 4 | 0.0005142 | [6 empty] | 260
15080150 |  | 0 | 1 | 50 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1387 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00029847 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1387 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [22 empty] | 280
15080160 |  | 0 | 1 | 50 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1518 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00082222 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1518 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 1 | 7 | 0.0025582 | 1.4943 | 3 | 0.00056162 | [6 empty] | 300
15080200 |  | 0 | 1 | 50 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1940 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00045556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1940 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 4 | 8 | 0.000937 | 1.789 | 4 | 0.00139 | [6 empty] | 350
15080210 |  | 0 | 1 | 50 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2066 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2066 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [22 empty] | 490
15090100 |  | 0 | 1 | 50 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 968 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 968 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15090110 |  | 0 | 1 | 50 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1247 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0004658 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1247 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15090150 |  | 0 | 1 | 50 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1561 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1561 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15090160 |  | 0 | 1 | 50 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1708 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010961 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1708 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15090200 |  | 0 | 1 | 50 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2183 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 218 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00056402 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2183 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15090210 |  | 0 | 1 | 50 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2324 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00070324 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2324 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150100100 |  | 0 | 1 | 50 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1076 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150100110 |  | 0 | 1 | 50 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1386 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00050061 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1386 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150100150 |  | 0 | 1 | 50 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1734 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00052096 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1734 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [9 empty] | Δp [kPa] | 0.087303 | 21 | 0.0001276 | 1.7219 | 4 | 0.0005142
150100160 |  | 0 | 1 | 50 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1898 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011255 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1898 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [9 empty] | mass flow | 100
150100200 |  | 0 | 1 | 50 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2425 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 242 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00068594 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2425 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [9 empty] | Length | 280
150100210 |  | 0 | 1 | 50 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2582 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 214 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00087568 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [9 empty] | Type | 21
150110100 |  | 0 | 1 | 50 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1184 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150110110 |  | 0 | 1 | 50 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1525 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 136 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00071062 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1525 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150110150 |  | 0 | 1 | 50 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1907 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00065932 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1907 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150110160 |  | 0 | 1 | 50 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2088 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014504 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2088 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150110200 |  | 0 | 1 | 50 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2668 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 266 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.00094834 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2668 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150110210 |  | 0 | 1 | 50 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2840 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010707 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2840 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120100 |  | 0 | 1 | 50 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1291 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00041656 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1291 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120110 |  | 0 | 1 | 50 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1663 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00096572 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1663 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120150 |  | 0 | 1 | 50 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2081 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00081677 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2081 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120160 |  | 0 | 1 | 50 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2278 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0018216 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2278 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120200 |  | 0 | 1 | 50 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2910 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 290 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0011102 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2910 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150120210 |  | 0 | 1 | 50 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3098 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.001289 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3098 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140100 |  | 0 | 1 | 50 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1506 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0005905 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140110 |  | 0 | 1 | 50 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1940 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013393 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1940 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140150 |  | 0 | 1 | 50 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2428 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 242 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010236 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2428 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140160 |  | 0 | 1 | 50 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2657 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0027093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2657 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140200 |  | 0 | 1 | 50 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3395 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0014795 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3395 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150140210 |  | 0 | 1 | 50 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3615 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 299 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0017995 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3615 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160100 |  | 0 | 1 | 50 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1722 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 168 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00080367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1722 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160110 |  | 0 | 1 | 50 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2218 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 198 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017923 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2218 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160150 |  | 0 | 1 | 50 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2774 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0014495 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2774 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160160 |  | 0 | 1 | 50 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3037 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0032966 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3037 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160200 |  | 0 | 1 | 50 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3880 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 387 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0021095 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3880 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150160210 |  | 0 | 1 | 50 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4131 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 342 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0026889 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4131 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180100 |  | 0 | 1 | 50 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1937 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0010592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1937 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180110 |  | 0 | 1 | 50 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2495 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 223 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002729 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2495 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180150 |  | 0 | 1 | 50 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3121 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 311 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0019638 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180160 |  | 0 | 1 | 50 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3416 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 293 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.004512 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3416 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180200 |  | 0 | 1 | 50 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4365 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 436 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0026349 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4365 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150180210 |  | 0 | 1 | 50 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4648 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 384 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0034559 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4648 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200100 |  | 0 | 1 | 50 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2152 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0013601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2152 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200110 |  | 0 | 1 | 50 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2772 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 248 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0034217 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2772 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200150 |  | 0 | 1 | 50 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3468 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.002572 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3468 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200160 |  | 0 | 1 | 50 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3796 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 325 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0059484 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3796 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200200 |  | 0 | 1 | 50 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4850 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 484 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.003492 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4850 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150200210 |  | 0 | 1 | 50 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5164 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 427 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0043411 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 5164 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220100 |  | 0 | 1 | 50 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2207.7971 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 216 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0014597 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2207.7971 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220110 |  | 0 | 1 | 50 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2843.971 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 255 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0036879 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2843.971 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220150 |  | 0 | 1 | 50 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3558.8116 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 355 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0026912 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3558.8116 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220160 |  | 0 | 1 | 50 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3894.8551 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 334 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0061644 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 3894.8551 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220200 |  | 0 | 1 | 50 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4976.5217 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0038996 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4976.5217 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150220210 |  | 0 | 1 | 50 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5298.8841 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 438 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0049404 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 5298.8841 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240100 |  | 0 | 1 | 50 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2582 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 253 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0021099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240110 |  | 0 | 1 | 50 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3326 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 298 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0051154 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3326 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240150 |  | 0 | 1 | 50 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4162 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 415 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.003749 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4162 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240160 |  | 0 | 1 | 50 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4555 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 390 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.008683 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4555 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240200 |  | 0 | 1 | 50 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5820 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 581 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0052937 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 5820 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150240210 |  | 0 | 1 | 50 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6197 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 513 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0064891 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 6197 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260100 |  | 0 | 1 | 50 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2674.4607 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 262 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0025644 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2674.4607 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260110 |  | 0 | 1 | 50 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3444.9326 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 308 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0061274 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3444.9326 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260150 |  | 0 | 1 | 50 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4309.4944 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 430 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0042584 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4309.4944 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260160 |  | 0 | 1 | 50 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4716.9213 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 404 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0098363 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 4716.9213 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260200 |  | 0 | 1 | 50 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6027.0787 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 602 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0058183 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 6027.0787 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150260210 |  | 0 | 1 | 50 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6417.6404 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 531 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0072548 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 6417.6404 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280100 |  | 0 | 1 | 50 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3013 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0030758 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3013 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280110 |  | 0 | 1 | 50 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3881 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 347 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0080406 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3881 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280150 |  | 0 | 1 | 50 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4855 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 485 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0056162 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4855 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280160 |  | 0 | 1 | 50 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5314 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 455 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.012049 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 5314 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280200 |  | 0 | 1 | 50 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6790 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 678 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.0075486 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 6790 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150280210 |  | 0 | 1 | 50 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7230 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 598 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0097556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 7230 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16550100 |  | 0 | 1 | 65 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 606 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16550110 |  | 0 | 1 | 65 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00015139 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 772 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560100 |  | 0 | 1 | 65 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 727 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.6886e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 727 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560110 |  | 0 | 1 | 65 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 926 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 926 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560150 |  | 0 | 1 | 65 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1153 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 119 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00020381 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1153 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560160 |  | 0 | 1 | 65 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1304 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057313 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1304 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560200 |  | 0 | 1 | 65 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1611 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00034909 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1611 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16560210 |  | 0 | 1 | 65 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1818 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1818 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570100 |  | 0 | 1 | 65 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 848 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570110 |  | 0 | 1 | 65 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00028178 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1080 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570150 |  | 0 | 1 | 65 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1345 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00028678 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1345 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570160 |  | 0 | 1 | 65 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1521 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 129 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00079884 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1521 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570200 |  | 0 | 1 | 65 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1880 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 193 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00044237 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1880 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16570210 |  | 0 | 1 | 65 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2121 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053044 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580100 |  | 0 | 1 | 65 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 969 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 969 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580110 |  | 0 | 1 | 65 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1234 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00043099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1234 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580150 |  | 0 | 1 | 65 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1538 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00038621 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1538 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580160 |  | 0 | 1 | 65 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1738 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010667 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1738 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580200 |  | 0 | 1 | 65 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2148 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00054849 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2148 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16580210 |  | 0 | 1 | 65 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2424 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 196 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00067687 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2424 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590100 |  | 0 | 1 | 65 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 109 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1090 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590110 |  | 0 | 1 | 65 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1389 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0004658 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1389 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590150 |  | 0 | 1 | 65 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1730 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 178 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00050293 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1730 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590160 |  | 0 | 1 | 65 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1956 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013783 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1956 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590200 |  | 0 | 1 | 65 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2417 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 249 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00078032 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2417 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16590210 |  | 0 | 1 | 65 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2727 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00084461 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2727 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100100 |  | 0 | 1 | 65 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1211 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100110 |  | 0 | 1 | 65 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1543 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00066513 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1543 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100150 |  | 0 | 1 | 65 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1922 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 198 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0006377 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1922 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100160 |  | 0 | 1 | 65 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2173 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2173 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100200 |  | 0 | 1 | 65 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2685 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 276 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.00092481 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2685 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165100210 |  | 0 | 1 | 65 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3030 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012062 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3030 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110100 |  | 0 | 1 | 65 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00039382 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1332 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110110 |  | 0 | 1 | 65 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1697 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00090838 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1697 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110150 |  | 0 | 1 | 65 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2114 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 217 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00079129 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2114 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110160 |  | 0 | 1 | 65 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2390 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017784 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2390 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110200 |  | 0 | 1 | 65 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2954 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 304 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0012279 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2954 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165110210 |  | 0 | 1 | 65 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3333 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 270 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0014376 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3333 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120100 |  | 0 | 1 | 65 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00053316 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1453 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120110 |  | 0 | 1 | 65 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1852 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1852 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120150 |  | 0 | 1 | 65 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2306 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 237 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00096443 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2306 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120160 |  | 0 | 1 | 65 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2608 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2608 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120200 |  | 0 | 1 | 65 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3222 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 331 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0014138 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3222 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165120210 |  | 0 | 1 | 65 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3636 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0016935 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3636 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140100 |  | 0 | 1 | 65 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1695 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 170 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00073333 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1695 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140110 |  | 0 | 1 | 65 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2160 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016234 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2160 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140150 |  | 0 | 1 | 65 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2691 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0013722 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2691 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140160 |  | 0 | 1 | 65 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3042 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 258 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0031606 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3042 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140200 |  | 0 | 1 | 65 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3759 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 387 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0020225 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3759 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165140210 |  | 0 | 1 | 65 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4242 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 344 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0025438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4242 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160100 |  | 0 | 1 | 65 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1938 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00097475 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1938 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160110 |  | 0 | 1 | 65 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2469 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021315 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2469 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160150 |  | 0 | 1 | 65 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3075 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 316 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0018666 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3075 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160160 |  | 0 | 1 | 65 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3477 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0043379 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3477 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160200 |  | 0 | 1 | 65 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4296 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 442 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0027579 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 4296 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165160210 |  | 0 | 1 | 65 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4848 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 393 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.003282 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4848 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180100 |  | 0 | 1 | 65 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2180 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 218 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0012605 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2180 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180110 |  | 0 | 1 | 65 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2777 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 249 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0031555 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2777 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180150 |  | 0 | 1 | 65 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3460 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 356 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0024529 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3460 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180160 |  | 0 | 1 | 65 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3911 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 332 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0057325 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3911 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180200 |  | 0 | 1 | 65 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4833 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0036264 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4833 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165180210 |  | 0 | 1 | 65 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5454 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 442 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0044979 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5454 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200100 |  | 0 | 1 | 65 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2422 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 243 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0018437 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2422 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200110 |  | 0 | 1 | 65 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3086 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0039125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3086 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200150 |  | 0 | 1 | 65 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3844 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 395 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0031362 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3844 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200160 |  | 0 | 1 | 65 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4346 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 369 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0073547 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4346 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200200 |  | 0 | 1 | 65 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5370 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 552 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0043342 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 5370 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165200210 |  | 0 | 1 | 65 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6060 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 491 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0055199 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 6060 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220100 |  | 0 | 1 | 65 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2484.8406 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 249 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0019768 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2484.8406 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220110 |  | 0 | 1 | 65 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3166.3333 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 284 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0047741 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3166.3333 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220150 |  | 0 | 1 | 65 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3944.4493 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 406 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0035936 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3944.4493 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220160 |  | 0 | 1 | 65 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4459.2029 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 378 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0083972 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4459.2029 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220200 |  | 0 | 1 | 65 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5510.087 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 567 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0047992 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 5510.087 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165220210 |  | 0 | 1 | 65 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6218.087 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 504 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0062158 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 6218.087 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240100 |  | 0 | 1 | 65 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2906 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 291 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0027345 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2906 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240110 |  | 0 | 1 | 65 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3703 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 332 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0064089 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3703 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240150 |  | 0 | 1 | 65 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4613 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 475 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0051964 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4613 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240160 |  | 0 | 1 | 65 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5215 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 442 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.011322 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5215 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240200 |  | 0 | 1 | 65 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6444 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 663 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0.0067128 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 6444 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165240210 |  | 0 | 1 | 65 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7272 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 589 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0084792 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 7272 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260100 |  | 0 | 1 | 65 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3009.9888 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 301 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0032649 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 3009.9888 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260110 |  | 0 | 1 | 65 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3834.6067 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 344 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0075725 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3834.6067 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260150 |  | 0 | 1 | 65 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4777.2809 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 491 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0054063 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4777.2809 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260160 |  | 0 | 1 | 65 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5400.4045 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 458 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.012667 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 5400.4045 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260200 |  | 0 | 1 | 65 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6673.2809 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 686 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.0073206 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 6673.2809 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165260210 |  | 0 | 1 | 65 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7530.7416 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 610 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0093856 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 7530.7416 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280100 |  | 0 | 1 | 65 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3391 | 0 | 0 | 0 | 1.371 | 1.08 | 1.08 | 1.08 | 340 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.004275 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3391 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280110 |  | 0 | 1 | 65 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4320 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 387 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.009715 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4320 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280150 |  | 0 | 1 | 65 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5382 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 554 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0074067 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 5382 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280160 |  | 0 | 1 | 65 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6084 | 0 | 0 | 0 | 1.47 | 1.1 | 1.1 | 1.1 | 516 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.016317 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 6084 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280200 |  | 0 | 1 | 65 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7518 | 0 | 0 | 0 | 1.355 | 1.08 | 1.08 | 1.08 | 773 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0.0097152 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 7518 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
165280210 |  | 0 | 1 | 65 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8484 | 0 | 0 | 0 | 1.497 | 1.05 | 1.05 | 1.05 | 688 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.012886 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 8484 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560100 |  | 0 | 1 | 95 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00014785 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 836 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560110 |  | 0 | 1 | 95 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00025641 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1078 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560150 |  | 0 | 1 | 95 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1288 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00027509 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1288 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560160 |  | 0 | 1 | 95 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1606 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00077545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1606 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560200 |  | 0 | 1 | 95 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1795 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 196 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00042919 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1795 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19560210 |  | 0 | 1 | 95 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2352 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 183 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00050845 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2352 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570100 |  | 0 | 1 | 95 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016054 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 975 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570110 |  | 0 | 1 | 95 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1257 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 113 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00039617 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1257 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570150 |  | 0 | 1 | 95 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1502 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 164 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0003715 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1502 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570160 |  | 0 | 1 | 95 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1874 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010372 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1874 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570200 |  | 0 | 1 | 95 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2094 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0006318 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 2094 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19570210 |  | 0 | 1 | 95 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2744 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00078248 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2744 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580100 |  | 0 | 1 | 95 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1114 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024379 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 1114 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580110 |  | 0 | 1 | 95 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1437 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 129 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00057416 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1437 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580150 |  | 0 | 1 | 95 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1717 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 187 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00059445 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1717 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580160 |  | 0 | 1 | 95 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2142 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 178 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013422 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2142 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580200 |  | 0 | 1 | 95 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2394 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 261 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00075961 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2394 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19580210 |  | 0 | 1 | 95 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3136 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 244 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0011234 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3136 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590100 |  | 0 | 1 | 95 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1254 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034834 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1254 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590110 |  | 0 | 1 | 95 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1616 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00079369 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1616 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590150 |  | 0 | 1 | 95 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1931 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 211 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00074031 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1931 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590160 |  | 0 | 1 | 95 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2409 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016919 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2409 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590200 |  | 0 | 1 | 95 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2693 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 294 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0010308 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2693 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
19590210 |  | 0 | 1 | 95 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3528 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 274 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0013435 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3528 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100100 |  | 0 | 1 | 95 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1393 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00047582 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1393 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100110 |  | 0 | 1 | 95 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1796 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 162 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00085103 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1796 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100150 |  | 0 | 1 | 95 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2146 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 234 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0009052 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 2146 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100160 |  | 0 | 1 | 95 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2677 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 223 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0024725 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2677 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100200 |  | 0 | 1 | 95 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2992 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 326 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001348 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2992 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195100210 |  | 0 | 1 | 95 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3920 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 305 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.001797 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3920 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110100 |  | 0 | 1 | 95 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1532 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 161 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050449 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1532 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110110 |  | 0 | 1 | 95 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1976 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 178 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011283 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1976 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110150 |  | 0 | 1 | 95 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2361 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 258 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0010898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2361 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110160 |  | 0 | 1 | 95 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2945 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 245 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0029567 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2945 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110200 |  | 0 | 1 | 95 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3291 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 359 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.001713 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 3291 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195110210 |  | 0 | 1 | 95 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4312 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 335 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0020848 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4312 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120100 |  | 0 | 1 | 95 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1672 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 175 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00066299 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1672 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120110 |  | 0 | 1 | 95 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2155 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014545 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2155 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120150 |  | 0 | 1 | 95 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2575 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 281 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.001295 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2575 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120160 |  | 0 | 1 | 95 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3212 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 267 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.003491 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3212 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120200 |  | 0 | 1 | 95 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3590 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 392 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0019355 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3590 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195120210 |  | 0 | 1 | 95 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4704 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 366 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0026599 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4704 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140100 |  | 0 | 1 | 95 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1950 | 0 | 0 | 0 | 1.343 | 1.08 | 1.08 | 1.08 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0010612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1950 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140110 |  | 0 | 1 | 95 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2514 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 226 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0022656 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2514 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140150 |  | 0 | 1 | 95 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3004 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 328 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001986 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 3004 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140160 |  | 0 | 1 | 95 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3748 | 0 | 0 | 0 | 1.482 | 1.1 | 1.1 | 1.1 | 312 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0047157 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3748 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140200 |  | 0 | 1 | 95 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4189 | 0 | 0 | 0 | 1.32 | 1.08 | 1.08 | 1.08 | 457 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0028735 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 4189 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
195140210 |  | 0 | 1 | 95 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5488 | 0 | 0 | 0 | 1.522 | 1.05 | 1.05 | 1.05 | 427 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0037262 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5488 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22050100 |  | 0 | 2 | 20 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 26 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6.3694e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 284 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22060100 |  | 0 | 2 | 20 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 31 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 341 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22060150 |  | 0 | 2 | 20 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 623 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 623 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22060200 |  | 0 | 2 | 20 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 836 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22070100 |  | 0 | 2 | 20 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 398 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22070150 |  | 0 | 2 | 20 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 727 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.5819e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 727 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22070200 |  | 0 | 2 | 20 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 976 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011449 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 976 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22080100 |  | 0 | 2 | 20 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 454 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 41 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.1383e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 454 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22080150 |  | 0 | 2 | 20 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010164 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 830 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22080200 |  | 0 | 2 | 20 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011849 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1115 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22090100 |  | 0 | 2 | 20 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 511 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.3972e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 511 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22090150 |  | 0 | 2 | 20 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 934 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001061 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 934 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
22090200 |  | 0 | 2 | 20 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1255 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00017422 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1255 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220100100 |  | 0 | 2 | 20 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 568 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.7174e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 568 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220100150 |  | 0 | 2 | 20 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016918 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1038 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220100200 |  | 0 | 2 | 20 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1394 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00024191 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1394 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220110100 |  | 0 | 2 | 20 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.2405e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 625 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220110150 |  | 0 | 2 | 20 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1142 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017573 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1142 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220110200 |  | 0 | 2 | 20 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1533 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00024904 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1533 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220120100 |  | 0 | 2 | 20 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 682 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7635e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 682 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220120150 |  | 0 | 2 | 20 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1246 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00025759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1246 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220120200 |  | 0 | 2 | 20 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1673 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00033101 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1673 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220140100 |  | 0 | 2 | 20 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016581 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 795 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220140150 |  | 0 | 2 | 20 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00036862 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1453 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220140200 |  | 0 | 2 | 20 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1952 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00043706 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1952 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220160100 |  | 0 | 2 | 20 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 909 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220160150 |  | 0 | 2 | 20 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1661 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050396 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1661 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220160200 |  | 0 | 2 | 20 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2230 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 204 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00067276 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2230 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220180100 |  | 0 | 2 | 20 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1022 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0003001 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1022 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220180150 |  | 0 | 2 | 20 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1868 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00066522 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1868 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220180200 |  | 0 | 2 | 20 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2509 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00083029 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2509 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220200100 |  | 0 | 2 | 20 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1136 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00032548 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1136 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220200150 |  | 0 | 2 | 20 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2076 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00085394 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2076 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220200200 |  | 0 | 2 | 20 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2788 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 255 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0010081 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2788 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220220100 |  | 0 | 2 | 20 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1250 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00048748 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1250 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220220150 |  | 0 | 2 | 20 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2284 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 209 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0010716 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2284 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220220200 |  | 0 | 2 | 20 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3067 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 281 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0012072 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3067 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220240100 |  | 0 | 2 | 20 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1363 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0005223 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1363 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220240150 |  | 0 | 2 | 20 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2491 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0013198 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2491 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220240200 |  | 0 | 2 | 20 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3346 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 306 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0016129 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3346 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220260100 |  | 0 | 2 | 20 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1477 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00073496 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 1477 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220260150 |  | 0 | 2 | 20 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2699 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 247 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0015997 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 2699 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220260200 |  | 0 | 2 | 20 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3624 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 331 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001874 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3624 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220280100 |  | 0 | 2 | 20 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1591 | 0 | 0 | 0 | 1.436 | 1.08 | 1.08 | 1.08 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00078045 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1591 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220280150 |  | 0 | 2 | 20 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2906 | 0 | 0 | 0 | 1.424 | 1.08 | 1.08 | 1.08 | 266 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.001913 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2906 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220280200 |  | 0 | 2 | 20 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3903 | 0 | 0 | 0 | 1.425 | 1.08 | 1.08 | 1.08 | 357 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0021592 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3903 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23550100 |  | 0 | 2 | 35 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 393 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23550110 |  | 0 | 2 | 35 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 549 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 549 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560100 |  | 0 | 2 | 35 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 471 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 44 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 471 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560110 |  | 0 | 2 | 35 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 659 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 659 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560150 |  | 0 | 2 | 35 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 790 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 790 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560160 |  | 0 | 2 | 35 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 975 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560200 |  | 0 | 2 | 35 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1081 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1081 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23560210 |  | 0 | 2 | 35 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1247 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1247 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570100 |  | 0 | 2 | 35 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 550 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570110 |  | 0 | 2 | 35 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 769 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570150 |  | 0 | 2 | 35 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00014954 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 922 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570160 |  | 0 | 2 | 35 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1138 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00041403 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1138 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570200 |  | 0 | 2 | 35 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1261 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00016328 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1261 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23570210 |  | 0 | 2 | 35 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024224 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1455 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580100 |  | 0 | 2 | 35 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 628 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 628 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580110 |  | 0 | 2 | 35 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 878 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 878 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580150 |  | 0 | 2 | 35 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1054 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00015609 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1054 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580160 |  | 0 | 2 | 35 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1300 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00060898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1300 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580200 |  | 0 | 2 | 35 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1441 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00022764 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1441 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23580210 |  | 0 | 2 | 35 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1662 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034051 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1662 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590100 |  | 0 | 2 | 35 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 707 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 707 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590110 |  | 0 | 2 | 35 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 988 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 988 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590150 |  | 0 | 2 | 35 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1185 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 113 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002307 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1185 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590160 |  | 0 | 2 | 35 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1463 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00062691 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1463 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590200 |  | 0 | 2 | 35 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1621 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 155 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00030408 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1621 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
23590210 |  | 0 | 2 | 35 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1870 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00045824 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1870 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100100 |  | 0 | 2 | 35 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 785 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100110 |  | 0 | 2 | 35 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035791 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1098 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100150 |  | 0 | 2 | 35 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1317 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00032186 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1317 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100160 |  | 0 | 2 | 35 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1625 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00086899 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1625 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100200 |  | 0 | 2 | 35 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1801 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00039308 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1801 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235100210 |  | 0 | 2 | 35 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2078 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00059642 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2078 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110100 |  | 0 | 2 | 35 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 864 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 864 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110110 |  | 0 | 2 | 35 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1208 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110150 |  | 0 | 2 | 35 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1449 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00033355 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1449 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110160 |  | 0 | 2 | 35 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1788 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.001155 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 1788 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110200 |  | 0 | 2 | 35 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1981 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00049511 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1981 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235110210 |  | 0 | 2 | 35 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2286 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00075597 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2286 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120100 |  | 0 | 2 | 35 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 942 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 942 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120110 |  | 0 | 2 | 35 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1318 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057024 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1318 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120150 |  | 0 | 2 | 35 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1580 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 151 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00044509 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1580 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120160 |  | 0 | 2 | 35 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1950 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 167 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014865 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1950 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120200 |  | 0 | 2 | 35 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2161 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 206 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00061062 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2161 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235120210 |  | 0 | 2 | 35 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2494 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00093782 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2494 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140100 |  | 0 | 2 | 35 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1099 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00024935 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1099 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140110 |  | 0 | 2 | 35 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1537 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084707 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1537 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140150 |  | 0 | 2 | 35 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1844 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 176 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00059309 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1844 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140160 |  | 0 | 2 | 35 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2275 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0019081 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2275 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140200 |  | 0 | 2 | 35 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2421 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 231 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00075811 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2421 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235140210 |  | 0 | 2 | 35 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2909 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 242 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0011789 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 2909 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160100 |  | 0 | 2 | 35 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1256 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1256 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160110 |  | 0 | 2 | 35 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1757 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011951 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1757 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160150 |  | 0 | 2 | 35 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2107 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 202 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00076744 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2107 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160160 |  | 0 | 2 | 35 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 222 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0023937 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2600 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160200 |  | 0 | 2 | 35 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2882 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 275 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.001066 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2882 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235160210 |  | 0 | 2 | 35 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3325 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0016729 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 3325 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180100 |  | 0 | 2 | 35 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1413 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 131 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1413 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180110 |  | 0 | 2 | 35 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1976 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 170 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0016207 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1976 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180150 |  | 0 | 2 | 35 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2371 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 227 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0011421 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2371 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180160 |  | 0 | 2 | 35 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2925 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 250 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0034326 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 2925 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180200 |  | 0 | 2 | 35 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3242 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 310 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0014352 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3242 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235180210 |  | 0 | 2 | 35 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3740 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 311 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0022708 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3740 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200100 |  | 0 | 2 | 35 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1570 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 145 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00059851 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1570 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200110 |  | 0 | 2 | 35 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2196 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0021301 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2196 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200150 |  | 0 | 2 | 35 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2634 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 252 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0013958 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2634 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200160 |  | 0 | 2 | 35 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3250 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 278 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.004109 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3250 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200200 |  | 0 | 2 | 35 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3602 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 344 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.001869 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3602 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235200210 |  | 0 | 2 | 35 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4156 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0029791 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 4156 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220100 |  | 0 | 2 | 35 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1727 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00081987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1727 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220110 |  | 0 | 2 | 35 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2416 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0027293 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2416 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220150 |  | 0 | 2 | 35 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2897 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0016812 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2897 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220160 |  | 0 | 2 | 35 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3575 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 306 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0054937 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 3575 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220200 |  | 0 | 2 | 35 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3962 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 379 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0023704 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3962 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235220210 |  | 0 | 2 | 35 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4572 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0038038 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 4572 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240100 |  | 0 | 2 | 35 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1884 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001085 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1884 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240110 |  | 0 | 2 | 35 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2635 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 227 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0034241 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2635 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240150 |  | 0 | 2 | 35 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3161 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 303 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0022556 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3161 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240160 |  | 0 | 2 | 35 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3900 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 334 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0063803 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3900 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240200 |  | 0 | 2 | 35 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4322 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 413 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0026947 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4322 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235240210 |  | 0 | 2 | 35 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4987 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 415 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0043563 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 4987 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260100 |  | 0 | 2 | 35 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2041 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.001397 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2041 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260110 |  | 0 | 2 | 35 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2855 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0042203 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 2855 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260150 |  | 0 | 2 | 35 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3424 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 328 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0026338 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 3424 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260160 |  | 0 | 2 | 35 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4255 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 364 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0081394 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 4255 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260200 |  | 0 | 2 | 35 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4683 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 447 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.003311 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 4683 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235260210 |  | 0 | 2 | 35 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5403 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 450 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0053829 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 5403 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280100 |  | 0 | 2 | 35 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2198 | 0 | 0 | 0 | 1.419 | 1.08 | 1.08 | 1.08 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014814 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2198 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280110 |  | 0 | 2 | 35 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3074 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 265 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0051235 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3074 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280150 |  | 0 | 2 | 35 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3688 | 0 | 0 | 0 | 1.398 | 1.08 | 1.08 | 1.08 | 353 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0030486 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3688 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280160 |  | 0 | 2 | 35 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4550 | 0 | 0 | 0 | 1.465 | 1.1 | 1.1 | 1.1 | 389 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0092545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 4550 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280200 |  | 0 | 2 | 35 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5043 | 0 | 0 | 0 | 1.399 | 1.08 | 1.08 | 1.08 | 482 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0040028 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5043 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235280210 |  | 0 | 2 | 35 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5818 | 0 | 0 | 0 | 1.481 | 1.05 | 1.05 | 1.05 | 484 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0065417 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 5818 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25050100 |  | 0 | 2 | 50 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 482 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 482 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25050110 |  | 0 | 2 | 50 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 655 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 655 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060100 |  | 0 | 2 | 50 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 578 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060110 |  | 0 | 2 | 50 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 785 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060150 |  | 0 | 2 | 50 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 920 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.000143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 920 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060160 |  | 0 | 2 | 50 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1171 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1171 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060200 |  | 0 | 2 | 50 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1272 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 127 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00021338 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1272 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25060210 |  | 0 | 2 | 50 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1538 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 127 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031197 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1538 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070100 |  | 0 | 2 | 50 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 675 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 64 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 675 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070110 |  | 0 | 2 | 50 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 916 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 916 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070150 |  | 0 | 2 | 50 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1073 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00021277 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1073 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070160 |  | 0 | 2 | 50 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1366 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00059105 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1366 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070200 |  | 0 | 2 | 50 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1484 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00028612 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1484 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25070210 |  | 0 | 2 | 50 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1795 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00042233 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1795 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080100 |  | 0 | 2 | 50 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 771 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 771 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080110 |  | 0 | 2 | 50 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1047 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00030716 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1047 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080150 |  | 0 | 2 | 50 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00022173 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1226 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080160 |  | 0 | 2 | 50 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1561 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00082222 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1561 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080200 |  | 0 | 2 | 50 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1696 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1696 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25080210 |  | 0 | 2 | 50 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2051 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2051 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090100 |  | 0 | 2 | 50 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 868 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 868 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090110 |  | 0 | 2 | 50 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1178 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00033253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1178 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090150 |  | 0 | 2 | 50 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1380 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031016 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1380 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090160 |  | 0 | 2 | 50 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1756 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 151 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010961 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1756 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090200 |  | 0 | 2 | 50 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1908 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00046874 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1908 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
25090210 |  | 0 | 2 | 50 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2308 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 191 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00070324 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2308 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100100 |  | 0 | 2 | 50 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 964 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 964 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100110 |  | 0 | 2 | 50 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1309 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00050061 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1309 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100150 |  | 0 | 2 | 50 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1533 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00041565 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1533 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100160 |  | 0 | 2 | 50 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1951 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 167 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1951 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100200 |  | 0 | 2 | 50 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2120 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00057956 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2120 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250100210 |  | 0 | 2 | 50 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2564 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00087568 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2564 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110100 |  | 0 | 2 | 50 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1060 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110110 |  | 0 | 2 | 50 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1440 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00053543 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1440 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110150 |  | 0 | 2 | 50 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1686 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053899 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1686 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110160 |  | 0 | 2 | 50 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2146 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014504 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2146 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110200 |  | 0 | 2 | 50 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2332 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 233 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00070398 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2332 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250110210 |  | 0 | 2 | 50 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2820 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 233 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010707 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2820 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120100 |  | 0 | 2 | 50 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1157 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1157 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120110 |  | 0 | 2 | 50 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1571 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 137 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.0007561 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1571 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120150 |  | 0 | 2 | 50 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1840 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055702 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1840 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120160 |  | 0 | 2 | 50 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2341 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 201 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0018216 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2341 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120200 |  | 0 | 2 | 50 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2544 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 254 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00084245 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2544 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250120210 |  | 0 | 2 | 50 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3077 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 254 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.001289 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3077 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140100 |  | 0 | 2 | 50 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1350 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1350 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140110 |  | 0 | 2 | 50 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1833 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1833 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140150 |  | 0 | 2 | 50 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2146 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 215 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00086774 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2146 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140160 |  | 0 | 2 | 50 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2731 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 234 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0027093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2731 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140200 |  | 0 | 2 | 50 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2968 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 296 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0011632 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2968 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250140210 |  | 0 | 2 | 50 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3590 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 296 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0017995 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3590 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160100 |  | 0 | 2 | 50 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1542 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00064784 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1542 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160110 |  | 0 | 2 | 50 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2094 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00148 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2094 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160150 |  | 0 | 2 | 50 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2453 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 245 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012598 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2453 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160160 |  | 0 | 2 | 50 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3122 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 268 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0038 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3122 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160200 |  | 0 | 2 | 50 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3392 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0015452 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3392 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250160210 |  | 0 | 2 | 50 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4102 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0024135 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4102 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180100 |  | 0 | 2 | 50 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1735 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 165 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00087401 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1735 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180110 |  | 0 | 2 | 50 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2356 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0023308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2356 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180150 |  | 0 | 2 | 50 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2759 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 276 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0015267 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2759 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180160 |  | 0 | 2 | 50 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3512 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 301 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0051047 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3512 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180200 |  | 0 | 2 | 50 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3816 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0021964 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3816 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250180210 |  | 0 | 2 | 50 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4615 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0034559 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4615 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200100 |  | 0 | 2 | 50 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1928 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 183 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00094435 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1928 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200110 |  | 0 | 2 | 50 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2618 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0029607 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2618 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200150 |  | 0 | 2 | 50 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3066 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 307 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0020611 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3066 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200160 |  | 0 | 2 | 50 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3902 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 335 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0059484 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3902 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200200 |  | 0 | 2 | 50 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4240 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 423 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0027374 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4240 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250200210 |  | 0 | 2 | 50 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5128 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 423 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0043411 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 5128 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220100 |  | 0 | 2 | 50 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2121 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 202 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0012281 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220110 |  | 0 | 2 | 50 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2880 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 250 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0036879 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2880 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220150 |  | 0 | 2 | 50 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3373 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 337 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0024178 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3373 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220160 |  | 0 | 2 | 50 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4292 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 368 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0076163 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4292 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220200 |  | 0 | 2 | 50 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4664 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 465 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0033497 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4664 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250220210 |  | 0 | 2 | 50 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5641 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 466 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0053502 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 5641 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240100 |  | 0 | 2 | 50 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2314 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0015594 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2314 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240110 |  | 0 | 2 | 50 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3142 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 273 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.004518 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3142 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240150 |  | 0 | 2 | 50 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3679 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 368 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0031091 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3679 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240160 |  | 0 | 2 | 50 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4682 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 402 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0095255 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4682 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240200 |  | 0 | 2 | 50 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5088 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 508 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0040363 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 5088 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250240210 |  | 0 | 2 | 50 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6154 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 508 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0064891 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 6154 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260100 |  | 0 | 2 | 50 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2506 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 238 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0019411 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260110 |  | 0 | 2 | 50 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3403 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 296 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0054566 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3403 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260150 |  | 0 | 2 | 50 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3986 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 398 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0039044 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 3986 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260160 |  | 0 | 2 | 50 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5073 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 435 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.010742 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 5073 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260200 |  | 0 | 2 | 50 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5512 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 550 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0047999 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 5512 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250260210 |  | 0 | 2 | 50 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6666 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 550 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0077634 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 6666 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280100 |  | 0 | 2 | 50 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2699 | 0 | 0 | 0 | 1.402 | 1.08 | 1.08 | 1.08 | 257 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0023761 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2699 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280110 |  | 0 | 2 | 50 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3665 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 319 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0065091 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3665 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280150 |  | 0 | 2 | 50 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4292 | 0 | 0 | 0 | 1.372 | 1.08 | 1.08 | 1.08 | 429 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0044267 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4292 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280160 |  | 0 | 2 | 50 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5463 | 0 | 0 | 0 | 1.463 | 1.1 | 1.1 | 1.1 | 469 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.013058 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 5463 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280200 |  | 0 | 2 | 50 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5936 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 592 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0060033 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5936 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250280210 |  | 0 | 2 | 50 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7179 | 0 | 0 | 0 | 1.486 | 1.05 | 1.05 | 1.05 | 593 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0097556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 7179 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26550100 |  | 0 | 2 | 65 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 561 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26550110 |  | 0 | 2 | 65 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 742 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 742 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560100 |  | 0 | 2 | 65 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 673 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 673 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560110 |  | 0 | 2 | 65 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 890 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 890 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560150 |  | 0 | 2 | 65 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1029 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 108 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00020381 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1029 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560160 |  | 0 | 2 | 65 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1336 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057313 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1336 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560200 |  | 0 | 2 | 65 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1435 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00027715 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1435 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26560210 |  | 0 | 2 | 65 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1803 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1803 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570100 |  | 0 | 2 | 65 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 785 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570110 |  | 0 | 2 | 65 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00028178 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1038 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570150 |  | 0 | 2 | 65 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1201 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00028678 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1201 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570160 |  | 0 | 2 | 65 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1559 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00079884 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1559 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570200 |  | 0 | 2 | 65 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1674 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00036009 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1674 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26570210 |  | 0 | 2 | 65 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2104 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053044 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2104 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580100 |  | 0 | 2 | 65 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 897 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 897 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580110 |  | 0 | 2 | 65 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1186 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00030716 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1186 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580150 |  | 0 | 2 | 65 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1372 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00029847 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1372 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580160 |  | 0 | 2 | 65 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1782 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010667 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1782 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580200 |  | 0 | 2 | 65 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1913 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 199 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00045556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1913 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26580210 |  | 0 | 2 | 65 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2404 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 197 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00067687 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2404 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590100 |  | 0 | 2 | 65 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1009 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590110 |  | 0 | 2 | 65 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1335 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0004658 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1335 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590150 |  | 0 | 2 | 65 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1544 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 162 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1544 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590160 |  | 0 | 2 | 65 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2004 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013783 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2004 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590200 |  | 0 | 2 | 65 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2152 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 224 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00066789 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2152 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26590210 |  | 0 | 2 | 65 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2705 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 222 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00084461 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2705 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100100 |  | 0 | 2 | 65 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100110 |  | 0 | 2 | 65 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00066513 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1483 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100150 |  | 0 | 2 | 65 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1715 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00052096 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1715 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100160 |  | 0 | 2 | 65 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2227 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017352 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2227 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100200 |  | 0 | 2 | 65 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2391 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 249 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00080103 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2391 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265100210 |  | 0 | 2 | 65 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3005 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012062 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3005 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110100 |  | 0 | 2 | 65 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1233 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110110 |  | 0 | 2 | 65 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1631 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00071062 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1631 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110150 |  | 0 | 2 | 65 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1887 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 197 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00065932 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1887 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110160 |  | 0 | 2 | 65 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2450 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 211 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021389 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2450 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110200 |  | 0 | 2 | 65 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2630 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 274 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.00094834 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2630 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265110210 |  | 0 | 2 | 65 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3306 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 271 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0014376 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3306 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120100 |  | 0 | 2 | 65 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1345 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00041656 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1345 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120110 |  | 0 | 2 | 65 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1780 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00096572 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1780 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120150 |  | 0 | 2 | 65 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2058 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 215 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00081677 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2058 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120160 |  | 0 | 2 | 65 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2672 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 230 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0025909 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2672 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120200 |  | 0 | 2 | 65 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2869 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 299 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0011102 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2869 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265120210 |  | 0 | 2 | 65 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3606 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 296 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0016935 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3606 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140100 |  | 0 | 2 | 65 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1569 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0005905 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1569 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140110 |  | 0 | 2 | 65 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2076 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013393 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2076 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140150 |  | 0 | 2 | 65 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2401 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 251 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0011918 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2401 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140160 |  | 0 | 2 | 65 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3118 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 269 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0036455 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3118 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140200 |  | 0 | 2 | 65 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3347 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 348 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0016514 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3347 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265140210 |  | 0 | 2 | 65 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4207 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 345 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0025438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4207 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160100 |  | 0 | 2 | 65 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1794 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 175 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00080367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1794 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160110 |  | 0 | 2 | 65 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2373 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021315 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2373 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160150 |  | 0 | 2 | 65 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2744 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 287 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0016517 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2744 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160160 |  | 0 | 2 | 65 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3563 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 307 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0049102 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3563 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160200 |  | 0 | 2 | 65 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3826 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 398 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0023163 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3826 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265160210 |  | 0 | 2 | 65 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4808 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 394 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.003282 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4808 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180100 |  | 0 | 2 | 65 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2018 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 197 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0010592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2018 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180110 |  | 0 | 2 | 65 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2669 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 234 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002729 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2669 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180150 |  | 0 | 2 | 65 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3087 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 323 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0022019 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3087 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180160 |  | 0 | 2 | 65 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4009 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0063954 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 4009 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180200 |  | 0 | 2 | 65 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4304 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 448 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0028685 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4304 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265180210 |  | 0 | 2 | 65 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5409 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 444 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0044979 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5409 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200100 |  | 0 | 2 | 65 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2242 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0013601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2242 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200110 |  | 0 | 2 | 65 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2966 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0034217 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2966 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200150 |  | 0 | 2 | 65 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3430 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 359 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0028475 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3430 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200160 |  | 0 | 2 | 65 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4454 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 384 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0081115 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4454 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200200 |  | 0 | 2 | 65 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4782 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 498 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.003763 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4782 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265200210 |  | 0 | 2 | 65 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6010 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 493 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0055199 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 6010 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220100 |  | 0 | 2 | 65 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2466 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 241 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0017094 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2466 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220110 |  | 0 | 2 | 65 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3263 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 286 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0047741 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3263 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220150 |  | 0 | 2 | 65 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3773 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 395 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0032791 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3773 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220160 |  | 0 | 2 | 65 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4899 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 423 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.010068 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4899 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220200 |  | 0 | 2 | 65 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5260 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 547 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0044894 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 5260 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265220210 |  | 0 | 2 | 65 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6611 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 542 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0071424 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 6611 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240100 |  | 0 | 2 | 65 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2690 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 263 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0024131 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2690 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240110 |  | 0 | 2 | 65 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3559 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 312 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0057458 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3559 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240150 |  | 0 | 2 | 65 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4116 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 431 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.00409 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4116 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240160 |  | 0 | 2 | 65 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5345 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 461 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.012276 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5345 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240200 |  | 0 | 2 | 65 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5738 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 597 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0056334 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 5738 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265240210 |  | 0 | 2 | 65 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7212 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 591 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0084792 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 7212 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260100 |  | 0 | 2 | 65 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2915 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 285 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0029051 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2915 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260110 |  | 0 | 2 | 65 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3856 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 338 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0068328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3856 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260150 |  | 0 | 2 | 65 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4459 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 466 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0050094 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4459 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260160 |  | 0 | 2 | 65 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5790 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 499 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.014743 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 5790 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260200 |  | 0 | 2 | 65 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6217 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 647 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.0065489 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 6217 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265260210 |  | 0 | 2 | 65 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7813 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 641 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.010547 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 7813 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280100 |  | 0 | 2 | 65 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3139 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 307 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0034557 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3139 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280110 |  | 0 | 2 | 65 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4152 | 0 | 0 | 0 | 1.45 | 1.1 | 1.1 | 1.1 | 364 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0088602 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4152 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280150 |  | 0 | 2 | 65 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4802 | 0 | 0 | 0 | 1.345 | 1.08 | 1.08 | 1.08 | 502 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0060421 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4802 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280160 |  | 0 | 2 | 65 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6236 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 538 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.017479 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 6236 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280200 |  | 0 | 2 | 65 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6695 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 697 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.0079611 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 6695 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
265280210 |  | 0 | 2 | 65 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8414 | 0 | 0 | 0 | 1.49 | 1.05 | 1.05 | 1.05 | 690 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.012886 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 8414 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560100 |  | 0 | 2 | 95 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.6886e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 838 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560110 |  | 0 | 2 | 95 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00025641 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1055 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560150 |  | 0 | 2 | 95 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00027509 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1210 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560160 |  | 0 | 2 | 95 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1608 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00077545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1608 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560200 |  | 0 | 2 | 95 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1706 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00042919 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1706 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29560210 |  | 0 | 2 | 95 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2290 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 185 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00062414 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2290 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570100 |  | 0 | 2 | 95 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 977 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016054 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 977 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570110 |  | 0 | 2 | 95 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00039617 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1231 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570150 |  | 0 | 2 | 95 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1411 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 161 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0003715 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1411 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570160 |  | 0 | 2 | 95 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1876 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010372 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1876 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570200 |  | 0 | 2 | 95 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1991 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 226 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0006318 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1991 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29570210 |  | 0 | 2 | 95 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2671 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 216 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00078248 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2671 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580100 |  | 0 | 2 | 95 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024379 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 1117 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580110 |  | 0 | 2 | 95 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1406 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00043099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1406 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580150 |  | 0 | 2 | 95 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1613 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00048489 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1613 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580160 |  | 0 | 2 | 95 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2144 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 186 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016487 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2144 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580200 |  | 0 | 2 | 95 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2275 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 258 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00075961 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2275 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29580210 |  | 0 | 2 | 95 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3053 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 247 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0011234 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3053 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590100 |  | 0 | 2 | 95 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1256 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034834 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1256 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590110 |  | 0 | 2 | 95 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1582 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00061964 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590150 |  | 0 | 2 | 95 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1814 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 207 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00074031 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1814 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590160 |  | 0 | 2 | 95 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2412 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0020369 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2412 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590200 |  | 0 | 2 | 95 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2560 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 291 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0010308 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2560 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
29590210 |  | 0 | 2 | 95 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3434 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0013435 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3434 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100100 |  | 0 | 2 | 95 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1396 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 145 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1396 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100110 |  | 0 | 2 | 95 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1758 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00085103 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1758 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100150 |  | 0 | 2 | 95 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2016 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 230 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0009052 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 2016 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100160 |  | 0 | 2 | 95 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2680 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 233 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0024725 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2680 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100200 |  | 0 | 2 | 95 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2844 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 323 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001348 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2844 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295100210 |  | 0 | 2 | 95 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3816 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 308 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.001797 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3816 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110100 |  | 0 | 2 | 95 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1536 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050449 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1536 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110110 |  | 0 | 2 | 95 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1934 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011283 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1934 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110150 |  | 0 | 2 | 95 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2218 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 253 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0010898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2218 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110160 |  | 0 | 2 | 95 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2948 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0029567 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2948 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110200 |  | 0 | 2 | 95 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3128 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 355 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0015426 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 3128 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295110210 |  | 0 | 2 | 95 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4196 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0020848 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4196 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120100 |  | 0 | 2 | 95 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1675 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00066299 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1675 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120110 |  | 0 | 2 | 95 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2110 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 188 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014545 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2110 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120150 |  | 0 | 2 | 95 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2419 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 276 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.001295 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2419 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120160 |  | 0 | 2 | 95 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3216 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 280 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.003491 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3216 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120200 |  | 0 | 2 | 95 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3413 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 388 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0019355 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3413 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295120210 |  | 0 | 2 | 95 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4579 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 370 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0026599 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4579 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140100 |  | 0 | 2 | 95 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1954 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00089031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1954 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140110 |  | 0 | 2 | 95 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2461 | 0 | 0 | 0 | 1.441 | 1.1 | 1.1 | 1.1 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0019323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2461 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140150 |  | 0 | 2 | 95 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2822 | 0 | 0 | 0 | 1.293 | 1.08 | 1.08 | 1.08 | 322 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001986 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2822 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140160 |  | 0 | 2 | 95 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3752 | 0 | 0 | 0 | 1.455 | 1.1 | 1.1 | 1.1 | 326 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0053007 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3752 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140200 |  | 0 | 2 | 95 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3982 | 0 | 0 | 0 | 1.296 | 1.08 | 1.08 | 1.08 | 452 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0026472 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3982 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
295140210 |  | 0 | 2 | 95 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5342 | 0 | 0 | 0 | 1.499 | 1.05 | 1.05 | 1.05 | 432 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0037262 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5342 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32050100 |  | 0 | 3 | 20 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 31 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 328 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32060100 |  | 0 | 3 | 20 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 37 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 393 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32060150 |  | 0 | 3 | 20 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 654 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 654 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32060200 |  | 0 | 3 | 20 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 919 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 919 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32070100 |  | 0 | 3 | 20 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 459 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 459 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32070150 |  | 0 | 3 | 20 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.7187e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 763 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32070200 |  | 0 | 3 | 20 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1072 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011449 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1072 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32080100 |  | 0 | 3 | 20 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 524 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 524 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32080150 |  | 0 | 3 | 20 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 872 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010164 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 872 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32080200 |  | 0 | 3 | 20 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00016875 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1226 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32090100 |  | 0 | 3 | 20 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 590 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32090150 |  | 0 | 3 | 20 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 981 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016264 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 981 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
32090200 |  | 0 | 3 | 20 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1379 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00023478 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1379 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320100100 |  | 0 | 3 | 20 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 655 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.7174e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 655 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320100150 |  | 0 | 3 | 20 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016918 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1090 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320100200 |  | 0 | 3 | 20 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1532 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00024191 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1532 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320110100 |  | 0 | 3 | 20 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 721 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.2405e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 721 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320110150 |  | 0 | 3 | 20 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1199 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 113 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024862 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1199 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320110200 |  | 0 | 3 | 20 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1685 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00032203 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1685 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320120100 |  | 0 | 3 | 20 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 786 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 786 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320120150 |  | 0 | 3 | 20 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1308 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00025759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1308 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320120200 |  | 0 | 3 | 20 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1838 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00041507 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1838 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320140100 |  | 0 | 3 | 20 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016581 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 917 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320140150 |  | 0 | 3 | 20 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1526 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00036862 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1526 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320140200 |  | 0 | 3 | 20 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2145 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 202 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00053465 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2145 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320160100 |  | 0 | 3 | 20 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1048 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00027473 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1048 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320160150 |  | 0 | 3 | 20 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1744 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 164 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050396 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1744 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320160200 |  | 0 | 3 | 20 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2451 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 231 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0007942 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2451 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320180100 |  | 0 | 3 | 20 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1179 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00041786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1179 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320180150 |  | 0 | 3 | 20 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1962 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 185 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00081069 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1962 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320180200 |  | 0 | 3 | 20 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2758 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00096672 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2758 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320200100 |  | 0 | 3 | 20 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1310 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00045267 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1310 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320200150 |  | 0 | 3 | 20 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2180 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0010207 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2180 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320200200 |  | 0 | 3 | 20 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3064 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 288 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0013222 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3064 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320220100 |  | 0 | 3 | 20 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1441 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00064399 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1441 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320220150 |  | 0 | 3 | 20 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2398 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 226 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0012605 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2398 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320220200 |  | 0 | 3 | 20 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3370 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 317 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0015537 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3370 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320240100 |  | 0 | 3 | 20 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1572 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00087721 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1572 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320240150 |  | 0 | 3 | 20 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2616 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0015318 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2616 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320240200 |  | 0 | 3 | 20 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3677 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0020141 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3677 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320260100 |  | 0 | 3 | 20 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1703 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00093455 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 1703 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320260150 |  | 0 | 3 | 20 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2834 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 267 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0018357 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 2834 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320260200 |  | 0 | 3 | 20 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3983 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 375 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0023101 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3983 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320280100 |  | 0 | 3 | 20 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1834 | 0 | 0 | 0 | 1.413 | 1.08 | 1.08 | 1.08 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0012257 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1834 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320280150 |  | 0 | 3 | 20 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3052 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 287 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0021738 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3052 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
320280200 |  | 0 | 3 | 20 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4290 | 0 | 0 | 0 | 1.408 | 1.08 | 1.08 | 1.08 | 404 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0028839 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4290 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33050100 |  | 0 | 3 | 30 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 413 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33050110 |  | 0 | 3 | 30 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 50 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 561 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060100 |  | 0 | 3 | 30 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 496 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 496 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060110 |  | 0 | 3 | 30 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 673 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 673 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060150 |  | 0 | 3 | 30 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 815 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060160 |  | 0 | 3 | 30 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 888 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 888 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060200 |  | 0 | 3 | 30 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1144 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1144 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33060210 |  | 0 | 3 | 30 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1169 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1169 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070100 |  | 0 | 3 | 30 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 578 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070110 |  | 0 | 3 | 30 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 785 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070150 |  | 0 | 3 | 30 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 951 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00014954 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 951 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070160 |  | 0 | 3 | 30 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1036 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00041403 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1036 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070200 |  | 0 | 3 | 30 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1334 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00022051 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1334 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33070210 |  | 0 | 3 | 30 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1364 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024224 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1364 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080100 |  | 0 | 3 | 30 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 661 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 661 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080110 |  | 0 | 3 | 30 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 897 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 897 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080150 |  | 0 | 3 | 30 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1087 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00015609 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1087 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080160 |  | 0 | 3 | 30 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00042712 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1184 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080200 |  | 0 | 3 | 30 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1525 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0002951 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1525 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33080210 |  | 0 | 3 | 30 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1558 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034051 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1558 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090100 |  | 0 | 3 | 30 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 743 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 743 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090110 |  | 0 | 3 | 30 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00033253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1009 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090150 |  | 0 | 3 | 30 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002307 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1223 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090160 |  | 0 | 3 | 30 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00062691 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1332 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090200 |  | 0 | 3 | 30 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1715 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 165 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00038208 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1715 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
33090210 |  | 0 | 3 | 30 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1753 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00045824 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1753 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100100 |  | 0 | 3 | 30 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 826 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100110 |  | 0 | 3 | 30 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035791 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100150 |  | 0 | 3 | 30 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00032186 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1359 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100160 |  | 0 | 3 | 30 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1480 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 129 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00086899 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1480 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100200 |  | 0 | 3 | 30 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1906 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 183 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00039308 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1906 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330100210 |  | 0 | 3 | 30 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1948 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00059642 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 1948 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110100 |  | 0 | 3 | 30 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 909 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 909 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110110 |  | 0 | 3 | 30 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00053543 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1233 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110150 |  | 0 | 3 | 30 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1495 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00033355 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1495 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110160 |  | 0 | 3 | 30 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1628 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00089237 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 1628 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110200 |  | 0 | 3 | 30 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2097 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 201 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00049511 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2097 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330110210 |  | 0 | 3 | 30 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2143 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00061841 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2143 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120100 |  | 0 | 3 | 30 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 991 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 991 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120110 |  | 0 | 3 | 30 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1345 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057024 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1345 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120150 |  | 0 | 3 | 30 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1631 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00044509 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1631 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120160 |  | 0 | 3 | 30 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1776 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011844 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 1776 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120200 |  | 0 | 3 | 30 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2287 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00061062 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2287 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330120210 |  | 0 | 3 | 30 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2338 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 199 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00078234 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2338 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140100 |  | 0 | 3 | 30 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1156 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1156 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140110 |  | 0 | 3 | 30 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1569 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084707 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1569 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140150 |  | 0 | 3 | 30 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1903 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 183 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00059309 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1903 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140160 |  | 0 | 3 | 30 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2072 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0015586 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2072 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140200 |  | 0 | 3 | 30 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2668 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00088388 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2668 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330140210 |  | 0 | 3 | 30 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2727 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 232 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0011789 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 2727 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160100 |  | 0 | 3 | 30 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1322 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1322 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160110 |  | 0 | 3 | 30 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1794 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011951 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1794 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160150 |  | 0 | 3 | 30 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2174 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 209 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00091872 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2174 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160160 |  | 0 | 3 | 30 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2368 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 206 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0023937 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2368 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160200 |  | 0 | 3 | 30 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3050 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 293 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0012162 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3050 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330160210 |  | 0 | 3 | 30 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3117 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 265 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0016729 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 3117 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180100 |  | 0 | 3 | 30 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1487 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1487 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180110 |  | 0 | 3 | 30 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2018 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0016207 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2018 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180150 |  | 0 | 3 | 30 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2446 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0011421 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2446 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180160 |  | 0 | 3 | 30 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2664 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 231 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0029462 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 2664 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180200 |  | 0 | 3 | 30 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3431 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 329 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001611 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3431 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330180210 |  | 0 | 3 | 30 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3506 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 298 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0020114 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200100 |  | 0 | 3 | 30 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1652 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00076253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1652 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200110 |  | 0 | 3 | 30 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2242 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0021301 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2242 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200150 |  | 0 | 3 | 30 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2718 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 261 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0013958 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2718 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200160 |  | 0 | 3 | 30 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2960 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 257 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0035686 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 2960 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200200 |  | 0 | 3 | 30 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3812 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 366 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0020712 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3812 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330200210 |  | 0 | 3 | 30 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3896 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 332 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0026765 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 3896 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220100 |  | 0 | 3 | 30 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1817 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0010147 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1817 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220110 |  | 0 | 3 | 30 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2466 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0027293 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2466 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220150 |  | 0 | 3 | 30 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2990 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 287 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0019128 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2990 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220160 |  | 0 | 3 | 30 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3256 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 283 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.00486 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 3256 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220200 |  | 0 | 3 | 30 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4193 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 403 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0026001 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4193 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330220210 |  | 0 | 3 | 30 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4286 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 365 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0034561 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 4286 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240100 |  | 0 | 3 | 30 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1982 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 188 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0013125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1982 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240110 |  | 0 | 3 | 30 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2690 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 240 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0034241 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2690 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240150 |  | 0 | 3 | 30 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3262 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0022556 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3262 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240160 |  | 0 | 3 | 30 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3552 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 308 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0056881 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 3552 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240200 |  | 0 | 3 | 30 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4574 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 439 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0032004 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4574 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330240210 |  | 0 | 3 | 30 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4675 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 398 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0043563 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 4675 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260100 |  | 0 | 3 | 30 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2148 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 204 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.001659 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2148 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260110 |  | 0 | 3 | 30 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2915 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0042203 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 2915 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260150 |  | 0 | 3 | 30 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3533 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0026338 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 3533 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260160 |  | 0 | 3 | 30 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3848 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 334 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0065962 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 3848 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260200 |  | 0 | 3 | 30 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4956 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 476 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0038751 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 4956 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330260210 |  | 0 | 3 | 30 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5065 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 431 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.004956 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 5065 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280100 |  | 0 | 3 | 30 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2313 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0017586 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2313 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280110 |  | 0 | 3 | 30 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3139 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 280 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0051235 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3139 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280150 |  | 0 | 3 | 30 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3805 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 365 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0033706 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3805 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280160 |  | 0 | 3 | 30 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4144 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 360 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.008401 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 4144 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280200 |  | 0 | 3 | 30 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5337 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 512 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0043096 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5337 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330280210 |  | 0 | 3 | 30 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5454 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 464 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0060645 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 5454 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300100 |  | 0 | 3 | 30 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2478 | 0 | 0 | 0 | 1.403 | 1.08 | 1.08 | 1.08 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0021728 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2478 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300110 |  | 0 | 3 | 30 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3363 | 0 | 0 | 0 | 1.44 | 1.1 | 1.1 | 1.1 | 300 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.006139 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3363 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300150 |  | 0 | 3 | 30 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4077 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 391 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0038506 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 4077 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300160 |  | 0 | 3 | 30 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4440 | 0 | 0 | 0 | 1.456 | 1.1 | 1.1 | 1.1 | 386 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0095402 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 4440 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300200 |  | 0 | 3 | 30 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5718 | 0 | 0 | 0 | 1.396 | 1.08 | 1.08 | 1.08 | 549 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0051104 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 5718 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330300210 |  | 0 | 3 | 30 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5844 | 0 | 0 | 0 | 1.468 | 1.05 | 1.05 | 1.05 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0073089 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 5844 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34050100 |  | 0 | 3 | 40 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 482 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 482 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34050110 |  | 0 | 3 | 40 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 632 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 632 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060100 |  | 0 | 3 | 40 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 578 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060110 |  | 0 | 3 | 40 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 758 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060150 |  | 0 | 3 | 40 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 941 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.000143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 941 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060160 |  | 0 | 3 | 40 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1020 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060200 |  | 0 | 3 | 40 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1318 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 129 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00021338 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1318 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34060210 |  | 0 | 3 | 40 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1364 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1364 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070100 |  | 0 | 3 | 40 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 674 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 674 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070110 |  | 0 | 3 | 40 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 885 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070150 |  | 0 | 3 | 40 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00021277 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1098 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070160 |  | 0 | 3 | 40 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00041403 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1190 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070200 |  | 0 | 3 | 40 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1537 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 151 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00028612 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1537 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34070210 |  | 0 | 3 | 40 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1592 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00032624 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1592 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080100 |  | 0 | 3 | 40 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 770 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080110 |  | 0 | 3 | 40 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1011 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00030716 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1011 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080150 |  | 0 | 3 | 40 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1254 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00022173 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1254 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080160 |  | 0 | 3 | 40 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1360 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00060898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1360 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080200 |  | 0 | 3 | 40 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1757 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1757 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34080210 |  | 0 | 3 | 40 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1819 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00044029 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 1819 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090100 |  | 0 | 3 | 40 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 867 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 867 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090110 |  | 0 | 3 | 40 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1138 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00033253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1138 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090150 |  | 0 | 3 | 40 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1411 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031016 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1411 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090160 |  | 0 | 3 | 40 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1530 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084561 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1530 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090200 |  | 0 | 3 | 40 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1976 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00046874 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1976 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
34090210 |  | 0 | 3 | 40 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2047 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00057443 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2047 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100100 |  | 0 | 3 | 40 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 963 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100110 |  | 0 | 3 | 40 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1264 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 113 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00050061 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1264 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100150 |  | 0 | 3 | 40 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1568 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00041565 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1568 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100160 |  | 0 | 3 | 40 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1700 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011255 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1700 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100200 |  | 0 | 3 | 40 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2196 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 215 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00057956 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2196 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340100210 |  | 0 | 3 | 40 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2274 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 191 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00072961 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2274 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110100 |  | 0 | 3 | 40 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1059 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1059 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110110 |  | 0 | 3 | 40 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1390 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00053543 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1390 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110150 |  | 0 | 3 | 40 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1725 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053899 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1725 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110160 |  | 0 | 3 | 40 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1870 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 161 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.001155 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 1870 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110200 |  | 0 | 3 | 40 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2416 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 237 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00070398 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2416 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340110210 |  | 0 | 3 | 40 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2501 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00090675 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2501 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120100 |  | 0 | 3 | 40 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1156 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1156 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120110 |  | 0 | 3 | 40 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1517 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 136 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.0007561 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1517 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120150 |  | 0 | 3 | 40 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1882 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055702 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1882 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120160 |  | 0 | 3 | 40 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2040 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 176 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014865 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2040 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120200 |  | 0 | 3 | 40 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2635 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 258 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00084245 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2635 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340120210 |  | 0 | 3 | 40 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2729 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0011067 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2729 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140100 |  | 0 | 3 | 40 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1348 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1348 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140110 |  | 0 | 3 | 40 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1770 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1770 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140150 |  | 0 | 3 | 40 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2195 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 215 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00086774 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2195 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140160 |  | 0 | 3 | 40 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2380 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0022918 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2380 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140200 |  | 0 | 3 | 40 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3074 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 301 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0013168 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3074 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340140210 |  | 0 | 3 | 40 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3184 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 267 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0015788 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3184 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160100 |  | 0 | 3 | 40 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1541 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00064784 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1541 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160110 |  | 0 | 3 | 40 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2022 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 181 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00148 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2022 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160150 |  | 0 | 3 | 40 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2509 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 245 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012598 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2509 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160160 |  | 0 | 3 | 40 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2720 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0028278 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 2720 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160200 |  | 0 | 3 | 40 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3514 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 344 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0017239 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3514 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340160210 |  | 0 | 3 | 40 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3638 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 305 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0021524 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 3638 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180100 |  | 0 | 3 | 40 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1733 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 167 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00087401 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1733 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180110 |  | 0 | 3 | 40 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2275 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0019612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2275 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180150 |  | 0 | 3 | 40 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2822 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 276 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0015267 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2822 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180160 |  | 0 | 3 | 40 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3060 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 264 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0039545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3060 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180200 |  | 0 | 3 | 40 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3953 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 387 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0021964 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3953 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340180210 |  | 0 | 3 | 40 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4093 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 343 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.002834 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4093 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200100 |  | 0 | 3 | 40 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1926 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 186 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0011436 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1926 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200110 |  | 0 | 3 | 40 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2528 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 226 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0029607 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2528 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200150 |  | 0 | 3 | 40 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3136 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 307 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0020611 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3136 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200160 |  | 0 | 3 | 40 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3400 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 293 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.004686 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3400 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200200 |  | 0 | 3 | 40 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4392 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 430 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0027374 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4392 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340200210 |  | 0 | 3 | 40 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4548 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0036299 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 4548 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220100 |  | 0 | 3 | 40 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2119 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 204 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0014597 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2119 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220110 |  | 0 | 3 | 40 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2781 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 248 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0036879 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2781 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220150 |  | 0 | 3 | 40 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3450 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 337 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0024178 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3450 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220160 |  | 0 | 3 | 40 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3740 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 323 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0061644 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 3740 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220200 |  | 0 | 3 | 40 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4831 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 473 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0033497 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4831 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340220210 |  | 0 | 3 | 40 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5003 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 419 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.004546 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 5003 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240100 |  | 0 | 3 | 40 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2311 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 223 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0018252 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2311 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240110 |  | 0 | 3 | 40 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3034 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 271 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.004518 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3034 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240150 |  | 0 | 3 | 40 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3763 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 368 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0031091 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3763 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240160 |  | 0 | 3 | 40 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4080 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 352 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0071103 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4080 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240200 |  | 0 | 3 | 40 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5270 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 516 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0043354 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 5270 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340240210 |  | 0 | 3 | 40 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5458 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 457 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0055883 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 5458 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260100 |  | 0 | 3 | 40 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2504 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 241 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0019411 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2504 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260110 |  | 0 | 3 | 40 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3286 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 294 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0054566 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3286 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260150 |  | 0 | 3 | 40 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4077 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 399 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0039044 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4077 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260160 |  | 0 | 3 | 40 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4420 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0089687 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 4420 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260200 |  | 0 | 3 | 40 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5710 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 559 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.005129 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 5710 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340260210 |  | 0 | 3 | 40 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5912 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 496 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0067624 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 5912 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280100 |  | 0 | 3 | 40 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2696 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0023761 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2696 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280110 |  | 0 | 3 | 40 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3539 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 316 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0065091 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3539 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280150 |  | 0 | 3 | 40 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4390 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 429 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0044267 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4390 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280160 |  | 0 | 3 | 40 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4760 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 411 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.010147 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 4760 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280200 |  | 0 | 3 | 40 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6149 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 602 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0060033 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 6149 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340280210 |  | 0 | 3 | 40 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6367 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 534 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0080738 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 6367 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300100 |  | 0 | 3 | 40 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2889 | 0 | 0 | 0 | 1.394 | 1.08 | 1.08 | 1.08 | 278 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0028672 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2889 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300110 |  | 0 | 3 | 40 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3792 | 0 | 0 | 0 | 1.439 | 1.1 | 1.1 | 1.1 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0076808 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3792 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300150 |  | 0 | 3 | 40 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4704 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 460 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0054007 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 4704 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300160 |  | 0 | 3 | 40 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5100 | 0 | 0 | 0 | 1.46 | 1.1 | 1.1 | 1.1 | 440 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.012413 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 5100 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300200 |  | 0 | 3 | 40 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6588 | 0 | 0 | 0 | 1.384 | 1.08 | 1.08 | 1.08 | 645 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.0069609 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 6588 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
340300210 |  | 0 | 3 | 40 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6822 | 0 | 0 | 0 | 1.477 | 1.05 | 1.05 | 1.05 | 572 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0095281 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 6822 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35050100 |  | 0 | 3 | 50 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 538 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 538 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35050110 |  | 0 | 3 | 50 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 693 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 693 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060100 |  | 0 | 3 | 50 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 646 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 646 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060110 |  | 0 | 3 | 50 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 832 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060150 |  | 0 | 3 | 50 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.000143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1040 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060160 |  | 0 | 3 | 50 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1139 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1139 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060200 |  | 0 | 3 | 50 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 145 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00021338 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1455 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35060210 |  | 0 | 3 | 50 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1549 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031197 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1549 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070100 |  | 0 | 3 | 50 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 753 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070110 |  | 0 | 3 | 50 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 970 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070150 |  | 0 | 3 | 50 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00021277 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1214 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070160 |  | 0 | 3 | 50 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1329 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00059105 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1329 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070200 |  | 0 | 3 | 50 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1698 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00036009 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1698 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35070210 |  | 0 | 3 | 50 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1807 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00042233 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1807 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080100 |  | 0 | 3 | 50 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 861 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 861 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080110 |  | 0 | 3 | 50 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00030716 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1109 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080150 |  | 0 | 3 | 50 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1387 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00029847 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1387 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080160 |  | 0 | 3 | 50 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1518 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00082222 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1518 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080200 |  | 0 | 3 | 50 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1940 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00045556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1940 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35080210 |  | 0 | 3 | 50 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2066 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00055243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2066 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090100 |  | 0 | 3 | 50 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 968 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 968 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090110 |  | 0 | 3 | 50 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1247 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0004658 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1247 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090150 |  | 0 | 3 | 50 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1561 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1561 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090160 |  | 0 | 3 | 50 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1708 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010961 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1708 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090200 |  | 0 | 3 | 50 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2183 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 218 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00056402 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2183 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
35090210 |  | 0 | 3 | 50 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2324 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00070324 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2324 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100100 |  | 0 | 3 | 50 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1076 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100110 |  | 0 | 3 | 50 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1386 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00050061 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1386 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100150 |  | 0 | 3 | 50 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1734 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00052096 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1734 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100160 |  | 0 | 3 | 50 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1898 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011255 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 1898 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100200 |  | 0 | 3 | 50 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2425 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 242 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00068594 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2425 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350100210 |  | 0 | 3 | 50 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2582 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 214 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00087568 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110100 |  | 0 | 3 | 50 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1184 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110110 |  | 0 | 3 | 50 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1525 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 136 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00071062 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1525 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110150 |  | 0 | 3 | 50 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1907 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00065932 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1907 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110160 |  | 0 | 3 | 50 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2088 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014504 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2088 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110200 |  | 0 | 3 | 50 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2668 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 266 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.00094834 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2668 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350110210 |  | 0 | 3 | 50 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2840 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010707 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 2840 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120100 |  | 0 | 3 | 50 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1291 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00041656 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1291 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120110 |  | 0 | 3 | 50 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1663 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 149 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00096572 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1663 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120150 |  | 0 | 3 | 50 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2081 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00081677 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2081 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120160 |  | 0 | 3 | 50 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2278 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0018216 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2278 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120200 |  | 0 | 3 | 50 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2910 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 290 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0011102 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2910 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350120210 |  | 0 | 3 | 50 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3098 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.001289 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3098 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140100 |  | 0 | 3 | 50 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1506 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0005905 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140110 |  | 0 | 3 | 50 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1940 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013393 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 1940 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140150 |  | 0 | 3 | 50 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2428 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 242 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010236 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2428 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140160 |  | 0 | 3 | 50 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2657 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0027093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2657 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140200 |  | 0 | 3 | 50 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3395 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0014795 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3395 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350140210 |  | 0 | 3 | 50 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3615 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 299 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0017995 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3615 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160100 |  | 0 | 3 | 50 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1722 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 168 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00080367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1722 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160110 |  | 0 | 3 | 50 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2218 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 198 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017923 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2218 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160150 |  | 0 | 3 | 50 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2774 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0014495 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2774 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160160 |  | 0 | 3 | 50 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3037 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0032966 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3037 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160200 |  | 0 | 3 | 50 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3880 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 387 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0021095 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3880 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350160210 |  | 0 | 3 | 50 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4131 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 342 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0026889 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4131 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180100 |  | 0 | 3 | 50 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1937 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0010592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1937 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180110 |  | 0 | 3 | 50 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2495 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 223 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002729 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2495 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180150 |  | 0 | 3 | 50 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3121 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 311 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0019638 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3121 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180160 |  | 0 | 3 | 50 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3416 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 293 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.004512 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3416 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180200 |  | 0 | 3 | 50 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4365 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 436 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0026349 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4365 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350180210 |  | 0 | 3 | 50 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4648 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 384 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0034559 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4648 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200100 |  | 0 | 3 | 50 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2152 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0013601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2152 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200110 |  | 0 | 3 | 50 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2772 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 248 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0034217 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2772 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200150 |  | 0 | 3 | 50 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3468 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.002572 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3468 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200160 |  | 0 | 3 | 50 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3796 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 325 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0059484 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 3796 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200200 |  | 0 | 3 | 50 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4850 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 484 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.003492 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 4850 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350200210 |  | 0 | 3 | 50 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5164 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 427 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0043411 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 5164 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220100 |  | 0 | 3 | 50 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2367 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 232 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0017094 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2367 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220110 |  | 0 | 3 | 50 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3049 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 273 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0042153 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3049 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220150 |  | 0 | 3 | 50 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3815 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 381 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0032791 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 3815 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220160 |  | 0 | 3 | 50 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4176 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 358 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.006872 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4176 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220200 |  | 0 | 3 | 50 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5335 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 532 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0041896 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 5335 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350220210 |  | 0 | 3 | 50 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5680 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 470 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0053502 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 5680 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240100 |  | 0 | 3 | 50 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2582 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 253 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0021099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240110 |  | 0 | 3 | 50 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3326 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 298 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0051154 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3326 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240150 |  | 0 | 3 | 50 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4162 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 415 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.003749 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4162 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240160 |  | 0 | 3 | 50 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4555 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 390 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.008683 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 4555 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240200 |  | 0 | 3 | 50 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5820 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 581 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0052937 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 5820 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350240210 |  | 0 | 3 | 50 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6197 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 513 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0064891 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 6197 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260100 |  | 0 | 3 | 50 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2798 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 274 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0025644 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 2798 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260110 |  | 0 | 3 | 50 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3604 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 323 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0068328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3604 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260150 |  | 0 | 3 | 50 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4508 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 450 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0046267 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4508 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260160 |  | 0 | 3 | 50 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4935 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 423 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.010742 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 4935 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260200 |  | 0 | 3 | 50 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6305 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 629 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0.0061785 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 6305 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350260210 |  | 0 | 3 | 50 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6713 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 555 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0082881 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 6713 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280100 |  | 0 | 3 | 50 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3013 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0030758 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3013 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280110 |  | 0 | 3 | 50 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3881 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 347 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0080406 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 3881 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280150 |  | 0 | 3 | 50 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4855 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 485 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0056162 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 4855 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280160 |  | 0 | 3 | 50 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5314 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 455 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.012049 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 5314 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280200 |  | 0 | 3 | 50 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6790 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 678 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.0075486 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 6790 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350280210 |  | 0 | 3 | 50 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7230 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 598 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0097556 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 7230 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300100 |  | 0 | 3 | 50 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3228 | 0 | 0 | 0 | 1.385 | 1.08 | 1.08 | 1.08 | 316 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0036466 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3228 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300110 |  | 0 | 3 | 50 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4158 | 0 | 0 | 0 | 1.438 | 1.1 | 1.1 | 1.1 | 372 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0093743 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4158 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300150 |  | 0 | 3 | 50 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5202 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 519 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0067221 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 5202 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300160 |  | 0 | 3 | 50 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5694 | 0 | 0 | 0 | 1.464 | 1.1 | 1.1 | 1.1 | 488 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.014526 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 5694 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300200 |  | 0 | 3 | 50 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7275 | 0 | 0 | 0 | 1.373 | 1.08 | 1.08 | 1.08 | 726 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0.0086349 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 7275 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
350300210 |  | 0 | 3 | 50 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7746 | 0 | 0 | 0 | 1.485 | 1.05 | 1.05 | 1.05 | 641 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.011371 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 7746 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36050100 |  | 0 | 3 | 60 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 585 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 585 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36050110 |  | 0 | 3 | 60 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 747 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7894e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 747 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060100 |  | 0 | 3 | 60 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 702 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.6886e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 702 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060110 |  | 0 | 3 | 60 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 896 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 896 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060150 |  | 0 | 3 | 60 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00020381 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1120 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060160 |  | 0 | 3 | 60 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1250 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1250 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060200 |  | 0 | 3 | 60 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1565 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00027715 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1565 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36060210 |  | 0 | 3 | 60 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1729 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00031197 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1729 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070100 |  | 0 | 3 | 60 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 819 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 81 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 819 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070110 |  | 0 | 3 | 60 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1046 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00028178 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1046 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070150 |  | 0 | 3 | 60 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1306 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00028678 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1306 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070160 |  | 0 | 3 | 60 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1459 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00059105 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1459 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070200 |  | 0 | 3 | 60 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1826 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 186 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00044237 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1826 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36070210 |  | 0 | 3 | 60 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2017 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 165 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053044 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2017 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080100 |  | 0 | 3 | 60 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 936 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 936 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080110 |  | 0 | 3 | 60 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00043099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1195 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080150 |  | 0 | 3 | 60 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1493 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00038621 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1493 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080160 |  | 0 | 3 | 60 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1667 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 142 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00082222 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1667 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080200 |  | 0 | 3 | 60 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2086 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00054849 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2086 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36080210 |  | 0 | 3 | 60 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2306 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 188 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00067687 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2306 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090100 |  | 0 | 3 | 60 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1053 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1053 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090110 |  | 0 | 3 | 60 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1345 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0004658 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1345 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090150 |  | 0 | 3 | 60 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1679 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00050293 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1679 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090160 |  | 0 | 3 | 60 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1876 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010961 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 1876 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090200 |  | 0 | 3 | 60 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2347 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 239 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00066789 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2347 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
36090210 |  | 0 | 3 | 60 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2594 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00084461 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2594 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100100 |  | 0 | 3 | 60 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1170 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100110 |  | 0 | 3 | 60 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1494 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00066513 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1494 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100150 |  | 0 | 3 | 60 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1866 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0006377 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1866 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100160 |  | 0 | 3 | 60 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2084 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 177 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0014143 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2084 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100200 |  | 0 | 3 | 60 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2608 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 266 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.00092481 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2608 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360100210 |  | 0 | 3 | 60 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2882 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 235 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0010346 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2882 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110100 |  | 0 | 3 | 60 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1287 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00039382 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1287 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110110 |  | 0 | 3 | 60 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1643 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00090838 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1643 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110150 |  | 0 | 3 | 60 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2053 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 209 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00079129 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2053 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110160 |  | 0 | 3 | 60 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2292 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017784 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2292 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110200 |  | 0 | 3 | 60 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2869 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 292 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0010838 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2869 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360110210 |  | 0 | 3 | 60 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3170 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 259 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012476 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3170 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120100 |  | 0 | 3 | 60 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1404 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00041656 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1404 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120110 |  | 0 | 3 | 60 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1793 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 161 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00096572 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1793 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120150 |  | 0 | 3 | 60 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2239 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00096443 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2239 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120160 |  | 0 | 3 | 60 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2501 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2501 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120200 |  | 0 | 3 | 60 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3130 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 319 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0012576 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3130 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360120210 |  | 0 | 3 | 60 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3458 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 282 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0016935 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3458 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140100 |  | 0 | 3 | 60 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1638 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0005905 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1638 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140110 |  | 0 | 3 | 60 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2092 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 188 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016234 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2092 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140150 |  | 0 | 3 | 60 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2612 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 266 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0013722 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2612 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140160 |  | 0 | 3 | 60 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2918 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 248 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0031606 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 2918 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140200 |  | 0 | 3 | 60 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3651 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 372 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0018324 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3651 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360140210 |  | 0 | 3 | 60 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4035 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 329 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.002282 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4035 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160100 |  | 0 | 3 | 60 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1872 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 186 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00097475 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1872 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160110 |  | 0 | 3 | 60 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2390 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 214 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021315 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2390 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160150 |  | 0 | 3 | 60 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2986 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 304 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0018666 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2986 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160160 |  | 0 | 3 | 60 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3334 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 284 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0043379 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3334 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160200 |  | 0 | 3 | 60 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4173 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 425 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0025324 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 4173 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360160210 |  | 0 | 3 | 60 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4611 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 376 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0029784 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 4611 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180100 |  | 0 | 3 | 60 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2106 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 209 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0012605 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2106 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180110 |  | 0 | 3 | 60 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2689 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 241 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002729 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2689 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180150 |  | 0 | 3 | 60 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3359 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 342 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0024529 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3359 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180160 |  | 0 | 3 | 60 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3751 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 319 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0051047 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 3751 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180200 |  | 0 | 3 | 60 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4694 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 478 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0033642 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4694 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360180210 |  | 0 | 3 | 60 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5188 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 423 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0041361 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5188 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200100 |  | 0 | 3 | 60 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2340 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 232 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0015935 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2340 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200110 |  | 0 | 3 | 60 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2988 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 268 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0039125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 2988 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200150 |  | 0 | 3 | 60 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3732 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 380 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0031362 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3732 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200160 |  | 0 | 3 | 60 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4168 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 355 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0066337 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4168 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200200 |  | 0 | 3 | 60 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5216 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 531 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0040437 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 5216 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360200210 |  | 0 | 3 | 60 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5764 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 470 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0051121 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 5764 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220100 |  | 0 | 3 | 60 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2574 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0019768 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2574 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220110 |  | 0 | 3 | 60 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3287 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0047741 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3287 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220150 |  | 0 | 3 | 60 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4105 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 418 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0039216 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 4105 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220160 |  | 0 | 3 | 60 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4585 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 390 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0083972 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4585 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220200 |  | 0 | 3 | 60 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5738 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 584 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0051189 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 5738 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360220210 |  | 0 | 3 | 60 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6340 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 517 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0066715 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 6340 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240100 |  | 0 | 3 | 60 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2808 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 279 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0024131 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2808 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240110 |  | 0 | 3 | 60 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3586 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 321 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0064089 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3586 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240150 |  | 0 | 3 | 60 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4478 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 456 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0048138 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4478 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240160 |  | 0 | 3 | 60 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5002 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 426 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.010405 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5002 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240200 |  | 0 | 3 | 60 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6259 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 637 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.0063429 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 6259 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360240210 |  | 0 | 3 | 60 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6917 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 564 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0079583 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 6917 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260100 |  | 0 | 3 | 60 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3042 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 302 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0032649 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 3042 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260110 |  | 0 | 3 | 60 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3884 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 348 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0075725 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 3884 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260150 |  | 0 | 3 | 60 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4852 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 494 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0054063 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 4852 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260160 |  | 0 | 3 | 60 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5418 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 461 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.012667 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 5418 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260200 |  | 0 | 3 | 60 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6781 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 691 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.0077218 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 6781 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360260210 |  | 0 | 3 | 60 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7493 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 611 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0.0099584 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 7493 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280100 |  | 0 | 3 | 60 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3276 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 325 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0038556 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3276 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280110 |  | 0 | 3 | 60 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4183 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 375 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0088602 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4183 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280150 |  | 0 | 3 | 60 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5225 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 532 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0064825 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 5225 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280160 |  | 0 | 3 | 60 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5835 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.015192 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 5835 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280200 |  | 0 | 3 | 60 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7302 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 744 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0.0088174 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 7302 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360280210 |  | 0 | 3 | 60 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8070 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 658 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0.011585 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 8070 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300100 |  | 0 | 3 | 60 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3510 | 0 | 0 | 0 | 1.376 | 1.08 | 1.08 | 1.08 | 349 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0045091 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3510 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300110 |  | 0 | 3 | 60 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4482 | 0 | 0 | 0 | 1.437 | 1.1 | 1.1 | 1.1 | 402 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.011217 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4482 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300150 |  | 0 | 3 | 60 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5598 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 570 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0076778 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 5598 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300160 |  | 0 | 3 | 60 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6252 | 0 | 0 | 0 | 1.468 | 1.1 | 1.1 | 1.1 | 532 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.016796 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6252 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300200 |  | 0 | 3 | 60 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7824 | 0 | 0 | 0 | 1.361 | 1.08 | 1.08 | 1.08 | 797 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0.010479 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 7824 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360300210 |  | 0 | 3 | 60 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8646 | 0 | 0 | 0 | 1.493 | 1.05 | 1.05 | 1.05 | 706 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.013365 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 8646 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37050100 |  | 0 | 3 | 70 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 624 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 624 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37050110 |  | 0 | 3 | 70 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00015139 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 795 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060100 |  | 0 | 3 | 70 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 749 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.6886e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 749 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060110 |  | 0 | 3 | 70 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016862 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 954 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060150 |  | 0 | 3 | 70 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1183 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00020381 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1183 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060160 |  | 0 | 3 | 70 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1356 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057313 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1356 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060200 |  | 0 | 3 | 70 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1652 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00034909 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1652 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37060210 |  | 0 | 3 | 70 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 1906 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1906 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070100 |  | 0 | 3 | 70 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 874 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016054 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 874 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070110 |  | 0 | 3 | 70 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00028178 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1113 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070150 |  | 0 | 3 | 70 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1380 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00028678 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1380 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070160 |  | 0 | 3 | 70 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1582 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00079884 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070200 |  | 0 | 3 | 70 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1927 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00044237 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1927 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37070210 |  | 0 | 3 | 70 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2224 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00053044 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2224 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080100 |  | 0 | 3 | 70 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 998 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 998 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080110 |  | 0 | 3 | 70 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1272 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00043099 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1272 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080150 |  | 0 | 3 | 70 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1578 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 164 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00038621 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1578 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080160 |  | 0 | 3 | 70 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1808 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010667 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1808 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080200 |  | 0 | 3 | 70 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2202 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00064985 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2202 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37080210 |  | 0 | 3 | 70 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2542 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00081354 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2542 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090100 |  | 0 | 3 | 70 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1123 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 113 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1123 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090110 |  | 0 | 3 | 70 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1431 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00061964 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1431 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090150 |  | 0 | 3 | 70 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1775 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00050293 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1775 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090160 |  | 0 | 3 | 70 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2034 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013783 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2034 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090200 |  | 0 | 3 | 70 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2478 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 257 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00078032 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2478 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
37090210 |  | 0 | 3 | 70 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2859 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 230 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00099848 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2859 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100100 |  | 0 | 3 | 70 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1248 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1248 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100110 |  | 0 | 3 | 70 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1590 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00066513 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1590 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100150 |  | 0 | 3 | 70 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1972 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 205 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0007658 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1972 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100160 |  | 0 | 3 | 70 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2260 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 191 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0017352 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2260 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100200 |  | 0 | 3 | 70 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2753 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 286 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0010573 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2753 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370100210 |  | 0 | 3 | 70 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3177 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0012062 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3177 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110100 |  | 0 | 3 | 70 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1373 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00039382 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1373 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110110 |  | 0 | 3 | 70 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1749 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00090838 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1749 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110150 |  | 0 | 3 | 70 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2169 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 225 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00093481 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2169 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110160 |  | 0 | 3 | 70 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2486 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0021389 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2486 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110200 |  | 0 | 3 | 70 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3028 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 315 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0012279 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 3028 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370110210 |  | 0 | 3 | 70 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3495 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 281 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0014376 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3495 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120100 |  | 0 | 3 | 70 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1498 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 151 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00053316 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1498 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120110 |  | 0 | 3 | 70 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1908 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 1908 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120150 |  | 0 | 3 | 70 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2366 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 245 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0011238 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2366 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120160 |  | 0 | 3 | 70 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2712 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0025909 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2712 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120200 |  | 0 | 3 | 70 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3304 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 343 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0015788 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3304 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370120210 |  | 0 | 3 | 70 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3812 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 307 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0019155 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3812 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140100 |  | 0 | 3 | 70 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1747 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 176 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00073333 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1747 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140110 |  | 0 | 3 | 70 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2226 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016234 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2226 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140150 |  | 0 | 3 | 70 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2761 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 286 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0015647 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2761 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140160 |  | 0 | 3 | 70 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3164 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 267 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0036455 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3164 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140200 |  | 0 | 3 | 70 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3854 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 400 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0022217 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3854 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370140210 |  | 0 | 3 | 70 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4448 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 358 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0025438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4448 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160100 |  | 0 | 3 | 70 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1997 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 202 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00097475 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1997 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160110 |  | 0 | 3 | 70 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2544 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0024973 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2544 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160150 |  | 0 | 3 | 70 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3155 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 327 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.002094 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3155 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160160 |  | 0 | 3 | 70 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3616 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 306 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0049102 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3616 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160200 |  | 0 | 3 | 70 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4405 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 458 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0029926 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 4405 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370160210 |  | 0 | 3 | 70 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5083 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 409 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0035996 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 5083 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180100 |  | 0 | 3 | 70 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2246 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 227 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0014777 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2246 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180110 |  | 0 | 3 | 70 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2862 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 257 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0031555 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 2862 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180150 |  | 0 | 3 | 70 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3550 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 368 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0027167 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3550 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180160 |  | 0 | 3 | 70 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4068 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 344 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0063954 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 4068 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180200 |  | 0 | 3 | 70 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4955 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 515 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0038979 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4955 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370180210 |  | 0 | 3 | 70 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5719 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 460 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.004874 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5719 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200100 |  | 0 | 3 | 70 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2496 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 252 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0018437 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2496 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200110 |  | 0 | 3 | 70 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3180 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 286 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0044329 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3180 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200150 |  | 0 | 3 | 70 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3944 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 409 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0034381 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3944 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200160 |  | 0 | 3 | 70 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4520 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 382 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0081115 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4520 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200200 |  | 0 | 3 | 70 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5506 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 572 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.004944 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 5506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370200210 |  | 0 | 3 | 70 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6354 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 512 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0059425 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 6354 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220100 |  | 0 | 3 | 70 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2746 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 277 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0022617 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 2746 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220110 |  | 0 | 3 | 70 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3498 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 314 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0053641 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3498 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220150 |  | 0 | 3 | 70 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4338 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 450 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0042631 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 4338 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220160 |  | 0 | 3 | 70 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4972 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 420 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.010068 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 4972 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220200 |  | 0 | 3 | 70 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6057 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 629 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0.0057878 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 6057 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370220210 |  | 0 | 3 | 70 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6989 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 563 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.0076284 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 6989 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240100 |  | 0 | 3 | 70 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2995 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 302 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0030741 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2995 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240110 |  | 0 | 3 | 70 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3816 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 343 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0071043 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 3816 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240150 |  | 0 | 3 | 70 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4733 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 491 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.0051964 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 4733 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240160 |  | 0 | 3 | 70 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5424 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 458 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.012276 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 5424 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240200 |  | 0 | 3 | 70 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6607 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 687 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.0070927 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 6607 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370240210 |  | 0 | 3 | 70 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7625 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 614 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0.0095676 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 7625 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260100 |  | 0 | 3 | 70 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3245 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 328 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0036436 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 3245 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260110 |  | 0 | 3 | 70 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4134 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 371 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.008346 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 4134 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260150 |  | 0 | 3 | 70 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5127 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 532 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0062428 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 5127 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260160 |  | 0 | 3 | 70 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5876 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 497 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.014743 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 5876 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260200 |  | 0 | 3 | 70 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7158 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 744 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0.0085548 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 7158 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370260210 |  | 0 | 3 | 70 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8260 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 665 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0.011151 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 8260 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280100 |  | 0 | 3 | 70 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3494 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 353 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.004275 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3494 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280110 |  | 0 | 3 | 70 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4452 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 400 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.010605 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4452 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280150 |  | 0 | 3 | 70 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5522 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 573 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0078904 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 5522 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280160 |  | 0 | 3 | 70 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6328 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 535 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.017479 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 6328 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280200 |  | 0 | 3 | 70 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7708 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 801 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0.01018 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 7708 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370280210 |  | 0 | 3 | 70 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8896 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 716 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0.013561 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 8896 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300100 |  | 0 | 3 | 70 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3744 | 0 | 0 | 0 | 1.366 | 1.08 | 1.08 | 1.08 | 378 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0054529 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3744 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300110 |  | 0 | 3 | 70 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4770 | 0 | 0 | 0 | 1.436 | 1.1 | 1.1 | 1.1 | 428 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.012193 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4770 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300150 |  | 0 | 3 | 70 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5916 | 0 | 0 | 0 | 1.35 | 1.08 | 1.08 | 1.08 | 614 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0.0092221 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 5916 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300160 |  | 0 | 3 | 70 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6780 | 0 | 0 | 0 | 1.472 | 1.1 | 1.1 | 1.1 | 573 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.020493 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6780 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300200 |  | 0 | 3 | 70 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 8259 | 0 | 0 | 0 | 1.349 | 1.08 | 1.08 | 1.08 | 858 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0.011973 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 8259 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
370300210 |  | 0 | 3 | 70 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 9531 | 0 | 0 | 0 | 1.501 | 1.05 | 1.05 | 1.05 | 767 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0.016256 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 9531 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39050100 |  | 0 | 3 | 90 | 50 | 10 | 11.5 | 0 | 0 | 0 | 0 | 685 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 8.827e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 |  | 685 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39050110 |  | 0 | 3 | 90 | 50 | 11 | 11.5 | 0 | 0 | 0 | 0 | 879 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00015139 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 879 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060100 |  | 0 | 3 | 90 | 60 | 10 | 11.5 | 0 | 0 | 0 | 0 | 821 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.6886e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 |  | 821 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060110 |  | 0 | 3 | 90 | 60 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00025641 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1055 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060150 |  | 0 | 3 | 90 | 60 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1272 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 137 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00027509 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1272 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060160 |  | 0 | 3 | 90 | 60 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1558 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00077545 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1558 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060200 |  | 0 | 3 | 90 | 60 | 20 | 21.5 | 0 | 0 | 0 | 0 | 1774 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00042919 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1774 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39060210 |  | 0 | 3 | 90 | 60 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2262 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 177 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00050845 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2262 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070100 |  | 0 | 3 | 90 | 70 | 10 | 11.5 | 0 | 0 | 0 | 0 | 958 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016054 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 958 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070110 |  | 0 | 3 | 90 | 70 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00039617 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1231 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070150 |  | 0 | 3 | 90 | 70 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1484 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0003715 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1484 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070160 |  | 0 | 3 | 90 | 70 | 16 | 16.5 | 0 | 0 | 0 | 0 | 1817 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0010372 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 1817 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070200 |  | 0 | 3 | 90 | 70 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2070 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 224 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0006318 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 2070 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39070210 |  | 0 | 3 | 90 | 70 | 21 | 21.5 | 0 | 0 | 0 | 0 | 2639 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 206 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00078248 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2639 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080100 |  | 0 | 3 | 90 | 80 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00024379 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 |  | 1095 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080110 |  | 0 | 3 | 90 | 80 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1406 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 127 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00057416 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 1406 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080150 |  | 0 | 3 | 90 | 80 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1696 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 183 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00048489 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1696 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080160 |  | 0 | 3 | 90 | 80 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2077 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 173 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0013422 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2077 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080200 |  | 0 | 3 | 90 | 80 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2366 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.00075961 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2366 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39080210 |  | 0 | 3 | 90 | 80 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3016 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 236 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.00096239 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 3016 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090100 |  | 0 | 3 | 90 | 90 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 128 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00034834 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 |  | 1232 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090110 |  | 0 | 3 | 90 | 90 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1582 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 143 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00061964 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 1582 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090150 |  | 0 | 3 | 90 | 90 | 15 | 16.5 | 0 | 0 | 0 | 0 | 1908 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 206 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.00074031 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1908 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090160 |  | 0 | 3 | 90 | 90 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2336 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0016919 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 2336 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090200 |  | 0 | 3 | 90 | 90 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2661 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 287 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0010308 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2661 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
39090210 |  | 0 | 3 | 90 | 90 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3393 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 265 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0013435 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3393 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100100 |  | 0 | 3 | 90 | 100 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1369 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 142 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1369 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100110 |  | 0 | 3 | 90 | 100 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1758 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00085103 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 1758 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100150 |  | 0 | 3 | 90 | 100 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2120 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0009052 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 2120 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100160 |  | 0 | 3 | 90 | 100 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2596 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 217 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0020879 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2596 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100200 |  | 0 | 3 | 90 | 100 | 20 | 21.5 | 0 | 0 | 0 | 0 | 2957 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 319 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0011983 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2957 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390100210 |  | 0 | 3 | 90 | 100 | 21 | 21.5 | 0 | 0 | 0 | 0 | 3770 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 295 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0015875 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3770 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110100 |  | 0 | 3 | 90 | 110 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1506 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050449 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 |  | 1506 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110110 |  | 0 | 3 | 90 | 110 | 11 | 11.5 | 0 | 0 | 0 | 0 | 1934 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011283 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 1934 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110150 |  | 0 | 3 | 90 | 110 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2332 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 252 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0010898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2332 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110160 |  | 0 | 3 | 90 | 110 | 16 | 16.5 | 0 | 0 | 0 | 0 | 2856 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 238 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0025317 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 2856 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110200 |  | 0 | 3 | 90 | 110 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3253 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 351 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0015426 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 3253 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390110210 |  | 0 | 3 | 90 | 110 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4147 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 324 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0020848 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 4147 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120100 |  | 0 | 3 | 90 | 120 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1643 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 171 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00066299 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 1643 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120110 |  | 0 | 3 | 90 | 120 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2110 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014545 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 2110 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120150 |  | 0 | 3 | 90 | 120 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2544 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 275 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.001295 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2544 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120160 |  | 0 | 3 | 90 | 120 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3115 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 260 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0030247 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3115 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120200 |  | 0 | 3 | 90 | 120 | 20 | 21.5 | 0 | 0 | 0 | 0 | 3548 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 383 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0019355 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3548 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390120210 |  | 0 | 3 | 90 | 120 | 21 | 21.5 | 0 | 0 | 0 | 0 | 4524 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 354 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0023987 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4524 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140100 |  | 0 | 3 | 90 | 140 | 10 | 11.5 | 0 | 0 | 0 | 0 | 1917 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.00089031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 1917 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140110 |  | 0 | 3 | 90 | 140 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2461 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 222 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0019323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 2461 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140150 |  | 0 | 3 | 90 | 140 | 15 | 16.5 | 0 | 0 | 0 | 0 | 2968 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 321 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.001986 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 |  | 2968 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140160 |  | 0 | 3 | 90 | 140 | 16 | 16.5 | 0 | 0 | 0 | 0 | 3634 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 303 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0047157 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 3634 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140200 |  | 0 | 3 | 90 | 140 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4140 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 447 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.0026472 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 4140 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390140210 |  | 0 | 3 | 90 | 140 | 21 | 21.5 | 0 | 0 | 0 | 0 | 5278 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 413 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0034104 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 5278 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160100 |  | 0 | 3 | 90 | 160 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2190 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0013618 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 |  | 2190 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160110 |  | 0 | 3 | 90 | 160 | 11 | 11.5 | 0 | 0 | 0 | 0 | 2813 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 253 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0028892 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 2813 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160150 |  | 0 | 3 | 90 | 160 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3392 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 366 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0025859 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3392 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160160 |  | 0 | 3 | 90 | 160 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4154 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 346 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0061571 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4154 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160200 |  | 0 | 3 | 90 | 160 | 20 | 21.5 | 0 | 0 | 0 | 0 | 4731 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 511 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0034897 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 |  | 4731 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390160210 |  | 0 | 3 | 90 | 160 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6032 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 472 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0046359 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 |  | 6032 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180100 |  | 0 | 3 | 90 | 180 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2464 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 256 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0017106 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 |  | 2464 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180110 |  | 0 | 3 | 90 | 180 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3164 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 285 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0040917 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 3164 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180150 |  | 0 | 3 | 90 | 180 | 15 | 16.5 | 0 | 0 | 0 | 0 | 3816 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 412 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0032827 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 |  | 3816 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180160 |  | 0 | 3 | 90 | 180 | 16 | 16.5 | 0 | 0 | 0 | 0 | 4673 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 390 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0078257 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 |  | 4673 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180200 |  | 0 | 3 | 90 | 180 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5323 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 575 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0047692 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 5323 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390180210 |  | 0 | 3 | 90 | 180 | 21 | 21.5 | 0 | 0 | 0 | 0 | 6786 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 531 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.0060883 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 6786 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200100 |  | 0 | 3 | 90 | 200 | 10 | 11.5 | 0 | 0 | 0 | 0 | 2738 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 285 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0023933 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 |  | 2738 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200110 |  | 0 | 3 | 90 | 200 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3516 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 317 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0049825 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 3516 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200150 |  | 0 | 3 | 90 | 200 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4240 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 458 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.0044225 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 4240 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200160 |  | 0 | 3 | 90 | 200 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5192 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 433 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0097316 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 5192 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200200 |  | 0 | 3 | 90 | 200 | 20 | 21.5 | 0 | 0 | 0 | 0 | 5914 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 639 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.0059309 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 |  | 5914 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390200210 |  | 0 | 3 | 90 | 200 | 21 | 21.5 | 0 | 0 | 0 | 0 | 7540 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 590 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0.0077799 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 |  | 7540 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220100 |  | 0 | 3 | 90 | 220 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3012 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0028833 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 |  | 3012 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220110 |  | 0 | 3 | 90 | 220 | 11 | 11.5 | 0 | 0 | 0 | 0 | 3868 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 348 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0066361 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 3868 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220150 |  | 0 | 3 | 90 | 220 | 15 | 16.5 | 0 | 0 | 0 | 0 | 4664 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 504 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.0053683 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 |  | 4664 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220160 |  | 0 | 3 | 90 | 220 | 16 | 16.5 | 0 | 0 | 0 | 0 | 5711 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 476 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.012847 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 |  | 5711 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220200 |  | 0 | 3 | 90 | 220 | 20 | 21.5 | 0 | 0 | 0 | 0 | 6505 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 703 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0.0072432 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 |  | 6505 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390220210 |  | 0 | 3 | 90 | 220 | 21 | 21.5 | 0 | 0 | 0 | 0 | 8294 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 649 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.009723 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 |  | 8294 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240100 |  | 0 | 3 | 90 | 240 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3286 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 342 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0.0038068 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 |  | 3286 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240110 |  | 0 | 3 | 90 | 240 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4219 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 380 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.008591 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 4219 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240150 |  | 0 | 3 | 90 | 240 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5088 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 549 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0.0064269 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 |  | 5088 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240160 |  | 0 | 3 | 90 | 240 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6230 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 520 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0.015358 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 0 | 0 |  | 6230 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240200 |  | 0 | 3 | 90 | 240 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7097 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 766 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0.0091414 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 |  | 7097 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390240210 |  | 0 | 3 | 90 | 240 | 21 | 21.5 | 0 | 0 | 0 | 0 | 9048 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 708 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0.012558 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 |  | 9048 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260100 |  | 0 | 3 | 90 | 260 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3559 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 370 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0044567 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 |  | 3559 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260110 |  | 0 | 3 | 90 | 260 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4571 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 412 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0099933 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 4571 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260150 |  | 0 | 3 | 90 | 260 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5512 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 595 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.0080843 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 |  | 5512 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260160 |  | 0 | 3 | 90 | 260 | 16 | 16.5 | 0 | 0 | 0 | 0 | 6750 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 563 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0.018138 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 |  | 6750 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260200 |  | 0 | 3 | 90 | 260 | 20 | 21.5 | 0 | 0 | 0 | 0 | 7688 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 830 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0.010815 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 |  | 7688 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390260210 |  | 0 | 3 | 90 | 260 | 21 | 21.5 | 0 | 0 | 0 | 0 | 9802 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 767 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0.015109 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 |  | 9802 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280100 |  | 0 | 3 | 90 | 280 | 10 | 11.5 | 0 | 0 | 0 | 0 | 3833 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 399 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0.0056491 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 |  | 3833 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280110 |  | 0 | 3 | 90 | 280 | 11 | 11.5 | 0 | 0 | 0 | 0 | 4922 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 443 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0.012489 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 4922 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280150 |  | 0 | 3 | 90 | 280 | 15 | 16.5 | 0 | 0 | 0 | 0 | 5936 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 641 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0.0094275 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 |  | 5936 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280160 |  | 0 | 3 | 90 | 280 | 16 | 16.5 | 0 | 0 | 0 | 0 | 7269 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 606 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0.021195 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 |  | 7269 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280200 |  | 0 | 3 | 90 | 280 | 20 | 21.5 | 0 | 0 | 0 | 0 | 8280 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 894 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0.012656 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 |  | 8280 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390280210 |  | 0 | 3 | 90 | 280 | 21 | 21.5 | 0 | 0 | 0 | 0 | 10556 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 826 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0.017948 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 |  | 10556 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300100 |  | 0 | 3 | 90 | 300 | 10 | 11.5 | 0 | 0 | 0 | 0 | 4107 | 0 | 0 | 0 | 1.348 | 1.08 | 1.08 | 1.08 | 427 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0064768 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 4107 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300110 |  | 0 | 3 | 90 | 300 | 11 | 11.5 | 0 | 0 | 0 | 0 | 5274 | 0 | 0 | 0 | 1.434 | 1.1 | 1.1 | 1.1 | 475 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0.015337 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 5274 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300150 |  | 0 | 3 | 90 | 300 | 15 | 16.5 | 0 | 0 | 0 | 0 | 6360 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 687 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.010898 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 6360 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300160 |  | 0 | 3 | 90 | 300 | 16 | 16.5 | 0 | 0 | 0 | 0 | 7788 | 0 | 0 | 0 | 1.48 | 1.1 | 1.1 | 1.1 | 650 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0.025965 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 7788 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300200 |  | 0 | 3 | 90 | 300 | 20 | 21.5 | 0 | 0 | 0 | 0 | 8871 | 0 | 0 | 0 | 1.326 | 1.08 | 1.08 | 1.08 | 958 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0.014672 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 8871 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
390300210 |  | 0 | 3 | 90 | 300 | 21 | 21.5 | 0 | 0 | 0 | 0 | 11310 | 0 | 0 | 0 | 1.518 | 1.05 | 1.05 | 1.05 | 885 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0.021086 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 11310 |  | 100% |  |  | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Rail-uitzondering
135501010 | 80 | 10 | 1 | 35 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 404.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 33 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 449 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135501110 | 80 | 10 | 1 | 35 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 406.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 33 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 598 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135601010 | 80 | 10 | 1 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 485.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 539 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135601110 | 80 | 10 | 1 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 488.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 718 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135601510 | 80 | 10 | 1 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 705.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 882 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135601610 | 80 | 10 | 1 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 650.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 956 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135602010 | 80 | 10 | 1 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 988.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1236 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135602110 | 80 | 10 | 1 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1014.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1268 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135701010 | 80 | 10 | 1 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 566.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 629 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0
135701110 | 80 | 10 | 1 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 569.16 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 837 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  | CF,Regime,Dynamic,HEAT | CF,Regime,Static,HEAT | CF,Regime,Dynamic,COOL | CF,Regime,Static,COOL |  | 0
135701510 | 70 | 10 | 1 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 823.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 66 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.5819e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | 146 | 156 | 207 | 31 | 34 | 45 | 0.0051949 | 0.0062235 | 0.010773 | 0.7 | 6 | 6.7 | 9 |  | 1029 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 146 | 156 | 207 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 10
135701610 | 70 | 10 | 1 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 758.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 61 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 0.00015302 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 243 | 261 | 345 | 52 | 56 | 74 | 0.041033 | 0.047492 | 0.082323 | 1.4 | 6 | 6.7 | 9 |  | 1115 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 243 | 261 | 345 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 10
135702010 | 70 | 10 | 1 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1153.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 93 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011449 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 148 | 158 | 189 | 32 | 34 | 41 | 0.0043225 | 0.0048694 | 0.0070364 | 0.9 | 6 | 6.7 | 9 |  | 1442 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 189 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | CF,F2 | CF,F1 | [6 empty] | 10
135702110 | 70 | 10 | 1 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1184 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 95 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017042 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | 224 | 240 | 318 | 48 | 52 | 68 | 0.013794 | 0.016132 | 0.027279 | 1.9 | 6 | 6.7 | 9 |  | 1480 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224 | 240 | 318 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 10
135801010 | 80 | 10 | 1 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 646.2 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 52 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 133 | 143 | 172 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 718 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 133 | 143 | 172 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135801110 | 80 | 10 | 1 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 650.76 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219 | 236 | 284 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 957 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219 | 236 | 284 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135801510 | 80 | 10 | 1 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 940.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 76 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00010164 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | 172 | 184 | 247 | 37 | 40 | 53 | 0.0075494 | 0.0087896 | 0.015228 | 0.8 | 6 | 6.7 | 9 |  | 1176 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 172 | 184 | 247 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135801610 | 80 | 10 | 1 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 866.32 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 70 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 286 | 306 | 411 | 61 | 66 | 88 | 0.057198 | 0.066798 | 0.11776 | 1.6 | 6 | 6.7 | 9 |  | 1274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 286 | 306 | 411 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135802010 | 80 | 10 | 1 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1318.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 106 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011849 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 174 | 187 | 226 | 37 | 40 | 49 | 0.0058755 | 0.0068463 | 0.010196 | 1.1 | 6 | 6.7 | 9 |  | 1648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174 | 187 | 226 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
135802110 | 80 | 10 | 1 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1352.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 109 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025318 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | 263 | 282 | 379 | 57 | 61 | 81 | 0.019835 | 0.022643 | 0.039404 | 2.1 | 6 | 6.7 | 9 |  | 1691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 263 | 282 | 379 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135901010 | 80 | 10 | 1 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 727.2 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 205 | 220 | 266 | 3 | 11 | 11 | 14 | 7.1943e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 132 | 141 | 172 | 28 | 30 | 37 | 0.0047265 | 0.0053862 | 0.0080163 | 0.6 | 6 | 6.7 | 9 |  | 808 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132 | 141 | 172 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
135901110 | 80 | 10 | 1 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 731.68 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 276 | 295 | 355 | 3 | 14 | 15 | 18 | 0.00012974 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 217 | 234 | 284 | 47 | 50 | 61 | 0.021784 | 0.024482 | 0.035642 | 1.2 | 6 | 6.7 | 9 |  | 1076 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217 | 234 | 284 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
135901510 | 80 | 10 | 1 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1058.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 85 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.0001061 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | 169 | 181 | 247 | 36 | 39 | 53 | 0.0073534 | 0.0085918 | 0.015611 | 0.9 | 6 | 6.7 | 9 |  | 1323 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 169 | 181 | 247 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135901610 | 80 | 10 | 1 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 975.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 79 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00028576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 282 | 302 | 411 | 61 | 65 | 88 | 0.058175 | 0.065909 | 0.11959 | 1.8 | 6 | 6.7 | 9 |  | 1434 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282 | 302 | 411 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135902010 | 80 | 10 | 1 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1483.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 120 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00017422 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | 172 | 185 | 226 | 37 | 40 | 49 | 0.0060009 | 0.0069897 | 0.0104 | 1.2 | 6 | 6.7 | 9 |  | 1854 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 172 | 185 | 226 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
135902110 | 80 | 10 | 1 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1522.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00026412 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | 260 | 278 | 379 | 56 | 60 | 81 | 0.019674 | 0.022501 | 0.040371 | 2.4 | 6 | 6.7 | 9 |  | 1903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 260 | 278 | 379 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351001010 | 80 | 10 | 1 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 808.2 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 65 | 212 | 227 | 275 | 3 | 11 | 12 | 14 | 7.7174e-05 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 898 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351001110 | 80 | 10 | 1 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 813.28 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 66 | 291 | 311 | 374 | 3 | 15 | 16 | 19 | 0.0001402 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1196 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351001510 | 80 | 10 | 1 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1176 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 95 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1470 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351001610 | 80 | 10 | 1 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1083.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 87 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00029467 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1593 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351002010 | 80 | 10 | 1 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1648 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 133 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00024191 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2060 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351002110 | 80 | 10 | 1 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 1691.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 136 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036904 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2114 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351101010 | 80 | 10 | 1 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 889.2 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 222 | 237 | 284 | 4 | 11 | 12 | 15 | 0.00013996 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 988 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351101110 | 80 | 10 | 1 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 894.88 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1316 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351101510 | 70 | 10 | 1 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1293.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 104 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017573 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1617 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1351101610 | 70 | 10 | 1 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1191.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00046639 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 1752 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1351102010 | 70 | 10 | 1 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1812.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 146 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00032203 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2266 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1351102110 | 70 | 10 | 1 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 1860 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00049415 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2325 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1351201010 | 80 | 10 | 1 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 970.2 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 227 | 243 | 293 | 4 | 12 | 13 | 15 | 0.00014858 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1078 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351201110 | 80 | 10 | 1 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 975.8 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 324 | 344 | 410 | 4 | 17 | 18 | 21 | 0.000272 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1435 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351201510 | 80 | 10 | 1 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1411.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 114 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025759 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1764 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351201610 | 80 | 10 | 1 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1300.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 105 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00047948 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 1912 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351202010 | 80 | 10 | 1 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 1977.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 159 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00033101 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2472 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351202110 | 80 | 10 | 1 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2029.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 164 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0005121 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2537 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351401010 | 80 | 10 | 1 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1131.3 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 243 | 258 | 311 | 5 | 13 | 13 | 16 | 0.00024935 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1257 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351401110 | 80 | 10 | 1 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1138.32 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 92 | 356 | 377 | 447 | 5 | 18 | 19 | 23 | 0.00045941 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1674 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351401510 | 80 | 10 | 1 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1646.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 133 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2058 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351401610 | 80 | 10 | 1 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1516.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 122 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00071654 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2230 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351402010 | 80 | 10 | 1 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2307.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 186 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00053465 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2884 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351402110 | 80 | 10 | 1 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2368 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00083507 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 2960 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351601010 | 80 | 10 | 1 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1293.3 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 258 | 274 | 330 | 5 | 13 | 14 | 17 | 0.00027473 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1437 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351601110 | 80 | 10 | 1 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1301.52 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 105 | 389 | 410 | 483 | 5 | 20 | 21 | 25 | 0.00051016 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 1914 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351601510 | 80 | 10 | 1 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1881.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 152 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00050396 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2352 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351601610 | 80 | 10 | 1 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 1733.32 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 140 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.0010093 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2549 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351602010 | 80 | 10 | 1 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 2636.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 213 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00067276 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3296 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351602110 | 80 | 10 | 1 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 2705.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 218 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0010621 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 3382 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351801010 | 80 | 10 | 1 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1454.4 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 117 | 276 | 292 | 348 | 6 | 14 | 15 | 18 | 0.00041786 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1616 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351801110 | 80 | 10 | 1 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1464.04 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 426 | 447 | 520 | 6 | 22 | 23 | 27 | 0.00077912 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2153 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351801510 | 60 | 10 | 1 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2116.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 171 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00066522 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2646 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1351801610 | 60 | 10 | 1 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 1949.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 157 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001361 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 2867 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1351802010 | 60 | 10 | 1 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 2966.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 239 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00083029 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3708 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1351802110 | 60 | 10 | 1 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 3044 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 245 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0015376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3805 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352001010 | 80 | 10 | 1 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1616.4 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 130 | 290 | 307 | 366 | 7 | 15 | 16 | 19 | 0.00059851 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1796 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352001110 | 80 | 10 | 1 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1626.56 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 457 | 478 | 556 | 7 | 24 | 25 | 29 | 0.00112 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2392 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352001510 | 80 | 10 | 1 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2352 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 190 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00085394 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352001610 | 80 | 10 | 1 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2166.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 175 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.001775 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3186 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352002010 | 80 | 10 | 1 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3296 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 266 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0011601 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352002110 | 80 | 10 | 1 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 3382.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 273 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0018611 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 4228 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352201010 | 80 | 10 | 1 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1658.413 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 306 | 322 | 384 | 7 | 16 | 17 | 20 | 0.00064399 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 1842.6812 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352201110 | 80 | 10 | 1 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1668.7594 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 490 | 511 | 593 | 7 | 25 | 26 | 31 | 0.001211 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2454.058 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352201510 | 80 | 10 | 1 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2413.3565 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00089719 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3016.6957 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352201610 | 80 | 10 | 1 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2222.8806 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 179 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0018471 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 3268.942 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352202010 | 80 | 10 | 1 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3381.9826 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 273 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0012072 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4227.4783 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352202110 | 80 | 10 | 1 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 3470.9101 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 280 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0019552 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 4338.6377 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352401010 | 80 | 10 | 1 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1939.5 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 321 | 338 | 402 | 8 | 17 | 17 | 21 | 0.00087721 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2155 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352401110 | 80 | 10 | 1 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1951.6 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 523 | 545 | 629 | 8 | 27 | 28 | 32 | 0.0016538 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 2870 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352401510 | 80 | 10 | 1 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 2822.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 228 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0013198 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3528 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352401610 | 80 | 10 | 1 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 2599.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 210 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0028015 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3823 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352402010 | 80 | 10 | 1 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 3955.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 319 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0016129 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352402110 | 80 | 10 | 1 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 4059.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 327 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0029395 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 5074 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352601010 | 80 | 10 | 1 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2008.3753 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 162 | 338 | 356 | 421 | 8 | 17 | 18 | 22 | 0.00093455 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2231.5281 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352601110 | 80 | 10 | 1 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2021.4413 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 163 | 558 | 581 | 666 | 8 | 29 | 30 | 34 | 0.0017685 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 2972.7079 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352601510 | 60 | 10 | 1 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2922.8225 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 236 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.001379 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 3653.5281 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1352601610 | 60 | 10 | 1 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2692.036 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 217 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0029035 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 3958.8764 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352602010 | 60 | 10 | 1 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4095.9281 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 330 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.001874 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 5119.9101 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1352602110 | 60 | 10 | 1 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4203.1551 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 339 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.003071 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 5253.9438 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352801010 | 60 | 10 | 1 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2262.6 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 318 | 331 | 374 | 9 | 16 | 17 | 19 | 0.0012257 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 2514 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352801110 | 60 | 10 | 1 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2277.32 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 184 | 557 | 573 | 630 | 9 | 29 | 30 | 33 | 0.0023241 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3349 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1352801510 | 80 | 10 | 1 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3292.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 266 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001913 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352801610 | 80 | 10 | 1 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3032.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 245 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0041124 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 4460 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352802010 | 80 | 10 | 1 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4614.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 372 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0023897 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5768 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352802110 | 80 | 10 | 1 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4735.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 382 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0043256 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 5919 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150501010 | 80 | 10 | 1 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 484.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 538 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150501110 | 80 | 10 | 1 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 471.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 38 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 693 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150601010 | 80 | 10 | 1 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 581.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 646 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150601110 | 80 | 10 | 1 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 565.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 832 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150601510 | 80 | 10 | 1 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 832 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1040 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150601610 | 80 | 10 | 1 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 774.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1139 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150602010 | 80 | 10 | 1 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1164 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1455 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150602110 | 80 | 10 | 1 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1239.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1549 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150701010 | 80 | 10 | 1 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 677.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 753 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150701110 | 80 | 10 | 1 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 659.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 970 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150701510 | 70 | 10 | 1 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 971.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 78 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1214 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
150701610 | 70 | 10 | 1 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 903.72 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 73 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1329 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
150702010 | 70 | 10 | 1 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1358.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 110 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1698 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
150702110 | 70 | 10 | 1 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1445.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 117 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024224 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1807 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
150801010 | 80 | 10 | 1 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 861 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150801110 | 80 | 10 | 1 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 1109 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150801510 | 80 | 10 | 1 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1109.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150801610 | 80 | 10 | 1 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1032.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 83 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150802010 | 80 | 10 | 1 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1552 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016875 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150802110 | 80 | 10 | 1 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1652.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 133 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150901010 | 80 | 10 | 1 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 968 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150901110 | 80 | 10 | 1 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 1247 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150901510 | 80 | 10 | 1 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1248.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 101 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016264 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1561 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150901610 | 80 | 10 | 1 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1161.44 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 94 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00044021 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1708 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150902010 | 80 | 10 | 1 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1746.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 141 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00023478 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2183 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150902110 | 80 | 10 | 1 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1859.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00045824 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2324 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501001010 | 80 | 10 | 1 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1076 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501001110 | 80 | 10 | 1 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1386 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501001510 | 80 | 10 | 1 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1387.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 112 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00023966 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1734 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501001610 | 80 | 10 | 1 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1290.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 104 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.0004533 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1898 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501002010 | 80 | 10 | 1 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1940 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00031305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2425 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501002110 | 80 | 10 | 1 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2065.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059642 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2582 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501101010 | 80 | 10 | 1 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 222 | 237 | 284 | 4 | 11 | 12 | 15 | 0.00013996 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1184 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501101110 | 80 | 10 | 1 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1525 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501101510 | 70 | 10 | 1 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1525.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1907 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1501101610 | 70 | 10 | 1 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1419.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 115 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00066276 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2088 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1501102010 | 70 | 10 | 1 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2134.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 172 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00040407 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1501102110 | 70 | 10 | 1 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2272 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 183 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00061841 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1501201010 | 80 | 10 | 1 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 227 | 243 | 293 | 5 | 12 | 13 | 15 | 0.00022398 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501201110 | 80 | 10 | 1 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 91 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501201510 | 80 | 10 | 1 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1664.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034524 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2081 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501201610 | 80 | 10 | 1 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1549.04 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00068069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2278 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501202010 | 80 | 10 | 1 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2328 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 188 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00050829 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2910 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501202110 | 80 | 10 | 1 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2478.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 200 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00078234 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501401010 | 80 | 10 | 1 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 243 | 258 | 311 | 6 | 13 | 13 | 16 | 0.00034823 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501401110 | 80 | 10 | 1 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 356 | 377 | 447 | 5 | 18 | 19 | 23 | 0.00045941 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1940 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501401510 | 80 | 10 | 1 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1942.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 157 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00047453 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2428 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501401610 | 80 | 10 | 1 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1806.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 146 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0012433 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2657 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501402010 | 80 | 10 | 1 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2716 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 219 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00064169 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3395 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501402110 | 80 | 10 | 1 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2892 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 233 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011789 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 3615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501601010 | 80 | 10 | 1 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 258 | 274 | 330 | 6 | 13 | 14 | 17 | 0.00038304 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1722 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501601110 | 80 | 10 | 1 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 389 | 410 | 483 | 6 | 20 | 21 | 25 | 0.00070949 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 2218 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501601510 | 80 | 10 | 1 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2219.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 179 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00062916 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2774 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501601610 | 80 | 10 | 1 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2065.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0016307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3037 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501602010 | 80 | 10 | 1 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3104 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 250 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0009253 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501602110 | 80 | 10 | 1 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3304.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 267 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0016729 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4131 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501801010 | 80 | 10 | 1 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 276 | 292 | 348 | 7 | 14 | 15 | 18 | 0.00055302 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1937 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501801110 | 80 | 10 | 1 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 137 | 426 | 447 | 520 | 7 | 22 | 23 | 27 | 0.001029 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2495 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501801510 | 60 | 10 | 1 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2496.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 201 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00081069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1501801610 | 60 | 10 | 1 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2322.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 187 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0020811 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3416 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1501802010 | 60 | 10 | 1 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3492 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 282 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0012692 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4365 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1501802110 | 60 | 10 | 1 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 3718.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 300 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0020114 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502001010 | 80 | 10 | 1 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 290 | 307 | 366 | 8 | 15 | 16 | 19 | 0.00076253 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2152 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502001110 | 80 | 10 | 1 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 457 | 478 | 556 | 8 | 24 | 25 | 29 | 0.0014244 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2772 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502001510 | 80 | 10 | 1 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2774.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 224 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012013 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3468 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502001610 | 80 | 10 | 1 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2581.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 208 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0025976 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502002010 | 80 | 10 | 1 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3880 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0014945 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4850 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502002110 | 80 | 10 | 1 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4131.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 333 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0026765 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 5164 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502201010 | 80 | 10 | 1 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1987.0174 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 160 | 306 | 322 | 384 | 8 | 16 | 17 | 20 | 0.00081987 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2207.7971 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502201110 | 80 | 10 | 1 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1933.9003 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 156 | 490 | 511 | 593 | 8 | 25 | 26 | 31 | 0.0015391 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2843.971 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502201510 | 80 | 10 | 1 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2847.0493 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 230 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012605 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3558.8116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502201610 | 80 | 10 | 1 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2648.5014 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 214 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0026996 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 3894.8551 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502202010 | 80 | 10 | 1 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3981.2174 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 321 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0017425 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4976.5217 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502202110 | 80 | 10 | 1 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 4239.1072 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 342 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0031242 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 5298.8841 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502401010 | 80 | 10 | 1 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 321 | 338 | 402 | 10 | 17 | 17 | 21 | 0.0013125 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2582 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502401110 | 80 | 10 | 1 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 182 | 523 | 545 | 629 | 9 | 27 | 28 | 32 | 0.0020427 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 3326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502401510 | 80 | 10 | 1 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3329.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 269 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0017585 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4162 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502401610 | 80 | 10 | 1 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3097.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 250 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0038405 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4555 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502402010 | 80 | 10 | 1 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 4656 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 375 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0022305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 5820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502402110 | 80 | 10 | 1 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 4957.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 400 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0043563 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 6197 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502601010 | 80 | 10 | 1 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2407.0146 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 194 | 338 | 356 | 421 | 10 | 17 | 18 | 22 | 0.001397 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2674.4607 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502601110 | 80 | 10 | 1 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2342.5542 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 189 | 558 | 581 | 666 | 10 | 29 | 30 | 34 | 0.0026367 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 3444.9326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502601510 | 60 | 10 | 1 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3447.5955 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 278 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0018357 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4309.4944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1502601610 | 60 | 10 | 1 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3207.5065 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 259 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0039765 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 4716.9213 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502602010 | 60 | 10 | 1 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4821.6629 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 389 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0025443 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 6027.0787 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1502602110 | 60 | 10 | 1 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5134.1124 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 414 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0045455 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 6417.6404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502801010 | 60 | 10 | 1 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 318 | 331 | 374 | 11 | 16 | 17 | 19 | 0.0017586 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3013 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502801110 | 60 | 10 | 1 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 557 | 573 | 630 | 11 | 29 | 30 | 33 | 0.003327 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3881 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1502801510 | 80 | 10 | 1 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3884 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0024501 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4855 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502801610 | 80 | 10 | 1 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3613.52 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 291 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005382 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 5314 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502802010 | 80 | 10 | 1 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5432 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 438 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0034217 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 6790 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502802110 | 80 | 10 | 1 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5784 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 466 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0060645 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 7230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165501010 | 80 | 10 | 1 | 65 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 545.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 44 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 606 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165501110 | 80 | 10 | 1 | 65 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 524.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 772 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165601010 | 80 | 10 | 1 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 654.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 727 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165601110 | 80 | 10 | 1 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 629.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 926 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165601510 | 80 | 10 | 1 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 922.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1153 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165601610 | 80 | 10 | 1 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 886.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1304 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165602010 | 80 | 10 | 1 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1288.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1611 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165602110 | 80 | 10 | 1 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1454.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1818 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165701010 | 80 | 10 | 1 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 763.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 848 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165701110 | 80 | 10 | 1 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 734.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1080 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165701510 | 70 | 10 | 1 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1076 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 87 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1345 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
165701610 | 70 | 10 | 1 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1034.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 83 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1521 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
165702010 | 70 | 10 | 1 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1504 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 121 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
165702110 | 70 | 10 | 1 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1696.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 137 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032624 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
165801010 | 80 | 10 | 1 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 872.1 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 969 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165801110 | 80 | 10 | 1 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 839.12 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 260 | 279 | 337 | 4 | 13 | 14 | 17 | 0.00020308 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255 | 274 | 331 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.8862 | 263.2129 | 44 | 47 | 57 | 0.018134 | 0.020547 | 0.029625 | 1.1 | 6 | 6.7 | 9 |  | 1234 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.8862 | 263.2129 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165801510 | 80 | 10 | 1 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1230.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1538 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165801610 | 80 | 10 | 1 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1181.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 95 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00042712 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1738 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165802010 | 80 | 10 | 1 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1718.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 139 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022764 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2148 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165802110 | 80 | 10 | 1 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1939.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044029 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2424 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165901010 | 80 | 10 | 1 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 981 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1090 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165901110 | 80 | 10 | 1 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 944.52 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 256 | 276 | 336 | 0.95 | 0.95 | 0.95 | 203.5725 | 219.4766 | 267.1889 | 44 | 47 | 57 | 0.019237 | 0.021784 | 0.031354 | 1.2 | 6 | 6.7 | 9 |  | 1389 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 203.5725 | 219.4766 | 267.1889 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165901510 | 80 | 10 | 1 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1384 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 112 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1730 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165901610 | 80 | 10 | 1 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1330.08 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 107 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00062691 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1956 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165902010 | 80 | 10 | 1 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1933.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00030408 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2417 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165902110 | 80 | 10 | 1 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2181.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 176 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00057443 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651001010 | 80 | 10 | 1 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1089.9 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 88 | 212 | 227 | 275 | 5 | 11 | 12 | 14 | 0.0001986 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1211 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651001110 | 80 | 10 | 1 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1049.24 | 1957 | 2107 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 85 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 257.23 | 276.95 | 340 | 0.95 | 0.95 | 0.95 | 204.5506 | 220.2321 | 270.3698 | 44 | 47 | 58 | 0.02034 | 0.023021 | 0.034183 | 1.3 | 6 | 6.7 | 9 |  | 1543 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 204.5506 | 220.2321 | 270.3698 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651001510 | 80 | 10 | 1 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1537.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 124 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00023966 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1922 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651001610 | 80 | 10 | 1 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1477.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 119 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00064483 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2173 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651002010 | 80 | 10 | 1 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2148 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 173 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00039308 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2685 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651002110 | 80 | 10 | 1 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2424 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00072961 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3030 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651101010 | 80 | 10 | 1 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1198.8 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 97 | 222 | 237 | 284 | 5 | 11 | 12 | 15 | 0.00021129 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1332 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651101110 | 80 | 10 | 1 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1153.96 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 93 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 261 | 281 | 345 | 0.95 | 0.95 | 0.95 | 207.5486 | 223.4527 | 274.3458 | 45 | 48 | 59 | 0.022364 | 0.025233 | 0.037136 | 1.5 | 6 | 6.7 | 9 |  | 1697 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 207.5486 | 223.4527 | 274.3458 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651101510 | 70 | 10 | 1 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1691.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 136 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00033355 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2114 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1651101610 | 70 | 10 | 1 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1625.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 131 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00089237 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1651102010 | 70 | 10 | 1 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2363.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00049511 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2954 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1651102110 | 70 | 10 | 1 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2666.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 215 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00090675 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3333 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1651201010 | 80 | 10 | 1 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1307.7 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 227 | 243 | 293 | 5 | 12 | 13 | 15 | 0.00022398 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1453 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651201110 | 80 | 10 | 1 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1259.36 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 102 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 260 | 281 | 349 | 0.95 | 0.95 | 0.95 | 206.7534 | 223.4527 | 277.5266 | 44 | 48 | 60 | 0.022547 | 0.026516 | 0.040214 | 1.6 | 6 | 6.7 | 9 |  | 1852 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.7534 | 223.4527 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651201510 | 80 | 10 | 1 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1844.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 149 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044509 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651201610 | 80 | 10 | 1 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1773.44 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 143 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00091576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2608 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81417 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651202010 | 80 | 10 | 1 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2577.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 208 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00061062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3222 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651202110 | 80 | 10 | 1 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2908.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 235 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011067 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3636 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651401010 | 80 | 10 | 1 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1525.5 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 243 | 258 | 311 | 6 | 13 | 13 | 16 | 0.00034823 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1695 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651401110 | 80 | 10 | 1 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1468.8 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 356 | 377 | 447 | 6 | 18 | 19 | 23 | 0.00063987 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 263 | 284 | 359 | 0.95 | 0.95 | 0.95 | 209.139 | 225.8383 | 285.4787 | 45 | 49 | 61 | 0.025805 | 0.030215 | 0.045364 | 1.9 | 6 | 6.7 | 9 |  | 2160 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 209.139 | 225.8383 | 285.4787 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651401510 | 80 | 10 | 1 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2152.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 174 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059309 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651401610 | 80 | 10 | 1 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2068.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0015586 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3042 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651402010 | 80 | 10 | 1 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 3007.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 243 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.00088388 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3759 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651402110 | 80 | 10 | 1 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3393.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 274 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0015788 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 4242 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651601010 | 80 | 10 | 1 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1744.2 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 258 | 274 | 330 | 7 | 13 | 14 | 17 | 0.00050754 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1938 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651601110 | 80 | 10 | 1 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1678.92 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 389 | 410 | 483 | 7 | 20 | 21 | 25 | 0.00093804 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 266 | 288 | 368 | 0.95 | 0.95 | 0.95 | 211.5246 | 229.0191 | 292.6355 | 45 | 49 | 63 | 0.0281 | 0.032875 | 0.052279 | 2.1 | 6 | 6.7 | 9 |  | 2469 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 211.5246 | 229.0191 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651601510 | 80 | 10 | 1 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2460 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00076744 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3075 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651601610 | 80 | 10 | 1 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2364.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0019946 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3477 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651602010 | 80 | 10 | 1 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3436.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 277 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001066 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 4296 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651602110 | 80 | 10 | 1 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3878.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0021524 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4848 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651801010 | 80 | 10 | 1 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1962 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 158 | 276 | 292 | 348 | 8 | 14 | 15 | 18 | 0.00070519 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 2180 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651801110 | 80 | 10 | 1 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1888.36 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 426 | 447 | 520 | 8 | 22 | 23 | 27 | 0.0013098 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 272 | 296 | 377 | 0.95 | 0.95 | 0.95 | 216.2958 | 235.3807 | 299.7924 | 47 | 51 | 64 | 0.032918 | 0.038242 | 0.058049 | 2.4 | 6 | 6.7 | 9 |  | 2777 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 216.2958 | 235.3807 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651801510 | 60 | 10 | 1 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2768 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 223 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011421 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3460 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1651801610 | 60 | 10 | 1 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2659.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 214 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0024957 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3911 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1651802010 | 60 | 10 | 1 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3866.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 312 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0014352 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4833 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1651802110 | 60 | 10 | 1 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 4363.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 352 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.002834 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5454 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652001010 | 80 | 10 | 1 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2179.8 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 176 | 290 | 307 | 366 | 9 | 15 | 16 | 19 | 0.00094435 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2422 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652001110 | 80 | 10 | 1 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2098.48 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 169 | 457 | 478 | 556 | 9 | 24 | 25 | 29 | 0.0017614 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 273 | 297 | 386 | 0.95 | 0.95 | 0.95 | 217.091 | 236.1759 | 306.9492 | 47 | 51 | 66 | 0.035392 | 0.041093 | 0.06589 | 2.7 | 6 | 6.7 | 9 |  | 3086 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.091 | 236.1759 | 306.9492 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652001510 | 80 | 10 | 1 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 3075.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 248 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0013958 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652001610 | 80 | 10 | 1 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2955.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 238 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0030647 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 4346 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652002010 | 80 | 10 | 1 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 4296 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 346 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.001869 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 5370 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652002110 | 80 | 10 | 1 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4848 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 391 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0036299 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 6060 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652201010 | 80 | 10 | 1 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2236.3565 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 180 | 306 | 322 | 384 | 9 | 16 | 17 | 20 | 0.0010147 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2484.8406 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652201110 | 80 | 10 | 1 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2153.1067 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 490 | 511 | 593 | 9 | 25 | 26 | 31 | 0.001902 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 275 | 300 | 396 | 0.95 | 0.95 | 0.95 | 218.6814 | 238.5616 | 314.9013 | 47 | 51 | 68 | 0.037866 | 0.043943 | 0.074292 | 2.9 | 6 | 6.7 | 9 |  | 3166.3333 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 218.6814 | 238.5616 | 314.9013 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652201510 | 80 | 10 | 1 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3155.5594 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 254 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0014638 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3944.4493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652201610 | 80 | 10 | 1 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 3032.258 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 245 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0037045 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4459.2029 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652202010 | 80 | 10 | 1 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 4408.0696 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 355 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0019415 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 5510.087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652202110 | 80 | 10 | 1 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 4974.4696 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 401 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0041671 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 6218.087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652401010 | 80 | 10 | 1 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2615.4 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 211 | 321 | 338 | 402 | 11 | 17 | 17 | 21 | 0.0015594 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2906 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652401110 | 80 | 10 | 1 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2518.04 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 203 | 523 | 545 | 629 | 10 | 27 | 28 | 32 | 0.0024679 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 304 | 405 | 0.95 | 0.95 | 0.95 | 220.2718 | 241.7424 | 322.0581 | 47 | 52 | 69 | 0.04034 | 0.048475 | 0.081117 | 3.2 | 6 | 6.7 | 9 |  | 3703 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 241.7424 | 322.0581 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652401510 | 80 | 10 | 1 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3690.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 298 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0019998 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652401610 | 80 | 10 | 1 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3546.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 286 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005034 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5215 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652402010 | 80 | 10 | 1 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 5155.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 416 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0026947 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 6444 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652402110 | 80 | 10 | 1 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 5817.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 469 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0055883 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 7272 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652601010 | 80 | 10 | 1 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2708.9899 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 218 | 338 | 356 | 421 | 11 | 17 | 18 | 22 | 0.001659 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 3009.9888 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652601110 | 80 | 10 | 1 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2607.5326 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 210 | 558 | 581 | 666 | 11 | 29 | 30 | 34 | 0.0031278 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 311 | 414 | 0.95 | 0.95 | 0.95 | 224.2479 | 247.3088 | 329.215 | 48 | 53 | 71 | 0.044479 | 0.053231 | 0.090513 | 3.5 | 6 | 6.7 | 9 |  | 3834.6067 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 247.3088 | 329.215 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652601510 | 60 | 10 | 1 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3821.8247 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 308 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0023528 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4777.2809 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1652601610 | 60 | 10 | 1 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3672.2751 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 296 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005208 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 5400.4045 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652602010 | 60 | 10 | 1 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5338.6247 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 431 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.0030448 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 6673.2809 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1652602110 | 60 | 10 | 1 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6024.5933 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 486 | #VALUE! | #VALUE! | #VALUE! | 25 | #VALUE! | #VALUE! | #VALUE! | 0.0062862 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 7530.7416 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652801010 | 60 | 10 | 1 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3051.9 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 318 | 331 | 374 | 13 | 16 | 17 | 19 | 0.0023761 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3391 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652801110 | 60 | 10 | 1 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2937.6 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 237 | 557 | 573 | 630 | 12 | 29 | 30 | 33 | 0.0038875 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222 | 245 | 326 | 0.95 | 0.95 | 0.95 | 176.5356 | 194.8253 | 259.2369 | 38 | 42 | 56 | 0.030851 | 0.03696 | 0.062174 | 3.7 | 6 | 6.7 | 9 |  | 4320 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.5356 | 194.8253 | 259.2369 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1652801510 | 80 | 10 | 1 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4305.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 347 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0030486 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 5382 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652801610 | 80 | 10 | 1 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4137.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 334 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0068121 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 6084 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652802010 | 80 | 10 | 1 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6014.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 485 | #VALUE! | #VALUE! | #VALUE! | 25 | #VALUE! | #VALUE! | #VALUE! | 0.0040028 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 7518 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652802110 | 80 | 10 | 1 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6787.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 547 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0080738 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 8484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195601010 | 80 | 10 | 1 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 752.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 836 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195601110 | 80 | 10 | 1 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 733.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1078 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195601510 | 80 | 10 | 1 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 1030.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1288 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195601610 | 80 | 10 | 1 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 1092.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1606 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195602010 | 80 | 10 | 1 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1436 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1795 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195602110 | 80 | 10 | 1 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1881.6 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2352 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195701010 | 80 | 10 | 1 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 877.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 975 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195701110 | 80 | 10 | 1 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 854.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1257 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195701510 | 70 | 10 | 1 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1201.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 97 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00014954 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1502 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
195701610 | 70 | 10 | 1 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1274.32 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 103 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00041403 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1874 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
195702010 | 70 | 10 | 1 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1675.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 135 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 2094 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
195702110 | 70 | 10 | 1 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 2195.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 177 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00053044 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
195801010 | 80 | 10 | 1 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1002.6 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 1114 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195801110 | 80 | 10 | 1 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 977.16 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 260 | 279 | 337 | 4 | 13 | 14 | 17 | 0.00020308 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 214 | 230 | 277 | 0.95 | 0.95 | 0.95 | 170.1739 | 182.8972 | 220.2718 | 37 | 39 | 47 | 0.013064 | 0.014431 | 0.020547 | 1.1 | 6 | 6.7 | 9 |  | 1437 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.1739 | 182.8972 | 220.2718 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195801510 | 80 | 10 | 1 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1373.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 111 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00022173 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1717 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195801610 | 80 | 10 | 1 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1456.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 117 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00060898 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195802010 | 80 | 10 | 1 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1915.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 154 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0002951 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195802110 | 80 | 10 | 1 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 2508.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 202 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00067687 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195901010 | 80 | 10 | 1 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1128.6 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 205 | 220 | 266 | 5 | 11 | 11 | 14 | 0.00018592 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1254 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195901110 | 80 | 10 | 1 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1098.88 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 89 | 276 | 295 | 355 | 5 | 14 | 15 | 18 | 0.00033253 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 215 | 231 | 281 | 0.95 | 0.95 | 0.95 | 170.9691 | 183.6924 | 223.4527 | 37 | 39 | 48 | 0.013881 | 0.015326 | 0.022667 | 1.2 | 6 | 6.7 | 9 |  | 1616 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.9691 | 183.6924 | 223.4527 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195901510 | 80 | 10 | 1 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1544.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1931 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195901610 | 80 | 10 | 1 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1638.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 132 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00084561 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2409 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195902010 | 80 | 10 | 1 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 2154.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 174 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00038208 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2693 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195902110 | 80 | 10 | 1 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2822.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 228 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00099848 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3528 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951001010 | 80 | 10 | 1 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1253.7 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 212 | 227 | 275 | 5 | 11 | 12 | 14 | 0.0001986 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1393 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951001110 | 80 | 10 | 1 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1221.28 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 291 | 311 | 374 | 5 | 15 | 16 | 19 | 0.00035791 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216 | 232 | 285 | 0.95 | 0.95 | 0.95 | 171.7643 | 184.4876 | 226.6335 | 37 | 40 | 49 | 0.014697 | 0.01701 | 0.024896 | 1.3 | 6 | 6.7 | 9 |  | 1796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.7643 | 184.4876 | 226.6335 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951001510 | 80 | 10 | 1 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1716.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 138 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032186 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 2146 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951001610 | 80 | 10 | 1 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1820.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0011255 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2677 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951002010 | 80 | 10 | 1 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2393.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 193 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00048192 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2992 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951002110 | 80 | 10 | 1 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 3136 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 253 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0012062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3920 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951101010 | 80 | 10 | 1 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1378.8 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 222 | 237 | 284 | 6 | 11 | 12 | 15 | 0.00029601 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1532 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951101110 | 80 | 10 | 1 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1343.68 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 108 | 310 | 329 | 392 | 6 | 16 | 17 | 20 | 0.00053543 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 218 | 235 | 289 | 0.95 | 0.95 | 0.95 | 173.3547 | 186.8732 | 229.8143 | 37 | 40 | 49 | 0.015514 | 0.017945 | 0.026226 | 1.5 | 6 | 6.7 | 9 |  | 1976 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.3547 | 186.8732 | 229.8143 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951101510 | 70 | 10 | 1 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1888.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 152 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00043037 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2361 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1951101610 | 70 | 10 | 1 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 2002.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 162 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001155 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2945 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1951102010 | 70 | 10 | 1 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2632.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 212 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00059509 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 3291 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1951102110 | 70 | 10 | 1 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 3449.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 278 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0014376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4312 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1951201010 | 80 | 10 | 1 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1504.8 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 227 | 243 | 293 | 6 | 12 | 13 | 15 | 0.00031342 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1672 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951201110 | 80 | 10 | 1 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1465.4 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 324 | 344 | 410 | 6 | 17 | 18 | 21 | 0.00057024 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 218 | 235 | 293 | 0.95 | 0.95 | 0.95 | 173.3547 | 186.8732 | 232.9951 | 37 | 40 | 50 | 0.016331 | 0.01888 | 0.028613 | 1.6 | 6 | 6.7 | 9 |  | 2155 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.3547 | 186.8732 | 232.9951 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951201510 | 80 | 10 | 1 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 2060 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 166 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00055702 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2575 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951201610 | 80 | 10 | 1 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 2184.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 176 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0014865 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3212 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951202010 | 80 | 10 | 1 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2872 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 232 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00072203 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3590 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951202110 | 80 | 10 | 1 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 3763.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 303 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0019155 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4704 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951401010 | 80 | 10 | 1 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1755 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 243 | 258 | 311 | 7 | 13 | 13 | 16 | 0.00046205 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1950 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951401110 | 80 | 10 | 1 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1709.52 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 138 | 356 | 377 | 447 | 7 | 18 | 19 | 23 | 0.00084707 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 220 | 238 | 300 | 0.95 | 0.95 | 0.95 | 174.9451 | 189.2588 | 238.5616 | 38 | 41 | 51 | 0.018873 | 0.021721 | 0.032541 | 1.9 | 6 | 6.7 | 9 |  | 2514 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 189.2588 | 238.5616 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951401510 | 80 | 10 | 1 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2403.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 194 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0007242 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 3004 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951401610 | 80 | 10 | 1 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2548.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 206 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0022918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3748 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951402010 | 80 | 10 | 1 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 3351.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 270 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0010189 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 4189 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951402110 | 80 | 10 | 1 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 4390.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 354 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0025438 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5488 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220501010 | 80 | 10 | 2 | 20 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 255.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6.3694e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 284 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
220601010 | 80 | 10 | 2 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 306.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.1473e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 341 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
220601510 | 80 | 10 | 2 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 498.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 40 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4254e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 623 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
220602010 | 80 | 10 | 2 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 668.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4.0779e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 836 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220701010 | 80 | 10 | 2 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 358.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.9253e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 398 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
220701510 | 70 | 10 | 2 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 581.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 47 | #VALUE! | #VALUE! | #VALUE! | 2 | #VALUE! | #VALUE! | #VALUE! | 2.5603e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
220702010 | 70 | 10 | 2 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 780.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 63 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 4.2437e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 976 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
220801010 | 80 | 10 | 2 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 408.6 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 33 | 198 | 213 | 257 | 2 | 10 | 11 | 13 | 3.1383e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 454 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
220801510 | 80 | 10 | 2 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 664 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 54 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.8533e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 830 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
220802010 | 80 | 10 | 2 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 892 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 72 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.6905e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1115 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220901010 | 80 | 10 | 2 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 459.9 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 37 | 205 | 220 | 266 | 2 | 11 | 11 | 14 | 3.3972e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 511 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
220901510 | 80 | 10 | 2 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 747.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 60 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 6.1246e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 934 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220902010 | 80 | 10 | 2 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1004 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 81 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.9626e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1255 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201001010 | 80 | 10 | 2 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 511.2 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 41 | 212 | 227 | 275 | 2 | 11 | 12 | 14 | 3.656e-05 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 568 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2201001510 | 80 | 10 | 2 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 830.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 67 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 6.3959e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1038 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201002010 | 80 | 10 | 2 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1115.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 90 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00012648 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 1394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201101010 | 80 | 10 | 2 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 562.5 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 45 | 222 | 237 | 284 | 2 | 11 | 12 | 15 | 3.9149e-05 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 625 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201101510 | 70 | 10 | 2 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 913.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 74 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011501 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1142 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
2201102010 | 70 | 10 | 2 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1226.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00013047 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 1533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2201201010 | 80 | 10 | 2 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 613.8 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 50 | 227 | 243 | 293 | 3 | 12 | 13 | 15 | 8.7635e-05 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 682 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201201510 | 80 | 10 | 2 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 996.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 80 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011946 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1246 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201202010 | 80 | 10 | 2 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 1338.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 108 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00019063 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1673 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201401010 | 80 | 10 | 2 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 715.5 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 58 | 243 | 258 | 311 | 3 | 13 | 13 | 16 | 9.8096e-05 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 795 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201401510 | 80 | 10 | 2 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1162.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 94 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00019536 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1453 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201402010 | 80 | 10 | 2 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1561.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 126 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00027044 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1952 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201601010 | 80 | 10 | 2 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 818.1 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 258 | 274 | 330 | 3 | 13 | 14 | 17 | 0.00010856 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 909 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201601510 | 80 | 10 | 2 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1328.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 107 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00029344 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1661 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201602010 | 80 | 10 | 2 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 1784 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 144 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00028471 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201801010 | 80 | 10 | 2 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 919.8 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 276 | 292 | 348 | 4 | 14 | 15 | 18 | 0.00020027 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1022 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201801510 | 60 | 10 | 2 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 1494.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 121 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00031137 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1868 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2201802010 | 60 | 10 | 2 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 2007.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 162 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00038487 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2509 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2202001010 | 80 | 10 | 2 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1022.4 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 290 | 307 | 366 | 4 | 15 | 16 | 19 | 0.0002175 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1136 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202001510 | 80 | 10 | 2 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 1660.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00043878 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2076 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202002010 | 80 | 10 | 2 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 2230.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 180 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00050303 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2788 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202201010 | 80 | 10 | 2 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1125 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 306 | 322 | 384 | 5 | 16 | 17 | 20 | 0.00035085 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 1250 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202201510 | 80 | 10 | 2 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 1827.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00059228 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2284 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202202010 | 80 | 10 | 2 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 2453.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00064012 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3067 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202401010 | 80 | 10 | 2 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1226.7 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 321 | 338 | 402 | 5 | 17 | 17 | 21 | 0.00037623 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 1363 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202401510 | 80 | 10 | 2 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 1992.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 161 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00062172 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2491 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202402010 | 80 | 10 | 2 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 2676.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 216 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00079703 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3346 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202601010 | 80 | 10 | 2 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1329.3 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 107 | 338 | 356 | 421 | 6 | 17 | 18 | 22 | 0.00055711 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 1477 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202601510 | 60 | 10 | 2 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2159.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 174 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00080948 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 2699 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2202602010 | 60 | 10 | 2 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2899.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 234 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00097465 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 3624 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2202801010 | 60 | 10 | 2 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1431.9 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 115 | 318 | 331 | 374 | 6 | 16 | 17 | 19 | 0.00059192 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 1591 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2202801510 | 80 | 10 | 2 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2324.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 187 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0010269 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2906 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202802010 | 80 | 10 | 2 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3122.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 252 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0011738 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 3903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235501010 | 80 | 10 | 2 | 35 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 353.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6.3694e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 393 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235501110 | 80 | 10 | 2 | 35 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 373.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 30 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 549 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235601010 | 80 | 10 | 2 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 423.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 34 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 471 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235601110 | 80 | 10 | 2 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 448.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 659 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235601510 | 80 | 10 | 2 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 632 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 790 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235601610 | 80 | 10 | 2 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 663 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 975 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235602010 | 80 | 10 | 2 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 864.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1081 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235602110 | 80 | 10 | 2 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 997.6 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1247 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235701010 | 80 | 10 | 2 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 495 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 40 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 550 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235701110 | 80 | 10 | 2 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 522.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 769 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235701510 | 70 | 10 | 2 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 737.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 59 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.5819e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 922 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
235701610 | 70 | 10 | 2 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 773.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 62 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 0.00015302 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1138 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
235702010 | 70 | 10 | 2 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1008.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 81 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.4184e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1261 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
235702110 | 70 | 10 | 2 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1164 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 94 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017042 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1455 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
235801010 | 80 | 10 | 2 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 565.2 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 46 | 198 | 213 | 257 | 2 | 10 | 11 | 13 | 3.1383e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 628 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235801110 | 80 | 10 | 2 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 597.04 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 48 | 260 | 279 | 337 | 2 | 13 | 14 | 17 | 5.6478e-05 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 878 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235801510 | 80 | 10 | 2 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 843.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 68 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00010164 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1054 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235801610 | 80 | 10 | 2 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 884 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 71 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1300 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235802010 | 80 | 10 | 2 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1152.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 93 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011849 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1441 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235802110 | 80 | 10 | 2 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1329.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 107 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025318 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 1662 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235901010 | 80 | 10 | 2 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 636.3 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 51 | 205 | 220 | 266 | 3 | 11 | 11 | 14 | 7.1943e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 707 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235901110 | 80 | 10 | 2 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 671.84 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 54 | 276 | 295 | 355 | 3 | 14 | 15 | 18 | 0.00012974 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 988 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
235901510 | 80 | 10 | 2 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 948 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 76 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.0001061 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1185 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235901610 | 80 | 10 | 2 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 994.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 80 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00028576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1463 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235902010 | 80 | 10 | 2 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1296.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 105 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00012248 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1621 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235902110 | 80 | 10 | 2 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1496 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 121 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00026412 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 1870 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351001010 | 80 | 10 | 2 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 706.5 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 212 | 227 | 275 | 3 | 11 | 12 | 14 | 7.7174e-05 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 785 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351001110 | 80 | 10 | 2 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 746.64 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 60 | 291 | 311 | 374 | 3 | 15 | 16 | 19 | 0.0001402 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1098 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351001510 | 80 | 10 | 2 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1053.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 85 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011055 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1317 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351001610 | 80 | 10 | 2 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1105 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.0004533 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1625 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351002010 | 80 | 10 | 2 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1440.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 116 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00017969 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 1801 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351002110 | 80 | 10 | 2 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 1662.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036904 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2078 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351101010 | 80 | 10 | 2 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 777.6 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 222 | 237 | 284 | 3 | 11 | 12 | 15 | 8.2405e-05 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 864 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351101110 | 80 | 10 | 2 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 821.44 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 66 | 310 | 329 | 392 | 3 | 16 | 17 | 20 | 0.00015066 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1208 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351101510 | 70 | 10 | 2 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1159.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 93 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017573 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1449 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2351101610 | 70 | 10 | 2 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1215.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 98 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00046639 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 1788 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2351102010 | 70 | 10 | 2 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1584.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 128 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00024904 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 1981 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2351102110 | 70 | 10 | 2 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 1828.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00049415 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2286 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2351201010 | 80 | 10 | 2 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 847.8 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 68 | 227 | 243 | 293 | 4 | 12 | 13 | 15 | 0.00014858 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 942 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351201110 | 80 | 10 | 2 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 896.24 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 324 | 344 | 410 | 4 | 17 | 18 | 21 | 0.000272 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1318 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351201510 | 80 | 10 | 2 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1264 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 102 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00018227 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1580 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351201610 | 80 | 10 | 2 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1326 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 107 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00068069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 1950 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351202010 | 80 | 10 | 2 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 1728.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 139 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00025617 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2161 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351202110 | 80 | 10 | 2 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 1995.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 161 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0005121 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2494 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351401010 | 80 | 10 | 2 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 989.1 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 80 | 243 | 258 | 311 | 4 | 13 | 13 | 16 | 0.00016581 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1099 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351401110 | 80 | 10 | 2 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1045.16 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 356 | 377 | 447 | 4 | 18 | 19 | 23 | 0.00030646 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1537 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351401510 | 80 | 10 | 2 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1475.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 119 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00027551 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351401610 | 80 | 10 | 2 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1547 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00071654 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2275 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351402010 | 80 | 10 | 2 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1936.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00034896 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2421 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351402110 | 80 | 10 | 2 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2327.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 188 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00083507 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 2909 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351601010 | 80 | 10 | 2 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1130.4 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 258 | 274 | 330 | 5 | 13 | 14 | 17 | 0.00027473 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1256 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351601110 | 80 | 10 | 2 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1194.76 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 389 | 410 | 483 | 5 | 20 | 21 | 25 | 0.00051016 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 1757 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351601510 | 80 | 10 | 2 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1685.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 136 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00039201 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2107 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351601610 | 80 | 10 | 2 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 1768 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 143 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.0010093 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2600 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351602010 | 80 | 10 | 2 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 2305.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 186 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00056102 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351602110 | 80 | 10 | 2 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 2660 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 215 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0010621 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 3325 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351801010 | 80 | 10 | 2 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1271.7 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 103 | 276 | 292 | 348 | 5 | 14 | 15 | 18 | 0.0003001 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1413 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351801110 | 80 | 10 | 2 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1343.68 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 108 | 426 | 447 | 520 | 6 | 22 | 23 | 27 | 0.00077912 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 1976 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351801510 | 60 | 10 | 2 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 1896.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 153 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0005334 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2371 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2351801610 | 60 | 10 | 2 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 1989 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 160 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001361 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 2925 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2351802010 | 60 | 10 | 2 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 2593.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 209 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00070383 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3242 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2351802110 | 60 | 10 | 2 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 2992 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 241 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0013233 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3740 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352001010 | 80 | 10 | 2 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1413 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 290 | 307 | 366 | 6 | 15 | 16 | 19 | 0.00045267 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1570 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352001110 | 80 | 10 | 2 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1493.28 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 120 | 457 | 478 | 556 | 6 | 24 | 25 | 29 | 0.00084875 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2196 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352001510 | 80 | 10 | 2 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2107.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 170 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00070129 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2634 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352001610 | 80 | 10 | 2 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2210 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 178 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.001775 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3250 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352002010 | 80 | 10 | 2 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 2881.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 232 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00086638 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3602 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352002110 | 80 | 10 | 2 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 3324.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 268 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0018611 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 4156 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352201010 | 80 | 10 | 2 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1554.3 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 306 | 322 | 384 | 6 | 16 | 17 | 20 | 0.00048748 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 1727 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352201110 | 80 | 10 | 2 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1642.88 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 132 | 490 | 511 | 593 | 7 | 25 | 26 | 31 | 0.001211 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2416 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352201510 | 80 | 10 | 2 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2317.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 187 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00089719 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2897 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352201610 | 80 | 10 | 2 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2431 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 196 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0022541 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 3575 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352202010 | 80 | 10 | 2 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3169.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 256 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0010496 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3962 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352202110 | 80 | 10 | 2 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 3657.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 295 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0022234 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 4572 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352401010 | 80 | 10 | 2 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1695.6 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 137 | 321 | 338 | 402 | 7 | 17 | 17 | 21 | 0.00068948 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 1884 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352401110 | 80 | 10 | 2 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1791.8 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 145 | 523 | 545 | 629 | 7 | 27 | 28 | 32 | 0.0013019 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 2635 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352401510 | 80 | 10 | 2 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 2528.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 204 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0011226 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3161 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352401610 | 80 | 10 | 2 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 2652 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 214 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0028015 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3900 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352402010 | 80 | 10 | 2 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 3457.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 279 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0012542 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4322 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352402110 | 80 | 10 | 2 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 3989.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 322 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0029395 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 4987 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352601010 | 80 | 10 | 2 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1836.9 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 148 | 338 | 356 | 421 | 8 | 17 | 18 | 22 | 0.00093455 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2041 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352601110 | 80 | 10 | 2 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1941.4 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 558 | 581 | 666 | 8 | 29 | 30 | 34 | 0.0017685 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 2855 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352601510 | 60 | 10 | 2 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2739.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 221 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0011736 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 3424 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2352601610 | 60 | 10 | 2 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2893.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 233 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00342 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 4255 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352602010 | 60 | 10 | 2 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3746.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 302 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0016721 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 4683 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2352602110 | 60 | 10 | 2 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4322.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 349 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0034143 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 5403 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352801010 | 60 | 10 | 2 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1978.2 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 160 | 318 | 331 | 374 | 8 | 16 | 17 | 19 | 0.00099189 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 2198 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352801110 | 60 | 10 | 2 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2090.32 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 169 | 557 | 573 | 630 | 9 | 29 | 30 | 33 | 0.0023241 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3074 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2352801510 | 80 | 10 | 2 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2950.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 238 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0014382 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3688 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352801610 | 80 | 10 | 2 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3094 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 250 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0041124 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 4550 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352802010 | 80 | 10 | 2 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4034.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 325 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0019397 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5043 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352802110 | 80 | 10 | 2 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4654.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 375 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0039338 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 5818 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250501010 | 80 | 10 | 2 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 35 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 482 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250501110 | 80 | 10 | 2 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 445.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 655 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250601010 | 80 | 10 | 2 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 578 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250601110 | 80 | 10 | 2 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 533.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250601510 | 80 | 10 | 2 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 736 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 920 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250601610 | 80 | 10 | 2 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 796.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 64 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1171 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250602010 | 80 | 10 | 2 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1017.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1272 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250602110 | 80 | 10 | 2 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1230.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1538 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250701010 | 80 | 10 | 2 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 607.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 675 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250701110 | 80 | 10 | 2 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 622.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 50 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 916 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250701510 | 70 | 10 | 2 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 858.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 69 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1073 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
250701610 | 70 | 10 | 2 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 928.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 75 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1366 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
250702010 | 70 | 10 | 2 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1187.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011449 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
250702110 | 70 | 10 | 2 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1436 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 116 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024224 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1795 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
250801010 | 80 | 10 | 2 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693.9 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 56 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 771 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250801110 | 80 | 10 | 2 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 711.96 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 1047 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250801510 | 80 | 10 | 2 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 980.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 79 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00010164 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250801610 | 80 | 10 | 2 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1061.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 86 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1561 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250802010 | 80 | 10 | 2 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1356.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 109 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016875 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250802110 | 80 | 10 | 2 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1640.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 132 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2051 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250901010 | 80 | 10 | 2 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 781.2 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 205 | 220 | 266 | 3 | 11 | 11 | 14 | 7.1943e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 868 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250901110 | 80 | 10 | 2 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 801.04 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 276 | 295 | 355 | 3 | 14 | 15 | 18 | 0.00012974 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 1178 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250901510 | 80 | 10 | 2 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1104 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016264 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1380 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250901610 | 80 | 10 | 2 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1194.08 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00044021 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1756 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250902010 | 80 | 10 | 2 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1526.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00017422 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1908 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250902110 | 80 | 10 | 2 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1846.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 149 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00045824 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2308 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501001010 | 80 | 10 | 2 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 867.6 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 964 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501001110 | 80 | 10 | 2 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 890.12 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1309 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501001510 | 80 | 10 | 2 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1226.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501001610 | 80 | 10 | 2 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1326.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 107 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00064483 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1951 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501002010 | 80 | 10 | 2 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1696 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 137 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00024191 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501002110 | 80 | 10 | 2 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2051.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 165 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059642 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2564 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501101010 | 80 | 10 | 2 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 954 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 222 | 237 | 284 | 4 | 11 | 12 | 15 | 0.00013996 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1060 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501101110 | 80 | 10 | 2 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 979.2 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1440 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501101510 | 70 | 10 | 2 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1348.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 109 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1686 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2501101610 | 70 | 10 | 2 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1459.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 118 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00066276 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2146 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2501102010 | 70 | 10 | 2 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1865.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00032203 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2332 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2501102110 | 70 | 10 | 2 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2256 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 182 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00061841 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2501201010 | 80 | 10 | 2 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1041.3 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 227 | 243 | 293 | 4 | 12 | 13 | 15 | 0.00014858 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1157 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501201110 | 80 | 10 | 2 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1068.28 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 324 | 344 | 410 | 4 | 17 | 18 | 21 | 0.000272 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501201510 | 80 | 10 | 2 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1472 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 119 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025759 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501201610 | 80 | 10 | 2 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1591.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 128 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00091576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2341 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501202010 | 80 | 10 | 2 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2035.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 164 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00033101 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501202110 | 80 | 10 | 2 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2461.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 199 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00078234 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501401010 | 80 | 10 | 2 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1215 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 243 | 258 | 311 | 5 | 13 | 13 | 16 | 0.00024935 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1350 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501401110 | 80 | 10 | 2 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1246.44 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 101 | 356 | 377 | 447 | 5 | 18 | 19 | 23 | 0.00045941 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1833 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501401510 | 80 | 10 | 2 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1716.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 138 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2146 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501401610 | 80 | 10 | 2 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1857.08 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0012433 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2731 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501402010 | 80 | 10 | 2 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2374.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00053465 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2968 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501402110 | 80 | 10 | 2 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2872 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 232 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011789 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 3590 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501601010 | 80 | 10 | 2 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1387.8 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 258 | 274 | 330 | 6 | 13 | 14 | 17 | 0.00038304 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1542 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501601110 | 80 | 10 | 2 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1423.92 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 389 | 410 | 483 | 6 | 20 | 21 | 25 | 0.00070949 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 2094 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501601510 | 80 | 10 | 2 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1962.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 158 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00050396 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2453 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501601610 | 80 | 10 | 2 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2122.96 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 171 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0016307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3122 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501602010 | 80 | 10 | 2 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 2713.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 219 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00067276 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501602110 | 80 | 10 | 2 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3281.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 265 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0016729 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4102 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501801010 | 80 | 10 | 2 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1561.5 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 276 | 292 | 348 | 7 | 14 | 15 | 18 | 0.00055302 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1735 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501801110 | 80 | 10 | 2 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1602.08 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 129 | 426 | 447 | 520 | 7 | 22 | 23 | 27 | 0.001029 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2356 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501801510 | 60 | 10 | 2 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2207.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 178 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00066522 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2759 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2501801610 | 60 | 10 | 2 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2388.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 193 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0020811 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3512 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2501802010 | 60 | 10 | 2 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3052.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.00096672 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2501802110 | 60 | 10 | 2 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 3692 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 298 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0020114 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502001010 | 80 | 10 | 2 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1735.2 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 290 | 307 | 366 | 7 | 15 | 16 | 19 | 0.00059851 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1928 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502001110 | 80 | 10 | 2 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1780.24 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 144 | 457 | 478 | 556 | 7 | 24 | 25 | 29 | 0.00112 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2618 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502001510 | 80 | 10 | 2 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2452.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00085394 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502001610 | 80 | 10 | 2 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2653.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 214 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0025976 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3902 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502002010 | 80 | 10 | 2 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3392 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 274 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0011601 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4240 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502002110 | 80 | 10 | 2 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4102.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 331 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0026765 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 5128 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502201010 | 80 | 10 | 2 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1908.9 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 306 | 322 | 384 | 8 | 16 | 17 | 20 | 0.00081987 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2121 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502201110 | 80 | 10 | 2 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1958.4 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 158 | 490 | 511 | 593 | 8 | 25 | 26 | 31 | 0.0015391 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2880 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502201510 | 80 | 10 | 2 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2698.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 218 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0010716 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3373 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502201610 | 80 | 10 | 2 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2918.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 235 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0031831 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4292 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502202010 | 80 | 10 | 2 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3731.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 301 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0015537 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4664 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502202110 | 80 | 10 | 2 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 4512.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 364 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0034561 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 5641 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502401010 | 80 | 10 | 2 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2082.6 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 321 | 338 | 402 | 9 | 17 | 17 | 21 | 0.001085 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2314 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502401110 | 80 | 10 | 2 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2136.56 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 172 | 523 | 545 | 629 | 9 | 27 | 28 | 32 | 0.0020427 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 3142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502401510 | 80 | 10 | 2 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 2943.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 237 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0013198 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3679 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502401610 | 80 | 10 | 2 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3183.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 257 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0038405 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4682 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502402010 | 80 | 10 | 2 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 4070.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 328 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0018082 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 5088 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502402110 | 80 | 10 | 2 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 4923.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 397 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0039778 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 6154 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502601010 | 80 | 10 | 2 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2255.4 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 338 | 356 | 421 | 9 | 17 | 18 | 22 | 0.0011554 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502601110 | 80 | 10 | 2 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2314.04 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 187 | 558 | 581 | 666 | 10 | 29 | 30 | 34 | 0.0026367 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 3403 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502601510 | 60 | 10 | 2 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3188.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 257 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0015997 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 3986 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2502601610 | 60 | 10 | 2 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3449.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 278 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0045725 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 5073 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502602010 | 60 | 10 | 2 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4409.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 356 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0020866 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 5512 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2502602110 | 60 | 10 | 2 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5332.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 430 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.004956 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 6666 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502801010 | 60 | 10 | 2 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2429.1 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 196 | 318 | 331 | 374 | 10 | 16 | 17 | 19 | 0.0014814 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 2699 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502801110 | 60 | 10 | 2 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2492.2 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 201 | 557 | 573 | 630 | 10 | 29 | 30 | 33 | 0.0028056 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3665 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2502801510 | 80 | 10 | 2 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3433.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 277 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001913 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4292 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502801610 | 80 | 10 | 2 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3714.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 300 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005382 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 5463 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502802010 | 80 | 10 | 2 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4748.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 383 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0026313 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5936 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502802110 | 80 | 10 | 2 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5743.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 463 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0060645 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 7179 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265501010 | 80 | 10 | 2 | 65 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 504.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 41 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 561 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265501110 | 80 | 10 | 2 | 65 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 504.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 41 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 742 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265601010 | 80 | 10 | 2 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 605.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 673 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265601110 | 80 | 10 | 2 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 605.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 890 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265601510 | 80 | 10 | 2 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 823.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1029 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265601610 | 80 | 10 | 2 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 908.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1336 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265602010 | 80 | 10 | 2 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1148 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1435 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265602110 | 80 | 10 | 2 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1442.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1803 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265701010 | 80 | 10 | 2 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 706.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265701110 | 80 | 10 | 2 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 705.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1038 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265701510 | 70 | 10 | 2 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 960.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 77 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1201 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
265701610 | 70 | 10 | 2 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1060.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 85 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1559 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
265702010 | 70 | 10 | 2 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1339.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 108 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1674 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
265702110 | 70 | 10 | 2 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1683.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 136 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032624 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2104 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
265801010 | 80 | 10 | 2 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 807.3 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 65 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 897 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265801110 | 80 | 10 | 2 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 806.48 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255 | 274 | 331 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.8862 | 263.2129 | 44 | 47 | 57 | 0.018134 | 0.020547 | 0.029625 | 1.1 | 6 | 6.7 | 9 |  | 1186 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.8862 | 263.2129 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265801510 | 80 | 10 | 2 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1097.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1372 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265801610 | 80 | 10 | 2 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1211.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 98 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00042712 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1782 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265802010 | 80 | 10 | 2 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1530.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016875 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1913 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265802110 | 80 | 10 | 2 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1923.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 155 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044029 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265901010 | 80 | 10 | 2 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 908.1 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 73 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1009 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265901110 | 80 | 10 | 2 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 907.8 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 256 | 276 | 336 | 0.95 | 0.95 | 0.95 | 203.5725 | 219.4766 | 267.1889 | 44 | 47 | 57 | 0.019237 | 0.021784 | 0.031354 | 1.2 | 6 | 6.7 | 9 |  | 1335 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 203.5725 | 219.4766 | 267.1889 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265901510 | 80 | 10 | 2 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1235.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 100 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016264 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265901610 | 80 | 10 | 2 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1362.72 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 110 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00062691 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2004 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265902010 | 80 | 10 | 2 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1721.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 139 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00023478 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2152 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265902110 | 80 | 10 | 2 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2164 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 175 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00057443 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2705 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651001010 | 80 | 10 | 2 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1008.9 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1121 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651001110 | 80 | 10 | 2 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1008.44 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 81 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 257 | 277 | 340 | 0.95 | 0.95 | 0.95 | 204.3677 | 220.2718 | 270.3698 | 44 | 47 | 58 | 0.02034 | 0.023021 | 0.034183 | 1.3 | 6 | 6.7 | 9 |  | 1483 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 204.3677 | 220.2718 | 270.3698 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651001510 | 80 | 10 | 2 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1372 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 111 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00023966 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1715 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651001610 | 80 | 10 | 2 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1514.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 122 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00064483 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2227 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651002010 | 80 | 10 | 2 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1912.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 154 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00031305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2391 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651002110 | 80 | 10 | 2 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2404 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 194 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00072961 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3005 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651101010 | 80 | 10 | 2 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.7 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 222 | 237 | 284 | 5 | 11 | 12 | 15 | 0.00021129 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1233 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651101110 | 80 | 10 | 2 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.08 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 89 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 261 | 281 | 345 | 0.95 | 0.95 | 0.95 | 207.5486 | 223.4527 | 274.3458 | 45 | 48 | 59 | 0.022364 | 0.025233 | 0.037136 | 1.5 | 6 | 6.7 | 9 |  | 1631 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 207.5486 | 223.4527 | 274.3458 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651101510 | 70 | 10 | 2 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1509.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 122 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1887 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2651101610 | 70 | 10 | 2 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1666 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00089237 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2450 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2651102010 | 70 | 10 | 2 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2104 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 170 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00040407 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2630 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2651102110 | 70 | 10 | 2 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2644.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 213 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00090675 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2651201010 | 80 | 10 | 2 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1210.5 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 227 | 243 | 293 | 5 | 12 | 13 | 15 | 0.00022398 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1345 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651201110 | 80 | 10 | 2 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1210.4 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 260 | 281 | 349 | 0.95 | 0.95 | 0.95 | 206.7534 | 223.4527 | 277.5266 | 44 | 48 | 60 | 0.022547 | 0.026516 | 0.040214 | 1.6 | 6 | 6.7 | 9 |  | 1780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.7534 | 223.4527 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651201510 | 80 | 10 | 2 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1646.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 133 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034524 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2058 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651201610 | 80 | 10 | 2 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1816.96 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0011844 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2672 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651202010 | 80 | 10 | 2 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2295.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 185 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00050829 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2869 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651202110 | 80 | 10 | 2 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2884.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 233 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011067 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3606 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651401010 | 80 | 10 | 2 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1412.1 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 243 | 258 | 311 | 6 | 13 | 13 | 16 | 0.00034823 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1569 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651401110 | 80 | 10 | 2 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1411.68 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 114 | 356 | 377 | 447 | 6 | 18 | 19 | 23 | 0.00063987 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 263 | 284 | 359 | 0.95 | 0.95 | 0.95 | 209.139 | 225.8383 | 285.4787 | 45 | 49 | 61 | 0.025805 | 0.030215 | 0.045364 | 1.9 | 6 | 6.7 | 9 |  | 2076 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 209.139 | 225.8383 | 285.4787 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651401510 | 80 | 10 | 2 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1920.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 155 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00047453 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2401 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651401610 | 80 | 10 | 2 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2120.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 171 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0015586 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3118 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651402010 | 80 | 10 | 2 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2677.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 216 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00064169 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3347 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651402110 | 80 | 10 | 2 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3365.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 271 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0015788 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 4207 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651601010 | 80 | 10 | 2 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1614.6 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 130 | 258 | 274 | 330 | 7 | 13 | 14 | 17 | 0.00050754 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1794 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651601110 | 80 | 10 | 2 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1613.64 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 130 | 389 | 410 | 483 | 7 | 20 | 21 | 25 | 0.00093804 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 266 | 288 | 368 | 0.95 | 0.95 | 0.95 | 211.5246 | 229.0191 | 292.6355 | 45 | 49 | 63 | 0.0281 | 0.032875 | 0.052279 | 2.1 | 6 | 6.7 | 9 |  | 2373 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 211.5246 | 229.0191 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651601510 | 80 | 10 | 2 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2195.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 177 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00062916 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651601610 | 80 | 10 | 2 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2422.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0019946 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3563 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651602010 | 80 | 10 | 2 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3060.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 247 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0009253 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3826 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651602110 | 80 | 10 | 2 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3846.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 310 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0021524 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4808 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651801010 | 80 | 10 | 2 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1816.2 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 146 | 276 | 292 | 348 | 8 | 14 | 15 | 18 | 0.00070519 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 2018 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651801110 | 80 | 10 | 2 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1814.92 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 146 | 426 | 447 | 520 | 8 | 22 | 23 | 27 | 0.0013098 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 272 | 296 | 377 | 0.95 | 0.95 | 0.95 | 216.2958 | 235.3807 | 299.7924 | 47 | 51 | 64 | 0.032918 | 0.038242 | 0.058049 | 2.4 | 6 | 6.7 | 9 |  | 2669 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 216.2958 | 235.3807 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651801510 | 60 | 10 | 2 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2469.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 199 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00081069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2651801610 | 60 | 10 | 2 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2726.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 220 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0024957 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 4009 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2651802010 | 60 | 10 | 2 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3443.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 278 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0011131 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4304 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2651802110 | 60 | 10 | 2 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 4327.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 349 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.002834 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5409 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652001010 | 80 | 10 | 2 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2017.8 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 163 | 290 | 307 | 366 | 8 | 15 | 16 | 19 | 0.00076253 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2242 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652001110 | 80 | 10 | 2 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2016.88 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 163 | 457 | 478 | 556 | 8 | 24 | 25 | 29 | 0.0014244 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 273 | 297 | 386 | 0.95 | 0.95 | 0.95 | 217.091 | 236.1759 | 306.9492 | 47 | 51 | 66 | 0.035392 | 0.041093 | 0.06589 | 2.7 | 6 | 6.7 | 9 |  | 2966 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.091 | 236.1759 | 306.9492 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652001510 | 80 | 10 | 2 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2744 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 221 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0010207 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3430 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652001610 | 80 | 10 | 2 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 3028.72 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 244 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0035686 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 4454 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652002010 | 80 | 10 | 2 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3825.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 309 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0014945 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4782 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652002110 | 80 | 10 | 2 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4808 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 388 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0036299 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 6010 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652201010 | 80 | 10 | 2 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2219.4 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 306 | 322 | 384 | 9 | 16 | 17 | 20 | 0.0010147 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2466 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652201110 | 80 | 10 | 2 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2218.84 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 179 | 490 | 511 | 593 | 9 | 25 | 26 | 31 | 0.001902 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 275 | 300 | 396 | 0.95 | 0.95 | 0.95 | 218.6814 | 238.5616 | 314.9013 | 47 | 51 | 68 | 0.037866 | 0.043943 | 0.074292 | 2.9 | 6 | 6.7 | 9 |  | 3263 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 218.6814 | 238.5616 | 314.9013 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652201510 | 80 | 10 | 2 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3018.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 243 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0014638 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3773 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652201610 | 80 | 10 | 2 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 3331.32 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 269 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0042635 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4899 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652202010 | 80 | 10 | 2 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 4208 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 339 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0017425 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 5260 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652202110 | 80 | 10 | 2 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 5288.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 427 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.004546 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 6611 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652401010 | 80 | 10 | 2 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2421 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 195 | 321 | 338 | 402 | 10 | 17 | 17 | 21 | 0.0013125 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2690 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652401110 | 80 | 10 | 2 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2420.12 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 195 | 523 | 545 | 629 | 10 | 27 | 28 | 32 | 0.0024679 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 304 | 405 | 0.95 | 0.95 | 0.95 | 220.2718 | 241.7424 | 322.0581 | 47 | 52 | 69 | 0.04034 | 0.048475 | 0.081117 | 3.2 | 6 | 6.7 | 9 |  | 3559 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 241.7424 | 322.0581 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652401510 | 80 | 10 | 2 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3292.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 266 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0017585 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652401610 | 80 | 10 | 2 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3634.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 293 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005034 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652402010 | 80 | 10 | 2 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 4590.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 370 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0022305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 5738 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652402110 | 80 | 10 | 2 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 5769.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 465 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0055883 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 7212 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652601010 | 80 | 10 | 2 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2623.5 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 212 | 338 | 356 | 421 | 11 | 17 | 18 | 22 | 0.001659 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2915 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652601110 | 80 | 10 | 2 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2622.08 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 211 | 558 | 581 | 666 | 11 | 29 | 30 | 34 | 0.0031278 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 311 | 414 | 0.95 | 0.95 | 0.95 | 224.2479 | 247.3088 | 329.215 | 48 | 53 | 71 | 0.044479 | 0.053231 | 0.090513 | 3.5 | 6 | 6.7 | 9 |  | 3856 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 247.3088 | 329.215 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652601510 | 60 | 10 | 2 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3567.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 288 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0020868 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4459 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2652601610 | 60 | 10 | 2 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3937.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 318 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0058826 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 5790 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652602010 | 60 | 10 | 2 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4973.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 401 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0027893 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 6217 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2652602110 | 60 | 10 | 2 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6250.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 504 | #VALUE! | #VALUE! | #VALUE! | 26 | #VALUE! | #VALUE! | #VALUE! | 0.0067624 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 7813 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652801010 | 60 | 10 | 2 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2825.1 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 228 | 318 | 331 | 374 | 12 | 16 | 17 | 19 | 0.002057 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3139 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652801110 | 60 | 10 | 2 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2823.36 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 228 | 557 | 573 | 630 | 12 | 29 | 30 | 33 | 0.0038875 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222 | 245 | 326 | 0.95 | 0.95 | 0.95 | 176.5356 | 194.8253 | 259.2369 | 38 | 42 | 56 | 0.030851 | 0.03696 | 0.062174 | 3.7 | 6 | 6.7 | 9 |  | 4152 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.5356 | 194.8253 | 259.2369 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2652801510 | 80 | 10 | 2 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3841.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 310 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0024501 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4802 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652801610 | 80 | 10 | 2 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4240.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 342 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0075868 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 6236 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652802010 | 80 | 10 | 2 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5356 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 432 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.0031473 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 6695 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652802110 | 80 | 10 | 2 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6731.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 543 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0080738 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 8414 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295601010 | 80 | 10 | 2 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 754.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 838 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295601110 | 80 | 10 | 2 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1055 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295601510 | 80 | 10 | 2 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 968 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1210 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295601610 | 80 | 10 | 2 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 1093.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1608 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295602010 | 80 | 10 | 2 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1364.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1706 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295602110 | 80 | 10 | 2 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1832 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2290 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295701010 | 80 | 10 | 2 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 879.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 977 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295701110 | 80 | 10 | 2 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1231 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295701510 | 70 | 10 | 2 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1128.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 91 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00014954 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1411 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
295701610 | 70 | 10 | 2 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1275.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 103 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00041403 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
295702010 | 70 | 10 | 2 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1592.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 128 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1991 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
295702110 | 70 | 10 | 2 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 2136.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 172 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00053044 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2671 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
295801010 | 80 | 10 | 2 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1005.3 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 1117 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295801110 | 80 | 10 | 2 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 77 | 260 | 279 | 337 | 4 | 13 | 14 | 17 | 0.00020308 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 214 | 230 | 277 | 0.95 | 0.95 | 0.95 | 170.1739 | 182.8972 | 220.2718 | 37 | 39 | 47 | 0.013064 | 0.014431 | 0.020547 | 1.1 | 6 | 6.7 | 9 |  | 1406 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.1739 | 182.8972 | 220.2718 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295801510 | 80 | 10 | 2 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1290.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 104 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295801610 | 80 | 10 | 2 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1457.92 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 118 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00060898 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295802010 | 80 | 10 | 2 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1820 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0002951 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295802110 | 80 | 10 | 2 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 2442.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 197 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00067687 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295901010 | 80 | 10 | 2 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1130.4 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 205 | 220 | 266 | 5 | 11 | 11 | 14 | 0.00018592 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1256 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295901110 | 80 | 10 | 2 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 215 | 231 | 281 | 0.95 | 0.95 | 0.95 | 170.9691 | 183.6924 | 223.4527 | 37 | 39 | 48 | 0.013881 | 0.015326 | 0.022667 | 1.2 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.9691 | 183.6924 | 223.4527 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295901510 | 80 | 10 | 2 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1451.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 117 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1814 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295901610 | 80 | 10 | 2 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1640.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 132 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00084561 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2412 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295902010 | 80 | 10 | 2 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 2048 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 165 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00038208 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2560 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295902110 | 80 | 10 | 2 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2747.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 222 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00084461 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3434 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951001010 | 80 | 10 | 2 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1256.4 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 212 | 227 | 275 | 5 | 11 | 12 | 14 | 0.0001986 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1396 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951001110 | 80 | 10 | 2 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 291 | 311 | 374 | 5 | 15 | 16 | 19 | 0.00035791 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216 | 232 | 285 | 0.95 | 0.95 | 0.95 | 171.7643 | 184.4876 | 226.6335 | 37 | 40 | 49 | 0.014697 | 0.01701 | 0.024896 | 1.3 | 6 | 6.7 | 9 |  | 1758 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.7643 | 184.4876 | 226.6335 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951001510 | 80 | 10 | 2 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1612.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 130 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032186 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 2016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951001610 | 80 | 10 | 2 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1822.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0011255 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2680 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951002010 | 80 | 10 | 2 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2275.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 183 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00039308 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951002110 | 80 | 10 | 2 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 3052.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0012062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951101010 | 80 | 10 | 2 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1382.4 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 222 | 237 | 284 | 6 | 11 | 12 | 15 | 0.00029601 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1536 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951101110 | 80 | 10 | 2 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 218 | 235 | 289 | 0.95 | 0.95 | 0.95 | 173.3547 | 186.8732 | 229.8143 | 37 | 40 | 49 | 0.015514 | 0.017945 | 0.026226 | 1.5 | 6 | 6.7 | 9 |  | 1934 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.3547 | 186.8732 | 229.8143 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951101510 | 70 | 10 | 2 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1774.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 143 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00033355 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2218 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2951101610 | 70 | 10 | 2 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 2004.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 162 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001155 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2948 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2951102010 | 70 | 10 | 2 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2502.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 202 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00049511 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 3128 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2951102110 | 70 | 10 | 2 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 3356.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 271 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0014376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4196 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2951201010 | 80 | 10 | 2 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1507.5 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 122 | 227 | 243 | 293 | 6 | 12 | 13 | 15 | 0.00031342 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1675 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951201110 | 80 | 10 | 2 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 116 | 324 | 344 | 410 | 6 | 17 | 18 | 21 | 0.00057024 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 218 | 235 | 293 | 0.95 | 0.95 | 0.95 | 173.3547 | 186.8732 | 232.9951 | 37 | 40 | 50 | 0.016331 | 0.01888 | 0.028613 | 1.6 | 6 | 6.7 | 9 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.3547 | 186.8732 | 232.9951 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951201510 | 80 | 10 | 2 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1935.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044509 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2419 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951201610 | 80 | 10 | 2 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 2186.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 176 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0014865 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3216 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951202010 | 80 | 10 | 2 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2730.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 220 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00061062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3413 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951202110 | 80 | 10 | 2 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 3663.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 295 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0016935 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4579 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951401010 | 80 | 10 | 2 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1758.6 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 243 | 258 | 311 | 7 | 13 | 13 | 16 | 0.00046205 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1954 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951401110 | 80 | 10 | 2 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 356 | 377 | 447 | 7 | 18 | 19 | 23 | 0.00084707 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 220 | 238 | 300 | 0.95 | 0.95 | 0.95 | 174.9451 | 189.2588 | 238.5616 | 38 | 41 | 51 | 0.018873 | 0.021721 | 0.032541 | 1.9 | 6 | 6.7 | 9 |  | 2461 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 189.2588 | 238.5616 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951401510 | 80 | 10 | 2 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2257.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 182 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059309 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951401610 | 80 | 10 | 2 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2551.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 206 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0022918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3752 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951402010 | 80 | 10 | 2 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 3185.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 257 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.00088388 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3982 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951402110 | 80 | 10 | 2 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 4273.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 345 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0025438 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5342 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320501010 | 80 | 10 | 3 | 20 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 295.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 24 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6.3694e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 328 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
320601010 | 80 | 10 | 3 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 353.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.1473e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 393 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
320601510 | 80 | 10 | 3 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 523.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4254e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 654 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
320602010 | 80 | 10 | 3 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 735.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4.0779e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 919 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320701010 | 80 | 10 | 3 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 413.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 33 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 459 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
320701510 | 70 | 10 | 3 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 610.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 49 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.5819e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 763 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
320702010 | 70 | 10 | 3 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 857.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 69 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.4184e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1072 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
320801010 | 80 | 10 | 3 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 471.6 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 38 | 198 | 213 | 257 | 2 | 10 | 11 | 13 | 3.1383e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 524 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
320801510 | 80 | 10 | 3 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 697.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 56 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.8533e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 872 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
320802010 | 80 | 10 | 3 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 980.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 79 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.6905e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320901010 | 80 | 10 | 3 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 531 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 43 | 205 | 220 | 266 | 2 | 11 | 11 | 14 | 3.3972e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 590 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
320901510 | 80 | 10 | 3 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 784.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 63 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 6.1246e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 981 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320902010 | 80 | 10 | 3 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1103.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00012248 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1379 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201001010 | 80 | 10 | 3 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 589.5 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 48 | 212 | 227 | 275 | 2 | 11 | 12 | 14 | 3.656e-05 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 655 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3201001510 | 80 | 10 | 3 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 872 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 70 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011055 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1090 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201002010 | 80 | 10 | 3 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1225.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00012648 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 1532 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201101010 | 80 | 10 | 3 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 648.9 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 52 | 222 | 237 | 284 | 3 | 11 | 12 | 15 | 8.2405e-05 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 721 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201101510 | 70 | 10 | 3 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 959.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 77 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011501 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1199 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
3201102010 | 70 | 10 | 3 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1348 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 109 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00018516 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 1685 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3201201010 | 80 | 10 | 3 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 707.4 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 227 | 243 | 293 | 3 | 12 | 13 | 15 | 8.7635e-05 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 786 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201201510 | 80 | 10 | 3 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1046.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 84 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00011946 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1308 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201202010 | 80 | 10 | 3 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 1470.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 119 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00019063 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1838 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201401010 | 80 | 10 | 3 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 825.3 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 243 | 258 | 311 | 3 | 13 | 13 | 16 | 9.8096e-05 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 917 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201401510 | 80 | 10 | 3 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1220.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 98 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00019536 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1526 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201402010 | 80 | 10 | 3 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1716 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 138 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00027044 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2145 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201601010 | 80 | 10 | 3 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 943.2 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 258 | 274 | 330 | 4 | 13 | 14 | 17 | 0.00018304 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1048 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201601510 | 80 | 10 | 3 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1395.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 113 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00029344 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201602010 | 80 | 10 | 3 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 1960.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 158 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00036692 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2451 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201801010 | 80 | 10 | 3 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1061.1 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 276 | 292 | 348 | 4 | 14 | 15 | 18 | 0.00020027 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1179 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201801510 | 60 | 10 | 3 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 1569.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 127 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00041539 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1962 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3201802010 | 60 | 10 | 3 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 2206.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 178 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00048104 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2758 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3202001010 | 80 | 10 | 3 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1179 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 95 | 290 | 307 | 366 | 5 | 15 | 16 | 19 | 0.00032548 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1310 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202001510 | 80 | 10 | 3 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 1744 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 141 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00043878 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2180 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202002010 | 80 | 10 | 3 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 2451.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00061375 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3064 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202201010 | 80 | 10 | 3 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1296.9 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 306 | 322 | 384 | 5 | 16 | 17 | 20 | 0.00035085 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 1441 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202201510 | 80 | 10 | 3 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 1918.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 155 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00059228 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2398 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202202010 | 80 | 10 | 3 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 2696 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 217 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00076596 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3370 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202401010 | 80 | 10 | 3 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1414.8 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 321 | 338 | 402 | 6 | 17 | 17 | 21 | 0.0005223 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 1572 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202401510 | 80 | 10 | 3 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 2092.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 169 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00077342 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2616 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202402010 | 80 | 10 | 3 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 2941.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 237 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00093856 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3677 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202601010 | 80 | 10 | 3 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1532.7 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 124 | 338 | 356 | 421 | 6 | 17 | 18 | 22 | 0.00055711 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 1703 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202601510 | 60 | 10 | 3 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2267.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 183 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00080948 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 2834 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3202602010 | 60 | 10 | 3 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3186.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 257 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0011324 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 3983 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3202801010 | 60 | 10 | 3 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1650.6 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 133 | 318 | 331 | 374 | 7 | 16 | 17 | 19 | 0.00078045 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 1834 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3202801510 | 80 | 10 | 3 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2441.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 197 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0010269 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3052 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202802010 | 80 | 10 | 3 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3432 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 277 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0013484 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 4290 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330501010 | 80 | 10 | 3 | 30 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 371.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 30 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 413 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330501110 | 80 | 10 | 3 | 30 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 381.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 31 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 561 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330601010 | 80 | 10 | 3 | 30 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 446.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 496 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330601110 | 80 | 10 | 3 | 30 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 457.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 37 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 673 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330601510 | 80 | 10 | 3 | 30 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 652 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 815 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330601610 | 80 | 10 | 3 | 30 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 603.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 888 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330602010 | 80 | 10 | 3 | 30 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 915.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1144 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330602110 | 80 | 10 | 3 | 30 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 935.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 75 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1169 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330701010 | 80 | 10 | 3 | 30 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 520.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 578 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330701110 | 80 | 10 | 3 | 30 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 533.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330701510 | 70 | 10 | 3 | 30 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 760.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 61 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 5.5819e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 951 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
330701610 | 70 | 10 | 3 | 30 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 704.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 57 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 0.00015302 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1036 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
330702010 | 70 | 10 | 3 | 30 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1067.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 86 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 7.4184e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1334 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
330702110 | 70 | 10 | 3 | 30 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1091.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 88 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017042 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1364 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
330801010 | 80 | 10 | 3 | 30 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 594.9 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 48 | 198 | 213 | 257 | 2 | 10 | 11 | 13 | 3.1383e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 661 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330801110 | 80 | 10 | 3 | 30 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 609.96 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 897 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330801510 | 80 | 10 | 3 | 30 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 869.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 70 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00010164 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330801610 | 80 | 10 | 3 | 30 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 805.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 65 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 0.00015844 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1184 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330802010 | 80 | 10 | 3 | 30 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1220 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 98 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011849 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1525 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330802110 | 80 | 10 | 3 | 30 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1246.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 101 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017841 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 1558 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330901010 | 80 | 10 | 3 | 30 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 668.7 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 205 | 220 | 266 | 3 | 11 | 11 | 14 | 7.1943e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 743 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330901110 | 80 | 10 | 3 | 30 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 686.12 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 55 | 276 | 295 | 355 | 3 | 14 | 15 | 18 | 0.00012974 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 1009 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
330901510 | 80 | 10 | 3 | 30 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 978.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 79 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.0001061 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1223 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330901610 | 80 | 10 | 3 | 30 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 905.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 73 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00028576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1332 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330902010 | 80 | 10 | 3 | 30 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1372 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 111 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00017422 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1715 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330902110 | 80 | 10 | 3 | 30 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1402.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 113 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00026412 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 1753 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301001010 | 80 | 10 | 3 | 30 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 743.4 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 60 | 212 | 227 | 275 | 3 | 11 | 12 | 14 | 7.7174e-05 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 826 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301001110 | 80 | 10 | 3 | 30 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 762.28 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 291 | 311 | 374 | 3 | 15 | 16 | 19 | 0.0001402 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1121 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301001510 | 80 | 10 | 3 | 30 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1087.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 88 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1359 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301001610 | 80 | 10 | 3 | 30 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1006.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 81 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00029467 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1480 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301002010 | 80 | 10 | 3 | 30 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1524.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00017969 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 1906 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301002110 | 80 | 10 | 3 | 30 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 1558.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 126 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036904 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 1948 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301101010 | 80 | 10 | 3 | 30 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 818.1 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 222 | 237 | 284 | 3 | 11 | 12 | 15 | 8.2405e-05 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 909 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301101110 | 80 | 10 | 3 | 30 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 838.44 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1233 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301101510 | 70 | 10 | 3 | 30 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1196 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017573 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1495 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3301101610 | 70 | 10 | 3 | 30 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1107.04 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00046639 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 1628 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3301102010 | 70 | 10 | 3 | 30 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1677.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 135 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00024904 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2097 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3301102110 | 70 | 10 | 3 | 30 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 1714.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 138 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00038331 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2143 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3301201010 | 80 | 10 | 3 | 30 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 891.9 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 227 | 243 | 293 | 4 | 12 | 13 | 15 | 0.00014858 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 991 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301201110 | 80 | 10 | 3 | 30 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 914.6 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 324 | 344 | 410 | 4 | 17 | 18 | 21 | 0.000272 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301201510 | 80 | 10 | 3 | 30 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1304.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 105 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00018227 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1631 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301201610 | 80 | 10 | 3 | 30 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1207.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 97 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00047948 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 1776 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301202010 | 80 | 10 | 3 | 30 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 1829.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 148 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00033101 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2287 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301202110 | 80 | 10 | 3 | 30 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 1870.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 151 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0005121 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2338 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301401010 | 80 | 10 | 3 | 30 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1040.4 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 243 | 258 | 311 | 4 | 13 | 13 | 16 | 0.00016581 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301401110 | 80 | 10 | 3 | 30 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1066.92 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 356 | 377 | 447 | 4 | 18 | 19 | 23 | 0.00030646 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1569 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301401510 | 80 | 10 | 3 | 30 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1522.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00027551 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301401610 | 80 | 10 | 3 | 30 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1408.96 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 114 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00071654 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2072 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301402010 | 80 | 10 | 3 | 30 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2134.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 172 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00043706 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301402110 | 80 | 10 | 3 | 30 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2181.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 176 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00068438 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 2727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301601010 | 80 | 10 | 3 | 30 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1189.8 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 258 | 274 | 330 | 5 | 13 | 14 | 17 | 0.00027473 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1322 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301601110 | 80 | 10 | 3 | 30 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1219.92 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 389 | 410 | 483 | 5 | 20 | 21 | 25 | 0.00051016 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 1794 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301601510 | 80 | 10 | 3 | 30 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 1739.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 140 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00039201 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2174 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301601610 | 80 | 10 | 3 | 30 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 1610.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 130 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.0010093 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2368 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301602010 | 80 | 10 | 3 | 30 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 2440 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 197 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00056102 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3050 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301602110 | 80 | 10 | 3 | 30 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 2493.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 201 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0008878 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 3117 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301801010 | 80 | 10 | 3 | 30 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1338.3 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 108 | 276 | 292 | 348 | 6 | 14 | 15 | 18 | 0.00041786 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1487 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301801110 | 80 | 10 | 3 | 30 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1372.24 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 111 | 426 | 447 | 520 | 6 | 22 | 23 | 27 | 0.00077912 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2018 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301801510 | 60 | 10 | 3 | 30 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 1956.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 158 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0005334 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2446 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3301801610 | 60 | 10 | 3 | 30 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 1811.52 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 146 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001361 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 2664 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3301802010 | 60 | 10 | 3 | 30 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 2744.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 221 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00070383 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3431 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3301802110 | 60 | 10 | 3 | 30 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 2804.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 226 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0013233 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3506 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302001010 | 80 | 10 | 3 | 30 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1486.8 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 120 | 290 | 307 | 366 | 6 | 15 | 16 | 19 | 0.00045267 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1652 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302001110 | 80 | 10 | 3 | 30 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1524.56 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 123 | 457 | 478 | 556 | 6 | 24 | 25 | 29 | 0.00084875 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2242 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302001510 | 80 | 10 | 3 | 30 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2174.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 175 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00070129 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2718 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302001610 | 80 | 10 | 3 | 30 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2012.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 162 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0014199 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 2960 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302002010 | 80 | 10 | 3 | 30 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3049.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0010081 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3812 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302002110 | 80 | 10 | 3 | 30 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 3116.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 251 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0016204 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 3896 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302201010 | 80 | 10 | 3 | 30 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1635.3 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 132 | 306 | 322 | 384 | 7 | 16 | 17 | 20 | 0.00064399 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 1817 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302201110 | 80 | 10 | 3 | 30 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1676.88 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 490 | 511 | 593 | 7 | 25 | 26 | 31 | 0.001211 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2466 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302201510 | 80 | 10 | 3 | 30 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2392 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 193 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00089719 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2990 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302201610 | 80 | 10 | 3 | 30 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2214.08 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 179 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0018471 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 3256 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302202010 | 80 | 10 | 3 | 30 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3354.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 271 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0012072 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4193 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302202110 | 80 | 10 | 3 | 30 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 3428.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 277 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0019552 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 4286 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302401010 | 80 | 10 | 3 | 30 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1783.8 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 144 | 321 | 338 | 402 | 7 | 17 | 17 | 21 | 0.00068948 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 1982 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302401110 | 80 | 10 | 3 | 30 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1829.2 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 148 | 523 | 545 | 629 | 8 | 27 | 28 | 32 | 0.0016538 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 2690 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302401510 | 80 | 10 | 3 | 30 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 2609.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 210 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0011226 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3262 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302401610 | 80 | 10 | 3 | 30 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 2415.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0023406 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 3552 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302402010 | 80 | 10 | 3 | 30 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 3659.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 295 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0014282 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4574 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302402110 | 80 | 10 | 3 | 30 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 3740 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 302 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0026262 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 4675 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302601010 | 80 | 10 | 3 | 30 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1933.2 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 338 | 356 | 421 | 8 | 17 | 18 | 22 | 0.00093455 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2148 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302601110 | 80 | 10 | 3 | 30 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1982.2 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 160 | 558 | 581 | 666 | 8 | 29 | 30 | 34 | 0.0017685 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 2915 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302601510 | 60 | 10 | 3 | 30 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2826.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 228 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.001379 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 3533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3302601610 | 60 | 10 | 3 | 30 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2616.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 211 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0029035 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 3848 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302602010 | 60 | 10 | 3 | 30 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3964.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 320 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.001874 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 4956 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3302602110 | 60 | 10 | 3 | 30 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4052 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 327 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.003071 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 5065 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302801010 | 60 | 10 | 3 | 30 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2081.7 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 318 | 331 | 374 | 9 | 16 | 17 | 19 | 0.0012257 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 2313 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302801110 | 60 | 10 | 3 | 30 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2134.52 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 172 | 557 | 573 | 630 | 9 | 29 | 30 | 33 | 0.0023241 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3139 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3302801510 | 80 | 10 | 3 | 30 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3044 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 245 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0016677 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3805 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302801610 | 80 | 10 | 3 | 30 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2817.92 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 227 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0035385 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 4144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302802010 | 80 | 10 | 3 | 30 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4269.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 344 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0021592 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5337 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302802110 | 80 | 10 | 3 | 30 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4363.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 352 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0035594 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 5454 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3303001010 | 40 | 10 | 3 | 30 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2230.2 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 180 | 298 | 305 | 327 | 9 | 15 | 16 | 17 | 0.001296 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 2478 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3303001110 | 40 | 10 | 3 | 30 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2286.84 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 184 | 556 | 564 | 594 | 9 | 29 | 29 | 31 | 0.0024648 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 175 | 193 | 257 | 0.95 | 0.95 | 0.95 | 139.1609 | 153.4746 | 204.3677 | 30 | 33 | 44 | 0.021281 | 0.02526 | 0.042407 | 4 | 6 | 6.7 | 9 |  | 3363 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 139.1609 | 153.4746 | 204.3677 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3303001510 | 60 | 10 | 3 | 30 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3261.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 263 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0019902 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 4077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3303001610 | 60 | 10 | 3 | 30 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3019.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 243 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0042484 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 4440 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3303002010 | 60 | 10 | 3 | 30 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4574.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 369 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0024693 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 5718 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3303002110 | 60 | 10 | 3 | 30 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4675.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 377 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0040931 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 5844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
340501010 | 80 | 10 | 3 | 40 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 35 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 482 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340501110 | 80 | 10 | 3 | 40 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 429.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 35 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 632 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340601010 | 80 | 10 | 3 | 40 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 578 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340601110 | 80 | 10 | 3 | 40 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 515.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 758 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340601510 | 80 | 10 | 3 | 40 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 752.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 941 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340601610 | 80 | 10 | 3 | 40 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 693.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1020 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340602010 | 80 | 10 | 3 | 40 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1054.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1318 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340602110 | 80 | 10 | 3 | 40 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1091.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1364 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340701010 | 80 | 10 | 3 | 40 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 606.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 674 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340701110 | 80 | 10 | 3 | 40 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 601.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 885 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340701510 | 70 | 10 | 3 | 40 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 878.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 71 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
340701610 | 70 | 10 | 3 | 40 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 809.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 65 | #VALUE! | #VALUE! | #VALUE! | 3 | #VALUE! | #VALUE! | #VALUE! | 0.00015302 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1190 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
340702010 | 70 | 10 | 3 | 40 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1229.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00011449 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1537 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
340702110 | 70 | 10 | 3 | 40 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1273.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 103 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00017042 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1592 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
340801010 | 80 | 10 | 3 | 40 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 56 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 770 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340801110 | 80 | 10 | 3 | 40 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 687.48 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 55 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 1011 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340801510 | 80 | 10 | 3 | 40 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1003.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 81 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00010164 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1254 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340801610 | 80 | 10 | 3 | 40 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 924.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 75 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1360 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340802010 | 80 | 10 | 3 | 40 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1405.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 113 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016875 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1757 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340802110 | 80 | 10 | 3 | 40 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1455.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 117 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025318 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 1819 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340901010 | 80 | 10 | 3 | 40 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 780.3 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 205 | 220 | 266 | 3 | 11 | 11 | 14 | 7.1943e-05 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 867 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340901110 | 80 | 10 | 3 | 40 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 773.84 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 276 | 295 | 355 | 3 | 14 | 15 | 18 | 0.00012974 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 1138 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340901510 | 80 | 10 | 3 | 40 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1128.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 91 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016264 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1411 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340901610 | 80 | 10 | 3 | 40 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1040.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 84 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00028576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1530 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340902010 | 80 | 10 | 3 | 40 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1580.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 127 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00023478 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1976 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340902110 | 80 | 10 | 3 | 40 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1637.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 132 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00035477 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2047 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401001010 | 80 | 10 | 3 | 40 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 866.7 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 963 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401001110 | 80 | 10 | 3 | 40 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 859.52 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1264 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401001510 | 80 | 10 | 3 | 40 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1254.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 101 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016918 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1568 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401001610 | 80 | 10 | 3 | 40 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1156 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 93 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.0004533 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1700 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401002010 | 80 | 10 | 3 | 40 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1756.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 142 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00024191 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2196 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401002110 | 80 | 10 | 3 | 40 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 1819.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 147 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0004762 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2274 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401101010 | 80 | 10 | 3 | 40 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 953.1 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 222 | 237 | 284 | 4 | 11 | 12 | 15 | 0.00013996 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1059 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401101110 | 80 | 10 | 3 | 40 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 945.2 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401101510 | 70 | 10 | 3 | 40 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1380 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 111 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1725 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3401101610 | 70 | 10 | 3 | 40 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1271.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 103 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00046639 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 1870 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3401102010 | 70 | 10 | 3 | 40 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 1932.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00032203 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2416 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3401102110 | 70 | 10 | 3 | 40 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2000.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 161 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00049415 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2501 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3401201010 | 80 | 10 | 3 | 40 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1040.4 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 227 | 243 | 293 | 4 | 12 | 13 | 15 | 0.00014858 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401201110 | 80 | 10 | 3 | 40 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1031.56 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 83 | 324 | 344 | 410 | 4 | 17 | 18 | 21 | 0.000272 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1517 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401201510 | 80 | 10 | 3 | 40 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1505.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 121 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00025759 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 1882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401201610 | 80 | 10 | 3 | 40 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1387.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 112 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00068069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2040 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401202010 | 80 | 10 | 3 | 40 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2108 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 170 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00041507 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2635 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401202110 | 80 | 10 | 3 | 40 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2183.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 176 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0006404 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2729 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401401010 | 80 | 10 | 3 | 40 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1213.2 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 243 | 258 | 311 | 5 | 13 | 13 | 16 | 0.00024935 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1348 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401401110 | 80 | 10 | 3 | 40 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1203.6 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 97 | 356 | 377 | 447 | 5 | 18 | 19 | 23 | 0.00045941 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1770 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401401510 | 80 | 10 | 3 | 40 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1756 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 142 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00036862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2195 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401401610 | 80 | 10 | 3 | 40 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1618.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 131 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00096253 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2380 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401402010 | 80 | 10 | 3 | 40 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2459.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00053465 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3074 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401402110 | 80 | 10 | 3 | 40 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2547.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 205 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00099995 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 3184 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401601010 | 80 | 10 | 3 | 40 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1386.9 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 258 | 274 | 330 | 6 | 13 | 14 | 17 | 0.00038304 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1541 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401601110 | 80 | 10 | 3 | 40 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1374.96 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 111 | 389 | 410 | 483 | 6 | 20 | 21 | 25 | 0.00070949 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 2022 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401601510 | 80 | 10 | 3 | 40 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2007.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 162 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00050396 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2509 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401601610 | 80 | 10 | 3 | 40 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 1849.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 149 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0013022 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 2720 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401602010 | 80 | 10 | 3 | 40 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 2811.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 227 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0007942 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3514 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401602110 | 80 | 10 | 3 | 40 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 2910.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 235 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012511 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 3638 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401801010 | 80 | 10 | 3 | 40 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1559.7 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 276 | 292 | 348 | 7 | 14 | 15 | 18 | 0.00055302 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1733 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401801110 | 80 | 10 | 3 | 40 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1547 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 125 | 426 | 447 | 520 | 6 | 22 | 23 | 27 | 0.00077912 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2275 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401801510 | 60 | 10 | 3 | 40 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2257.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 182 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00066522 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3401801610 | 60 | 10 | 3 | 40 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2080.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 168 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0017028 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3060 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3401802010 | 60 | 10 | 3 | 40 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3162.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 255 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.00096672 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3953 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3401802110 | 60 | 10 | 3 | 40 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 3274.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 264 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001767 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4093 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402001010 | 80 | 10 | 3 | 40 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1733.4 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 290 | 307 | 366 | 7 | 15 | 16 | 19 | 0.00059851 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 1926 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402001110 | 80 | 10 | 3 | 40 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1719.04 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 139 | 457 | 478 | 556 | 7 | 24 | 25 | 29 | 0.00112 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2528 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402001510 | 80 | 10 | 3 | 40 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2508.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 202 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00085394 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402001610 | 80 | 10 | 3 | 40 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2312 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 186 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0021676 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3400 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402002010 | 80 | 10 | 3 | 40 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3513.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 283 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0013222 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402002110 | 80 | 10 | 3 | 40 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 3638.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 293 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0021174 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 4548 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402201010 | 80 | 10 | 3 | 40 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1907.1 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 306 | 322 | 384 | 8 | 16 | 17 | 20 | 0.00081987 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2119 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402201110 | 80 | 10 | 3 | 40 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1891.08 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 153 | 490 | 511 | 593 | 8 | 25 | 26 | 31 | 0.0015391 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 2781 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402201510 | 80 | 10 | 3 | 40 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 2760 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 223 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012605 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3450 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402201610 | 80 | 10 | 3 | 40 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2543.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 205 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0026996 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 3740 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402202010 | 80 | 10 | 3 | 40 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 3864.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 312 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0015537 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4831 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402202110 | 80 | 10 | 3 | 40 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 4002.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 323 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.002808 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 5003 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402401010 | 80 | 10 | 3 | 40 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2079.9 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 321 | 338 | 402 | 9 | 17 | 17 | 21 | 0.001085 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2311 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402401110 | 80 | 10 | 3 | 40 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2063.12 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 166 | 523 | 545 | 629 | 9 | 27 | 28 | 32 | 0.0020427 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 3034 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402401510 | 80 | 10 | 3 | 40 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3010.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 243 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0015318 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3763 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402401610 | 80 | 10 | 3 | 40 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 2774.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 224 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0033016 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4080 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402402010 | 80 | 10 | 3 | 40 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 4216 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 340 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0020141 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 5270 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402402110 | 80 | 10 | 3 | 40 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 4366.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 352 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0032692 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 5458 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402601010 | 80 | 10 | 3 | 40 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2253.6 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 338 | 356 | 421 | 9 | 17 | 18 | 22 | 0.0011554 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2504 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402601110 | 80 | 10 | 3 | 40 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2234.48 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 180 | 558 | 581 | 666 | 9 | 29 | 30 | 34 | 0.0021834 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 3286 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402601510 | 60 | 10 | 3 | 40 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3261.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 263 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0018357 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3402601610 | 60 | 10 | 3 | 40 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3005.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 242 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00342 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 4420 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402602010 | 60 | 10 | 3 | 40 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4568 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 368 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0023101 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 5710 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3402602110 | 60 | 10 | 3 | 40 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4729.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 381 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0041517 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 5912 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402801010 | 60 | 10 | 3 | 40 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2426.4 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 196 | 318 | 331 | 374 | 10 | 16 | 17 | 19 | 0.0014814 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 2696 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402801110 | 60 | 10 | 3 | 40 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2406.52 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 194 | 557 | 573 | 630 | 10 | 29 | 30 | 33 | 0.0028056 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3539 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3402801510 | 80 | 10 | 3 | 40 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3512 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 283 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0021738 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4390 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402801610 | 80 | 10 | 3 | 40 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3236.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 261 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0041124 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 4760 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402802010 | 80 | 10 | 3 | 40 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4919.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 397 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0026313 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 6149 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402802110 | 80 | 10 | 3 | 40 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5093.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 411 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0047347 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 6367 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3403001010 | 40 | 10 | 3 | 40 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2600.1 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 210 | 298 | 305 | 327 | 11 | 15 | 16 | 17 | 0.0018582 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 2889 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3403001110 | 40 | 10 | 3 | 40 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2578.56 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 208 | 556 | 564 | 594 | 11 | 29 | 29 | 31 | 0.0035263 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 175 | 193 | 257 | 0.95 | 0.95 | 0.95 | 139.1609 | 153.4746 | 204.3677 | 30 | 33 | 44 | 0.021281 | 0.02526 | 0.042407 | 4 | 6 | 6.7 | 9 |  | 3792 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 139.1609 | 153.4746 | 204.3677 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3403001510 | 60 | 10 | 3 | 40 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3763.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 303 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0025473 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 4704 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3403001610 | 60 | 10 | 3 | 40 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3468 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 280 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0048816 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 5100 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3403002010 | 60 | 10 | 3 | 40 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5270.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 425 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.0032498 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 6588 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3403002110 | 60 | 10 | 3 | 40 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5457.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 440 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0058255 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 6822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
350501010 | 80 | 10 | 3 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 484.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 538 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350501110 | 80 | 10 | 3 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 471.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 38 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 693 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350601010 | 80 | 10 | 3 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 581.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 646 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350601110 | 80 | 10 | 3 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 565.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 832 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350601510 | 80 | 10 | 3 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 832 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1040 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350601610 | 80 | 10 | 3 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 774.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1139 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350602010 | 80 | 10 | 3 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1164 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1455 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350602110 | 80 | 10 | 3 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1239.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1549 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350701010 | 80 | 10 | 3 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 677.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 753 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350701110 | 80 | 10 | 3 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 659.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 970 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350701510 | 70 | 10 | 3 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 971.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 78 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1214 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
350701610 | 70 | 10 | 3 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 903.72 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 73 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1329 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
350702010 | 70 | 10 | 3 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1358.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 110 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1698 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
350702110 | 70 | 10 | 3 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1445.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 117 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024224 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 1807 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
350801010 | 80 | 10 | 3 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 198 | 213 | 257 | 3 | 10 | 11 | 13 | 6.6713e-05 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 861 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350801110 | 80 | 10 | 3 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 219.4766 | 235.3807 | 284.6835 | 47 | 51 | 61 | 0.020547 | 0.023989 | 0.033698 | 1.1 | 6 | 6.7 | 9 |  | 1109 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 235.3807 | 284.6835 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350801510 | 80 | 10 | 3 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1109.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350801610 | 80 | 10 | 3 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1032.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 83 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00027685 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350802010 | 80 | 10 | 3 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1552 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016875 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350802110 | 80 | 10 | 3 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1652.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 133 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350901010 | 80 | 10 | 3 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 968 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350901110 | 80 | 10 | 3 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277 | 298 | 363 | 0.95 | 0.95 | 0.95 | 220.2718 | 236.9712 | 288.6595 | 47 | 51 | 62 | 0.021784 | 0.025414 | 0.036755 | 1.2 | 6 | 6.7 | 9 |  | 1247 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 236.9712 | 288.6595 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350901510 | 80 | 10 | 3 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1248.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 101 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00016264 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1561 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350901610 | 80 | 10 | 3 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1161.44 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 94 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00044021 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1708 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350902010 | 80 | 10 | 3 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1746.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 141 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00023478 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2183 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350902110 | 80 | 10 | 3 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1859.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00045824 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2324 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501001010 | 80 | 10 | 3 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1076 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501001110 | 80 | 10 | 3 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 278 | 300 | 368 | 0.95 | 0.95 | 0.95 | 221.067 | 238.5616 | 292.6355 | 48 | 51 | 63 | 0.02395 | 0.026839 | 0.03994 | 1.3 | 6 | 6.7 | 9 |  | 1386 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.067 | 238.5616 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501001510 | 80 | 10 | 3 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1387.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 112 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00023966 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1734 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501001610 | 80 | 10 | 3 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1290.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 104 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.0004533 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 1898 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501002010 | 80 | 10 | 3 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 1940 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 156 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00031305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2425 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501002110 | 80 | 10 | 3 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2065.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059642 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2582 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501101010 | 80 | 10 | 3 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 222 | 237 | 284 | 4 | 11 | 12 | 15 | 0.00013996 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1184 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501101110 | 80 | 10 | 3 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 310 | 329 | 392 | 4 | 16 | 17 | 20 | 0.00025477 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 304 | 373 | 0.95 | 0.95 | 0.95 | 224.2479 | 241.7424 | 296.6115 | 48 | 52 | 64 | 0.025233 | 0.029311 | 0.043256 | 1.5 | 6 | 6.7 | 9 |  | 1525 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 241.7424 | 296.6115 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501101510 | 70 | 10 | 3 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1525.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00024862 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 1907 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3501101610 | 70 | 10 | 3 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1419.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 115 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00066276 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2088 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3501102010 | 70 | 10 | 3 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2134.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 172 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00040407 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3501102110 | 70 | 10 | 3 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2272 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 183 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00061841 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 2840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3501201010 | 80 | 10 | 3 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 227 | 243 | 293 | 5 | 12 | 13 | 15 | 0.00022398 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501201110 | 80 | 10 | 3 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 91 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 281 | 303 | 378 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.9472 | 300.5876 | 48 | 52 | 65 | 0.026516 | 0.030785 | 0.046703 | 1.6 | 6 | 6.7 | 9 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.9472 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501201510 | 80 | 10 | 3 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1664.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034524 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2081 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501201610 | 80 | 10 | 3 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1549.04 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 125 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00068069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2278 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501202010 | 80 | 10 | 3 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2328 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 188 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00050829 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2910 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501202110 | 80 | 10 | 3 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2478.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 200 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00078234 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501401010 | 80 | 10 | 3 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 243 | 258 | 311 | 6 | 13 | 13 | 16 | 0.00034823 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501401110 | 80 | 10 | 3 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 356 | 377 | 447 | 5 | 18 | 19 | 23 | 0.00045941 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 284 | 307 | 388 | 0.95 | 0.95 | 0.95 | 225.8383 | 244.128 | 308.5396 | 49 | 52 | 66 | 0.030215 | 0.033734 | 0.052514 | 1.9 | 6 | 6.7 | 9 |  | 1940 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 244.128 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501401510 | 80 | 10 | 3 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1942.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 157 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00047453 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2428 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501401610 | 80 | 10 | 3 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1806.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 146 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0012433 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2657 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501402010 | 80 | 10 | 3 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2716 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 219 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00064169 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3395 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501402110 | 80 | 10 | 3 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2892 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 233 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011789 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 3615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501601010 | 80 | 10 | 3 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 258 | 274 | 330 | 6 | 13 | 14 | 17 | 0.00038304 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1722 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501601110 | 80 | 10 | 3 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 389 | 410 | 483 | 6 | 20 | 21 | 25 | 0.00070949 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 287 | 312 | 398 | 0.95 | 0.95 | 0.95 | 228.2239 | 248.104 | 316.4917 | 49 | 53 | 68 | 0.032875 | 0.037994 | 0.060206 | 2.1 | 6 | 6.7 | 9 |  | 2218 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 248.104 | 316.4917 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501601510 | 80 | 10 | 3 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2219.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 179 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00062916 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2774 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501601610 | 80 | 10 | 3 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2065.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0016307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3037 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501602010 | 80 | 10 | 3 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3104 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 250 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0009253 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501602110 | 80 | 10 | 3 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3304.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 267 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0016729 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4131 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501801010 | 80 | 10 | 3 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 276 | 292 | 348 | 7 | 14 | 15 | 18 | 0.00055302 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 1937 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501801110 | 80 | 10 | 3 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 137 | 426 | 447 | 520 | 7 | 22 | 23 | 27 | 0.001029 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 294 | 320 | 408 | 0.95 | 0.95 | 0.95 | 233.7903 | 254.4657 | 324.4437 | 50 | 55 | 70 | 0.036877 | 0.043931 | 0.06846 | 2.4 | 6 | 6.7 | 9 |  | 2495 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 233.7903 | 254.4657 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501801510 | 60 | 10 | 3 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2496.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 201 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00081069 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3501801610 | 60 | 10 | 3 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2322.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 187 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0020811 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3416 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3501802010 | 60 | 10 | 3 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3492 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 282 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0012692 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4365 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3501802110 | 60 | 10 | 3 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 3718.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 300 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0020114 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502001010 | 80 | 10 | 3 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 290 | 307 | 366 | 8 | 15 | 16 | 19 | 0.00076253 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2152 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502001110 | 80 | 10 | 3 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 457 | 478 | 556 | 8 | 24 | 25 | 29 | 0.0014244 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 295 | 321 | 418 | 0.95 | 0.95 | 0.95 | 234.5855 | 255.2609 | 332.3958 | 50 | 55 | 71 | 0.039631 | 0.047181 | 0.075332 | 2.7 | 6 | 6.7 | 9 |  | 2772 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.5855 | 255.2609 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502001510 | 80 | 10 | 3 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2774.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 224 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012013 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3468 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502001610 | 80 | 10 | 3 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2581.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 208 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0025976 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 3796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502002010 | 80 | 10 | 3 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 3880 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0014945 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 4850 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502002110 | 80 | 10 | 3 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4131.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 333 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0026765 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 5164 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502201010 | 80 | 10 | 3 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2130.3 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 306 | 322 | 384 | 9 | 16 | 17 | 20 | 0.0010147 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2367 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502201110 | 80 | 10 | 3 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2073.32 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 167 | 490 | 511 | 593 | 9 | 25 | 26 | 31 | 0.001902 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 297 | 324 | 428 | 0.95 | 0.95 | 0.95 | 236.1759 | 257.6465 | 340.3478 | 51 | 55 | 73 | 0.043943 | 0.050431 | 0.084581 | 2.9 | 6 | 6.7 | 9 |  | 3049 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 257.6465 | 340.3478 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502201510 | 80 | 10 | 3 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3052 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0014638 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 3815 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502201610 | 80 | 10 | 3 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 2839.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 229 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0031831 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4176 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502202010 | 80 | 10 | 3 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 4268 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 344 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0019415 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 5335 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502202110 | 80 | 10 | 3 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 4544 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 366 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0034561 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 5680 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502401010 | 80 | 10 | 3 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 321 | 338 | 402 | 10 | 17 | 17 | 21 | 0.0013125 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2582 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502401110 | 80 | 10 | 3 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 182 | 523 | 545 | 629 | 9 | 27 | 28 | 32 | 0.0020427 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300 | 328 | 438 | 0.95 | 0.95 | 0.95 | 238.5616 | 260.8273 | 348.2999 | 51 | 56 | 75 | 0.046794 | 0.055469 | 0.094433 | 3.2 | 6 | 6.7 | 9 |  | 3326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 260.8273 | 348.2999 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502401510 | 80 | 10 | 3 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3329.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 269 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0017585 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4162 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502401610 | 80 | 10 | 3 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3097.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 250 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0038405 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 4555 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502402010 | 80 | 10 | 3 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 4656 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 375 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0022305 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 5820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502402110 | 80 | 10 | 3 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 4957.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 400 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0043563 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 6197 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502601010 | 80 | 10 | 3 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2518.2 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 203 | 338 | 356 | 421 | 10 | 17 | 18 | 22 | 0.001397 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 2798 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502601110 | 80 | 10 | 3 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2450.72 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 198 | 558 | 581 | 666 | 10 | 29 | 30 | 34 | 0.0026367 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 304 | 336 | 448 | 0.95 | 0.95 | 0.95 | 241.7424 | 267.1889 | 356.2519 | 52 | 57 | 77 | 0.051424 | 0.060741 | 0.1049 | 3.5 | 6 | 6.7 | 9 |  | 3604 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 267.1889 | 356.2519 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502601510 | 60 | 10 | 3 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3606.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 291 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0020868 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4508 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3502601610 | 60 | 10 | 3 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3355.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 271 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0045725 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 4935 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502602010 | 60 | 10 | 3 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5044 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 407 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0027893 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 6305 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3502602110 | 60 | 10 | 3 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5370.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 433 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.004956 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 6713 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502801010 | 60 | 10 | 3 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 318 | 331 | 374 | 11 | 16 | 17 | 19 | 0.0017586 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3013 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502801110 | 60 | 10 | 3 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 557 | 573 | 630 | 11 | 29 | 30 | 33 | 0.003327 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 265 | 352 | 0.95 | 0.95 | 0.95 | 190.8492 | 210.7294 | 279.9122 | 41 | 45 | 60 | 0.035386 | 0.041866 | 0.070446 | 3.7 | 6 | 6.7 | 9 |  | 3881 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 210.7294 | 279.9122 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3502801510 | 80 | 10 | 3 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3884 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0024501 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 4855 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502801610 | 80 | 10 | 3 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3613.52 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 291 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005382 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 5314 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502802010 | 80 | 10 | 3 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5432 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 438 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0034217 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 6790 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502802110 | 80 | 10 | 3 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5784 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 466 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0060645 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 7230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3503001010 | 40 | 10 | 3 | 50 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2905.2 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 234 | 298 | 305 | 327 | 12 | 15 | 16 | 17 | 0.0021728 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 3228 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3503001110 | 40 | 10 | 3 | 50 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2827.44 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 228 | 556 | 564 | 594 | 12 | 29 | 29 | 31 | 0.0041193 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 175 | 193 | 257 | 0.95 | 0.95 | 0.95 | 139.1609 | 153.4746 | 204.3677 | 30 | 33 | 44 | 0.021281 | 0.02526 | 0.042407 | 4 | 6 | 6.7 | 9 |  | 4158 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 139.1609 | 153.4746 | 204.3677 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3503001510 | 60 | 10 | 3 | 50 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4161.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 336 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0028497 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 5202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3503001610 | 60 | 10 | 3 | 50 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3871.92 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 312 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0062716 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 5694 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3503002010 | 60 | 10 | 3 | 50 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5820 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 469 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0038259 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 7275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3503002110 | 60 | 10 | 3 | 50 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6196.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 500 | #VALUE! | #VALUE! | #VALUE! | 26 | #VALUE! | #VALUE! | #VALUE! | 0.0073089 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 7746 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
360501010 | 80 | 10 | 3 | 60 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 526.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 585 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360501110 | 80 | 10 | 3 | 60 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 507.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 41 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 747 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360601010 | 80 | 10 | 3 | 60 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 631.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 702 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360601110 | 80 | 10 | 3 | 60 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 609.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 896 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360601510 | 80 | 10 | 3 | 60 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 896 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1120 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360601610 | 80 | 10 | 3 | 60 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 850 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1250 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360602010 | 80 | 10 | 3 | 60 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1252 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1565 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360602110 | 80 | 10 | 3 | 60 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1383.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1729 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360701010 | 80 | 10 | 3 | 60 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 737.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 819 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360701110 | 80 | 10 | 3 | 60 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 711.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1046 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360701510 | 70 | 10 | 3 | 60 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1044.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 84 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 9.7187e-05 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
360701610 | 70 | 10 | 3 | 60 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 992.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 80 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1459 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
360702010 | 70 | 10 | 3 | 60 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1460.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 118 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1826 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
360702110 | 70 | 10 | 3 | 60 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1613.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 130 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032624 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2017 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
360801010 | 80 | 10 | 3 | 60 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 842.4 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 68 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 936 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360801110 | 80 | 10 | 3 | 60 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 812.6 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 66 | 260 | 279 | 337 | 3 | 13 | 14 | 17 | 0.00011928 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 262 | 282 | 340 | 0.95 | 0.95 | 0.95 | 208.3438 | 224.2479 | 270.3698 | 45 | 48 | 58 | 0.018922 | 0.021384 | 0.03062 | 1.1 | 6 | 6.7 | 9 |  | 1195 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 224.2479 | 270.3698 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360801510 | 80 | 10 | 3 | 60 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1194.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360801610 | 80 | 10 | 3 | 60 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1133.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 91 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00042712 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1667 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360802010 | 80 | 10 | 3 | 60 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1668.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 135 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022764 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2086 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360802110 | 80 | 10 | 3 | 60 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 1844.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 149 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044029 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360901010 | 80 | 10 | 3 | 60 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 947.7 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1053 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360901110 | 80 | 10 | 3 | 60 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 914.6 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 263 | 283 | 345 | 0.95 | 0.95 | 0.95 | 209.139 | 225.0431 | 274.3458 | 45 | 48 | 59 | 0.020069 | 0.022667 | 0.033465 | 1.2 | 6 | 6.7 | 9 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 209.139 | 225.0431 | 274.3458 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360901510 | 80 | 10 | 3 | 60 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1343.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 108 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1679 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360901610 | 80 | 10 | 3 | 60 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1275.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 103 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00044021 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 1876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360902010 | 80 | 10 | 3 | 60 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1877.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 151 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00030408 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2347 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360902110 | 80 | 10 | 3 | 60 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2075.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 167 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00057443 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2594 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601001010 | 80 | 10 | 3 | 60 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1053 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 212 | 227 | 275 | 4 | 11 | 12 | 14 | 0.00013135 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1170 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601001110 | 80 | 10 | 3 | 60 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1015.92 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 82 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 264 | 285 | 349 | 0.95 | 0.95 | 0.95 | 209.9342 | 226.6335 | 277.5266 | 45 | 49 | 60 | 0.021217 | 0.024896 | 0.036435 | 1.3 | 6 | 6.7 | 9 |  | 1494 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 209.9342 | 226.6335 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601001510 | 80 | 10 | 3 | 60 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1492.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 120 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00023966 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1866 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601001610 | 80 | 10 | 3 | 60 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1417.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 114 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00064483 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2084 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601002010 | 80 | 10 | 3 | 60 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2086.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 168 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00039308 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2608 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601002110 | 80 | 10 | 3 | 60 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2305.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 186 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00072961 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 2882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601101010 | 80 | 10 | 3 | 60 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1158.3 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 93 | 222 | 237 | 284 | 5 | 11 | 12 | 15 | 0.00021129 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1287 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601101110 | 80 | 10 | 3 | 60 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1117.24 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 90 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 268 | 288 | 354 | 0.95 | 0.95 | 0.95 | 213.115 | 229.0191 | 281.5026 | 46 | 49 | 61 | 0.023302 | 0.026226 | 0.039531 | 1.5 | 6 | 6.7 | 9 |  | 1643 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 213.115 | 229.0191 | 281.5026 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601101510 | 70 | 10 | 3 | 60 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1642.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 132 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00033355 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3601101610 | 70 | 10 | 3 | 60 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1558.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 126 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00089237 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2292 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3601102010 | 70 | 10 | 3 | 60 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2295.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 185 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00049511 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 2869 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3601102110 | 70 | 10 | 3 | 60 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2536 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 205 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00090675 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3170 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3601201010 | 80 | 10 | 3 | 60 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1263.6 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 102 | 227 | 243 | 293 | 5 | 12 | 13 | 15 | 0.00022398 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1404 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601201110 | 80 | 10 | 3 | 60 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1219.24 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 267 | 288 | 359 | 0.95 | 0.95 | 0.95 | 212.3198 | 229.0191 | 285.4787 | 46 | 49 | 61 | 0.024494 | 0.027555 | 0.041475 | 1.6 | 6 | 6.7 | 9 |  | 1793 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 212.3198 | 229.0191 | 285.4787 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601201510 | 80 | 10 | 3 | 60 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1791.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 144 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00034524 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2239 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601201610 | 80 | 10 | 3 | 60 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1700.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 137 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00091576 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2501 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601202010 | 80 | 10 | 3 | 60 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2504 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 202 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00050829 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3130 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601202110 | 80 | 10 | 3 | 60 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 2766.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 223 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011067 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3458 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601401010 | 80 | 10 | 3 | 60 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1474.2 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 243 | 258 | 311 | 6 | 13 | 13 | 16 | 0.00034823 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1638 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601401110 | 80 | 10 | 3 | 60 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1422.56 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 356 | 377 | 447 | 6 | 18 | 19 | 23 | 0.00063987 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 270 | 292 | 368 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.1999 | 292.6355 | 46 | 50 | 63 | 0.026877 | 0.031368 | 0.048166 | 1.9 | 6 | 6.7 | 9 |  | 2092 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.1999 | 292.6355 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601401510 | 80 | 10 | 3 | 60 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2089.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 169 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059309 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2612 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601401610 | 80 | 10 | 3 | 60 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1984.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 160 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0012433 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 2918 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601402010 | 80 | 10 | 3 | 60 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2920.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 236 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00075811 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3651 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601402110 | 80 | 10 | 3 | 60 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3228 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 260 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0013719 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 4035 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601601010 | 80 | 10 | 3 | 60 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1684.8 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 136 | 258 | 274 | 330 | 7 | 13 | 14 | 17 | 0.00050754 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1872 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601601110 | 80 | 10 | 3 | 60 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1625.2 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 389 | 410 | 483 | 7 | 20 | 21 | 25 | 0.00093804 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 273 | 296 | 378 | 0.95 | 0.95 | 0.95 | 217.091 | 235.3807 | 300.5876 | 47 | 51 | 65 | 0.030444 | 0.035391 | 0.055387 | 2.1 | 6 | 6.7 | 9 |  | 2390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.091 | 235.3807 | 300.5876 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601601510 | 80 | 10 | 3 | 60 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2388.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 193 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00076744 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2986 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601601610 | 80 | 10 | 3 | 60 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2267.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 183 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0016307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3334 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601602010 | 80 | 10 | 3 | 60 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3338.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 269 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001066 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 4173 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601602110 | 80 | 10 | 3 | 60 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 3688.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 297 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0019054 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 4611 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601801010 | 80 | 10 | 3 | 60 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1895.4 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 153 | 276 | 292 | 348 | 8 | 14 | 15 | 18 | 0.00070519 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 2106 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601801110 | 80 | 10 | 3 | 60 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1828.52 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 147 | 426 | 447 | 520 | 8 | 22 | 23 | 27 | 0.0013098 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 280 | 304 | 387 | 0.95 | 0.95 | 0.95 | 222.6575 | 241.7424 | 307.7444 | 48 | 52 | 66 | 0.034214 | 0.03963 | 0.061431 | 2.4 | 6 | 6.7 | 9 |  | 2689 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 222.6575 | 241.7424 | 307.7444 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601801510 | 60 | 10 | 3 | 60 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2687.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 217 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00096969 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3359 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3601801610 | 60 | 10 | 3 | 60 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2550.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 206 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.0024957 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 3751 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3601802010 | 60 | 10 | 3 | 60 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3755.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 303 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0014352 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4694 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3601802110 | 60 | 10 | 3 | 60 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 4150.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 335 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.002545 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5188 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602001010 | 80 | 10 | 3 | 60 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2106 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 170 | 290 | 307 | 366 | 9 | 15 | 16 | 19 | 0.00094435 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2340 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602001110 | 80 | 10 | 3 | 60 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2031.84 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 164 | 457 | 478 | 556 | 8 | 24 | 25 | 29 | 0.0014244 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 280 | 305 | 397 | 0.95 | 0.95 | 0.95 | 222.6575 | 242.5376 | 315.6965 | 48 | 52 | 68 | 0.036781 | 0.042579 | 0.069597 | 2.7 | 6 | 6.7 | 9 |  | 2988 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 222.6575 | 242.5376 | 315.6965 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602001510 | 80 | 10 | 3 | 60 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 2985.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 241 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0012013 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3732 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602001610 | 80 | 10 | 3 | 60 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 2834.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 229 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0030647 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 4168 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602002010 | 80 | 10 | 3 | 60 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 4172.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 337 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0016767 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 5216 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602002110 | 80 | 10 | 3 | 60 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 4611.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 372 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0032969 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 5764 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602201010 | 80 | 10 | 3 | 60 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2316.6 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 306 | 322 | 384 | 10 | 16 | 17 | 20 | 0.0012281 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2574 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602201110 | 80 | 10 | 3 | 60 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2235.16 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 180 | 490 | 511 | 593 | 9 | 25 | 26 | 31 | 0.001902 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 282 | 308 | 406 | 0.95 | 0.95 | 0.95 | 224.2479 | 244.9232 | 322.8533 | 48 | 53 | 69 | 0.039347 | 0.047136 | 0.076301 | 2.9 | 6 | 6.7 | 9 |  | 3287 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 244.9232 | 322.8533 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602201510 | 80 | 10 | 3 | 60 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3284 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 265 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0016812 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 4105 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602201610 | 80 | 10 | 3 | 60 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 3117.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 251 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0037045 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4585 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602202010 | 80 | 10 | 3 | 60 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 4590.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 370 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0021509 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 5738 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602202110 | 80 | 10 | 3 | 60 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 5072 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 409 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0041671 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 6340 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602401010 | 80 | 10 | 3 | 60 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2527.2 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 204 | 321 | 338 | 402 | 11 | 17 | 17 | 21 | 0.0015594 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2808 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602401110 | 80 | 10 | 3 | 60 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2438.48 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 197 | 523 | 545 | 629 | 10 | 27 | 28 | 32 | 0.0024679 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 285 | 312 | 416 | 0.95 | 0.95 | 0.95 | 226.6335 | 248.104 | 330.8054 | 49 | 53 | 71 | 0.043513 | 0.050184 | 0.085453 | 3.2 | 6 | 6.7 | 9 |  | 3586 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 226.6335 | 248.104 | 330.8054 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602401510 | 80 | 10 | 3 | 60 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3582.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 289 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0019998 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4478 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602401610 | 80 | 10 | 3 | 60 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3401.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 274 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.004418 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5002 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602402010 | 80 | 10 | 3 | 60 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 5007.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 404 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0026947 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 6259 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602402110 | 80 | 10 | 3 | 60 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 5533.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 446 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0051617 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 6917 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602601010 | 80 | 10 | 3 | 60 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2737.8 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 221 | 338 | 356 | 421 | 11 | 17 | 18 | 22 | 0.001659 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 3042 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602601110 | 80 | 10 | 3 | 60 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2641.12 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 558 | 581 | 666 | 11 | 29 | 30 | 34 | 0.0031278 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 289 | 319 | 425 | 0.95 | 0.95 | 0.95 | 229.8143 | 253.6705 | 337.9622 | 49 | 55 | 73 | 0.046172 | 0.05693 | 0.095202 | 3.5 | 6 | 6.7 | 9 |  | 3884 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 229.8143 | 253.6705 | 337.9622 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602601510 | 60 | 10 | 3 | 60 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3881.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0023528 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 4852 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3602601610 | 60 | 10 | 3 | 60 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3684.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 297 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005208 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 5418 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602602010 | 60 | 10 | 3 | 60 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5424.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 437 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.003311 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 6781 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3602602110 | 60 | 10 | 3 | 60 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5994.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 483 | #VALUE! | #VALUE! | #VALUE! | 25 | #VALUE! | #VALUE! | #VALUE! | 0.0062862 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 7493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602801010 | 60 | 10 | 3 | 60 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2948.4 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 238 | 318 | 331 | 374 | 12 | 16 | 17 | 19 | 0.002057 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3276 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602801110 | 60 | 10 | 3 | 60 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2844.44 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 229 | 557 | 573 | 630 | 12 | 29 | 30 | 33 | 0.0038875 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 228 | 251 | 335 | 0.95 | 0.95 | 0.95 | 181.3068 | 199.5965 | 266.3937 | 39 | 43 | 57 | 0.032332 | 0.038565 | 0.064198 | 3.7 | 6 | 6.7 | 9 |  | 4183 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 181.3068 | 199.5965 | 266.3937 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3602801510 | 80 | 10 | 3 | 60 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4180 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 337 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0027417 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 5225 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602801610 | 80 | 10 | 3 | 60 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3967.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 320 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0068121 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 5835 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602802010 | 80 | 10 | 3 | 60 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5841.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 471 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0037069 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 7302 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602802110 | 80 | 10 | 3 | 60 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6456 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 521 | #VALUE! | #VALUE! | #VALUE! | 27 | #VALUE! | #VALUE! | #VALUE! | 0.0075464 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 8070 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3603001010 | 40 | 10 | 3 | 60 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3159 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 255 | 298 | 305 | 327 | 13 | 15 | 16 | 17 | 0.0025092 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 3510 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3603001110 | 40 | 10 | 3 | 60 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3047.76 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 246 | 556 | 564 | 594 | 13 | 29 | 29 | 31 | 0.0047528 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 166 | 183 | 244 | 0.95 | 0.95 | 0.95 | 132.0041 | 145.5226 | 194.0301 | 28 | 31 | 42 | 0.018799 | 0.022573 | 0.038996 | 4 | 6 | 6.7 | 9 |  | 4482 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.0041 | 145.5226 | 194.0301 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3603001510 | 60 | 10 | 3 | 60 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4478.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 361 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0035014 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 5598 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3603001610 | 60 | 10 | 3 | 60 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4251.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 343 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0078251 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 6252 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3603002010 | 60 | 10 | 3 | 60 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6259.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 505 | #VALUE! | #VALUE! | #VALUE! | 26 | #VALUE! | #VALUE! | #VALUE! | 0.0044462 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 7824 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3603002110 | 60 | 10 | 3 | 60 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6916.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 558 | #VALUE! | #VALUE! | #VALUE! | 29 | #VALUE! | #VALUE! | #VALUE! | 0.0089477 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 8646 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
370501010 | 80 | 10 | 3 | 70 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 561.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 45 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.3616e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 624 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370501110 | 80 | 10 | 3 | 70 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 540.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 44 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 795 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370601010 | 80 | 10 | 3 | 70 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 674.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 749 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370601110 | 80 | 10 | 3 | 70 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 648.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 954 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370601510 | 80 | 10 | 3 | 70 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 946.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1183 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370601610 | 80 | 10 | 3 | 70 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 922.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1356 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370602010 | 80 | 10 | 3 | 70 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1321.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1652 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370602110 | 80 | 10 | 3 | 70 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1524.8 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1906 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370701010 | 80 | 10 | 3 | 70 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 786.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 874 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370701110 | 80 | 10 | 3 | 70 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 756.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1113 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370701510 | 70 | 10 | 3 | 70 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1104 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 89 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00014954 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1380 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
370701610 | 70 | 10 | 3 | 70 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1075.76 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 87 | #VALUE! | #VALUE! | #VALUE! | 4 | #VALUE! | #VALUE! | #VALUE! | 0.00026794 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
370702010 | 70 | 10 | 3 | 70 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1541.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 124 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00016328 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1927 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
370702110 | 70 | 10 | 3 | 70 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 1779.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 143 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032624 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2224 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
370801010 | 80 | 10 | 3 | 70 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 898.2 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 998 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370801110 | 80 | 10 | 3 | 70 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 864.96 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 70 | 260 | 279 | 337 | 4 | 13 | 14 | 17 | 0.00020308 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 248 | 267 | 322 | 0.95 | 0.95 | 0.95 | 197.2109 | 212.3198 | 256.0561 | 42 | 46 | 55 | 0.016604 | 0.019727 | 0.027683 | 1.1 | 6 | 6.7 | 9 |  | 1272 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 197.2109 | 212.3198 | 256.0561 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370801510 | 80 | 10 | 3 | 70 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1262.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 102 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00015609 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1578 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370801610 | 80 | 10 | 3 | 70 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1229.44 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 99 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00042712 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 1808 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370802010 | 80 | 10 | 3 | 70 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1761.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 142 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022764 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370802110 | 80 | 10 | 3 | 70 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 2033.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 164 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044029 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 2542 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370901010 | 80 | 10 | 3 | 70 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1010.7 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 205 | 220 | 266 | 4 | 11 | 11 | 14 | 0.00012273 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1123 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370901110 | 80 | 10 | 3 | 70 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 973.08 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 78 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 249 | 268 | 326 | 0.95 | 0.95 | 0.95 | 198.0061 | 213.115 | 259.2369 | 43 | 46 | 56 | 0.018421 | 0.020919 | 0.030323 | 1.2 | 6 | 6.7 | 9 |  | 1431 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 213.115 | 259.2369 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370901510 | 80 | 10 | 3 | 70 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1420 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 115 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1775 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370901610 | 80 | 10 | 3 | 70 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1383.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 112 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00062691 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2034 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370902010 | 80 | 10 | 3 | 70 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1982.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 160 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00030408 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2478 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370902110 | 80 | 10 | 3 | 70 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2287.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 184 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00057443 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2859 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701001010 | 80 | 10 | 3 | 70 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1123.2 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 212 | 227 | 275 | 5 | 11 | 12 | 14 | 0.0001986 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1248 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701001110 | 80 | 10 | 3 | 70 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1081.2 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 291 | 311 | 374 | 4 | 15 | 16 | 19 | 0.00023754 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 250 | 270 | 331 | 0.95 | 0.95 | 0.95 | 198.8013 | 214.7054 | 263.2129 | 43 | 46 | 57 | 0.019481 | 0.02211 | 0.033083 | 1.3 | 6 | 6.7 | 9 |  | 1590 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.8013 | 214.7054 | 263.2129 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701001510 | 80 | 10 | 3 | 70 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1577.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 127 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032186 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 1972 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701001610 | 80 | 10 | 3 | 70 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1536.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 124 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00064483 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2260 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701002010 | 80 | 10 | 3 | 70 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2202.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 178 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00039308 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2753 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701002110 | 80 | 10 | 3 | 70 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 2541.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 205 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00087568 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3177 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701101010 | 80 | 10 | 3 | 70 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1235.7 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 100 | 222 | 237 | 284 | 5 | 11 | 12 | 15 | 0.00021129 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1373 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701101110 | 80 | 10 | 3 | 70 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1189.32 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 254 | 273 | 335 | 0.95 | 0.95 | 0.95 | 201.9821 | 217.091 | 266.3937 | 43 | 47 | 57 | 0.020542 | 0.024259 | 0.034811 | 1.5 | 6 | 6.7 | 9 |  | 1749 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 201.9821 | 217.091 | 266.3937 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701101510 | 70 | 10 | 3 | 70 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1735.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 140 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00033355 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2169 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3701101610 | 70 | 10 | 3 | 70 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1690.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 136 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00089237 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2486 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3701102010 | 70 | 10 | 3 | 70 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2422.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00049511 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 3028 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3701102110 | 70 | 10 | 3 | 70 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 2796 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 225 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0010707 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 3495 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3701201010 | 80 | 10 | 3 | 70 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1348.2 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 227 | 243 | 293 | 6 | 12 | 13 | 15 | 0.00031342 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1498 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701201110 | 80 | 10 | 3 | 70 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1297.44 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 105 | 324 | 344 | 410 | 5 | 17 | 18 | 21 | 0.00040866 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 253 | 273 | 340 | 0.95 | 0.95 | 0.95 | 201.1869 | 217.091 | 270.3698 | 43 | 47 | 58 | 0.021602 | 0.025496 | 0.037746 | 1.6 | 6 | 6.7 | 9 |  | 1908 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 201.1869 | 217.091 | 270.3698 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701201510 | 80 | 10 | 3 | 70 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 1892.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 153 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044509 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701201610 | 80 | 10 | 3 | 70 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 1844.16 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 149 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0011844 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 2712 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701202010 | 80 | 10 | 3 | 70 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2643.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 213 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00061062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3304 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701202110 | 80 | 10 | 3 | 70 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 3049.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.001289 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3812 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701401010 | 80 | 10 | 3 | 70 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1572.3 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 243 | 258 | 311 | 7 | 13 | 13 | 16 | 0.00046205 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1747 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701401110 | 80 | 10 | 3 | 70 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1513.68 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 356 | 377 | 447 | 6 | 18 | 19 | 23 | 0.00063987 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255 | 277 | 349 | 0.95 | 0.95 | 0.95 | 202.7773 | 220.2718 | 277.5266 | 44 | 47 | 60 | 0.024754 | 0.02797 | 0.043993 | 1.9 | 6 | 6.7 | 9 |  | 2226 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 220.2718 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701401510 | 80 | 10 | 3 | 70 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2208.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 178 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00059309 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2761 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701401610 | 80 | 10 | 3 | 70 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2151.52 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 174 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0015586 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3164 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701402010 | 80 | 10 | 3 | 70 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 3083.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 249 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.00088388 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 3854 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701402110 | 80 | 10 | 3 | 70 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3558.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 287 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0017995 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 4448 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701601010 | 80 | 10 | 3 | 70 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1797.3 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 145 | 258 | 274 | 330 | 7 | 13 | 14 | 17 | 0.00050754 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 1997 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701601110 | 80 | 10 | 3 | 70 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1729.92 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 140 | 389 | 410 | 483 | 7 | 20 | 21 | 25 | 0.00093804 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 259 | 281 | 358 | 0.95 | 0.95 | 0.95 | 205.9581 | 223.4527 | 284.6835 | 44 | 48 | 61 | 0.02696 | 0.031648 | 0.049253 | 2.1 | 6 | 6.7 | 9 |  | 2544 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 223.4527 | 284.6835 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701601510 | 80 | 10 | 3 | 70 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2524 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 204 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00091872 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3155 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701601610 | 80 | 10 | 3 | 70 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2458.88 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 198 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0019946 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 3616 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701602010 | 80 | 10 | 3 | 70 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3524 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 284 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0012162 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 4405 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701602110 | 80 | 10 | 3 | 70 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 4066.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 328 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0024135 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 5083 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701801010 | 80 | 10 | 3 | 70 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2021.4 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 163 | 276 | 292 | 348 | 8 | 14 | 15 | 18 | 0.00070519 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 2246 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701801110 | 80 | 10 | 3 | 70 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1946.16 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 426 | 447 | 520 | 8 | 22 | 23 | 27 | 0.0013098 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 265 | 288 | 367 | 0.95 | 0.95 | 0.95 | 210.7294 | 229.0191 | 291.8403 | 45 | 49 | 63 | 0.030394 | 0.035534 | 0.056391 | 2.4 | 6 | 6.7 | 9 |  | 2862 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 229.0191 | 291.8403 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701801510 | 60 | 10 | 3 | 70 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 2840 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 229 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0011421 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3550 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3701801610 | 60 | 10 | 3 | 70 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 2766.24 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 223 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0029462 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 4068 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3701802010 | 60 | 10 | 3 | 70 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 3964 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 320 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.001611 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4955 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3701802110 | 60 | 10 | 3 | 70 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 4575.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 369 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0031376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5719 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702001010 | 80 | 10 | 3 | 70 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2246.4 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 181 | 290 | 307 | 366 | 9 | 15 | 16 | 19 | 0.00094435 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2496 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702001110 | 80 | 10 | 3 | 70 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2162.4 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 457 | 478 | 556 | 9 | 24 | 25 | 29 | 0.0017614 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 265 | 289 | 376 | 0.95 | 0.95 | 0.95 | 210.7294 | 229.8143 | 298.9972 | 45 | 49 | 64 | 0.032688 | 0.038194 | 0.062276 | 2.7 | 6 | 6.7 | 9 |  | 3180 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 229.8143 | 298.9972 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702001510 | 80 | 10 | 3 | 70 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 3155.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 254 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0013958 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 3944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702001610 | 80 | 10 | 3 | 70 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 3073.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 248 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0035686 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 4520 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702002010 | 80 | 10 | 3 | 70 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 4404.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 355 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.001869 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 5506 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702002110 | 80 | 10 | 3 | 70 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 5083.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 410 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0039779 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 6354 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702201010 | 80 | 10 | 3 | 70 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2471.4 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 199 | 306 | 322 | 384 | 10 | 16 | 17 | 20 | 0.0012281 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 2746 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702201110 | 80 | 10 | 3 | 70 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2378.64 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 192 | 490 | 511 | 593 | 10 | 25 | 26 | 31 | 0.002299 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 267 | 292 | 385 | 0.95 | 0.95 | 0.95 | 212.3198 | 232.1999 | 306.154 | 46 | 50 | 66 | 0.036411 | 0.042386 | 0.070348 | 2.9 | 6 | 6.7 | 9 |  | 3498 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 212.3198 | 232.1999 | 306.154 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702201510 | 80 | 10 | 3 | 70 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3470.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 280 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0016812 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 4338 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702201610 | 80 | 10 | 3 | 70 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 3380.96 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 273 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0042635 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 4972 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702202010 | 80 | 10 | 3 | 70 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 4845.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 391 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0023704 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 6057 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702202110 | 80 | 10 | 3 | 70 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 5591.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 451 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0049404 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 6989 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702401010 | 80 | 10 | 3 | 70 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2695.5 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 217 | 321 | 338 | 402 | 11 | 17 | 17 | 21 | 0.0015594 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 2995 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702401110 | 80 | 10 | 3 | 70 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2594.88 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 209 | 523 | 545 | 629 | 11 | 27 | 28 | 32 | 0.0029285 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 270 | 296 | 394 | 0.95 | 0.95 | 0.95 | 214.7054 | 235.3807 | 313.3109 | 46 | 51 | 67 | 0.038795 | 0.046794 | 0.076884 | 3.2 | 6 | 6.7 | 9 |  | 3816 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 235.3807 | 313.3109 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702401510 | 80 | 10 | 3 | 70 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 3786.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 305 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0022556 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 4733 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702401610 | 80 | 10 | 3 | 70 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 3688.32 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 297 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.005034 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 5424 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702402010 | 80 | 10 | 3 | 70 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 5285.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 426 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.0029424 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 6607 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702402110 | 80 | 10 | 3 | 70 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 6100 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 492 | #VALUE! | #VALUE! | #VALUE! | 25 | #VALUE! | #VALUE! | #VALUE! | 0.0060308 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 7625 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702601010 | 80 | 10 | 3 | 70 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2920.5 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 236 | 338 | 356 | 421 | 12 | 17 | 18 | 22 | 0.0019411 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 3245 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702601110 | 80 | 10 | 3 | 70 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2811.12 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 227 | 558 | 581 | 666 | 12 | 29 | 30 | 34 | 0.0036558 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 274 | 302 | 403 | 0.95 | 0.95 | 0.95 | 217.8862 | 240.152 | 320.4677 | 47 | 52 | 69 | 0.042814 | 0.051424 | 0.085933 | 3.5 | 6 | 6.7 | 9 |  | 4134 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.8862 | 240.152 | 320.4677 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702601510 | 60 | 10 | 3 | 70 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4101.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 331 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0026338 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 5127 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3702601610 | 60 | 10 | 3 | 70 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3995.68 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 322 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0065962 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 5876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702602010 | 60 | 10 | 3 | 70 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5726.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 462 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0035878 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 7158 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3702602110 | 60 | 10 | 3 | 70 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6608 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 533 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0077634 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 8260 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702801010 | 60 | 10 | 3 | 70 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3144.6 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 254 | 318 | 331 | 374 | 13 | 16 | 17 | 19 | 0.0023761 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3494 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702801110 | 60 | 10 | 3 | 70 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3027.36 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 244 | 557 | 573 | 630 | 13 | 29 | 30 | 33 | 0.0044866 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216 | 238 | 317 | 0.95 | 0.95 | 0.95 | 171.7643 | 189.2588 | 252.08 | 37 | 41 | 54 | 0.029402 | 0.035386 | 0.058214 | 3.7 | 6 | 6.7 | 9 |  | 4452 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.7643 | 189.2588 | 252.08 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3702801510 | 80 | 10 | 3 | 70 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4417.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 356 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0030486 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 5522 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702801610 | 80 | 10 | 3 | 70 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4303.04 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 347 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0075868 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 6328 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702802010 | 80 | 10 | 3 | 70 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6166.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 497 | #VALUE! | #VALUE! | #VALUE! | 26 | #VALUE! | #VALUE! | #VALUE! | 0.0043096 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 7708 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702802110 | 80 | 10 | 3 | 70 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 7116.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 574 | #VALUE! | #VALUE! | #VALUE! | 30 | #VALUE! | #VALUE! | #VALUE! | 0.0091785 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 8896 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3703001010 | 40 | 10 | 3 | 70 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3369.6 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 272 | 298 | 305 | 327 | 14 | 15 | 16 | 17 | 0.0028672 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 3744 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3703001110 | 40 | 10 | 3 | 70 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3243.6 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 262 | 556 | 564 | 594 | 14 | 29 | 29 | 31 | 0.0054262 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 157 | 174 | 231 | 0.95 | 0.95 | 0.95 | 124.8472 | 138.3657 | 183.6924 | 27 | 30 | 39 | 0.01761 | 0.021281 | 0.034122 | 4 | 6 | 6.7 | 9 |  | 4770 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 124.8472 | 138.3657 | 183.6924 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3703001510 | 60 | 10 | 3 | 70 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4732.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 382 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0038506 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 5916 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3703001610 | 60 | 10 | 3 | 70 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4610.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 372 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0086626 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 6780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3703002010 | 60 | 10 | 3 | 70 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6607.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 533 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0051104 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 8259 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3703002110 | 60 | 10 | 3 | 70 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 7624.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 615 | #VALUE! | #VALUE! | #VALUE! | 32 | #VALUE! | #VALUE! | #VALUE! | 0.01074 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 9531 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
390501010 | 80 | 10 | 3 | 90 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 616.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 50 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.1021e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 685 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390501110 | 80 | 10 | 3 | 90 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 597.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 48 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.0945e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 879 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390601010 | 80 | 10 | 3 | 90 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 738.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 821 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390601110 | 80 | 10 | 3 | 90 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1055 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390601510 | 80 | 10 | 3 | 90 | 60 | 15 | 16.5 | 0 | 26 | 30 | 40 | 1017.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1272 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390601610 | 80 | 10 | 3 | 90 | 60 | 16 | 16.5 | 0 | 26 | 30 | 40 | 1059.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1558 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390602010 | 80 | 10 | 3 | 90 | 60 | 20 | 21.5 | 0 | 26 | 30 | 40 | 1419.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1774 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390602110 | 80 | 10 | 3 | 90 | 60 | 21 | 21.5 | 0 | 26 | 30 | 40 | 1809.6 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2262 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390701010 | 80 | 10 | 3 | 90 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 862.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 958 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390701110 | 80 | 10 | 3 | 90 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1231 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390701510 | 70 | 10 | 3 | 90 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41 | 1187.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 96 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00014954 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 6 | 6.7 | 9 |  | 1484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
390701610 | 70 | 10 | 3 | 90 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41 | 1235.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 100 | #VALUE! | #VALUE! | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | 0.00041403 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 1817 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
390702010 | 70 | 10 | 3 | 90 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41 | 1656 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 134 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00022051 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 2070 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
390702110 | 70 | 10 | 3 | 90 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41 | 2111.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 170 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00053044 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 2639 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 10
390801010 | 80 | 10 | 3 | 90 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 985.5 | 1214 | 1304 | 1574 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 198 | 213 | 257 | 4 | 10 | 11 | 13 | 0.00011412 | 0.00063698 | 0.00076237 | 0.001045 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168 | 181 | 218 | 0.98 | 0.98 | 0.98 | 132.6312 | 142.8943 | 172.1048 | 29 | 31 | 37 | 0.0047836 | 0.0054309 | 0.0076078 | 0.5 | 6 | 6.7 | 9 |  | 1095 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 132.6312 | 142.8943 | 172.1048 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.85519 | 0.79918 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390801110 | 80 | 10 | 3 | 90 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 77 | 260 | 279 | 337 | 4 | 13 | 14 | 17 | 0.00020308 | 0.0018243 | 0.0020961 | 0.0030171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 221 | 237 | 286 | 0.95 | 0.95 | 0.95 | 175.7404 | 188.4636 | 227.4287 | 38 | 41 | 49 | 0.013739 | 0.015864 | 0.022236 | 1.1 | 6 | 6.7 | 9 |  | 1406 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 188.4636 | 227.4287 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.85519 | 0.79918 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390801510 | 80 | 10 | 3 | 90 | 80 | 15 | 16.5 | 0 | 26 | 30 | 41.8 | 1356.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 109 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00022173 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390801610 | 80 | 10 | 3 | 90 | 80 | 16 | 16.5 | 0 | 26 | 30 | 41.8 | 1412.36 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 114 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.00060898 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 2077 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390802010 | 80 | 10 | 3 | 90 | 80 | 20 | 21.5 | 0 | 26 | 30 | 41.8 | 1892.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 153 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.0002951 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390802110 | 80 | 10 | 3 | 90 | 80 | 21 | 21.5 | 0 | 26 | 30 | 41.8 | 2412.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 195 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00067687 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 3016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390901010 | 80 | 10 | 3 | 90 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1108.8 | 1288 | 1385 | 1687 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 205 | 220 | 266 | 5 | 11 | 11 | 14 | 0.00018592 | 0.00081218 | 0.00081218 | 0.0012778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 171 | 184 | 224 | 0.98 | 0.98 | 0.98 | 134.9996 | 145.2628 | 176.8416 | 29 | 31 | 38 | 0.0050512 | 0.0057314 | 0.0084325 | 0.6 | 6 | 6.7 | 9 |  | 1232 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.9996 | 145.2628 | 176.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390901110 | 80 | 10 | 3 | 90 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1803 | 1940 | 2362 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 276 | 295 | 355 | 4 | 14 | 15 | 18 | 0.00022031 | 0.0022475 | 0.0025561 | 0.0035931 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222 | 238 | 290 | 0.95 | 0.95 | 0.95 | 176.5356 | 189.2588 | 230.6095 | 38 | 41 | 50 | 0.014595 | 0.01684 | 0.024482 | 1.2 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.5356 | 189.2588 | 230.6095 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390901510 | 80 | 10 | 3 | 90 | 90 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1526.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 123 | #VALUE! | #VALUE! | #VALUE! | 6 | #VALUE! | #VALUE! | #VALUE! | 0.0002307 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 6 | 6.7 | 9 |  | 1908 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390901610 | 80 | 10 | 3 | 90 | 90 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1588.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 128 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00084561 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 2336 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390902010 | 80 | 10 | 3 | 90 | 90 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 2128.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 172 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.00038208 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2661 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390902110 | 80 | 10 | 3 | 90 | 90 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2714.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 219 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00084461 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3393 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901001010 | 80 | 10 | 3 | 90 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1232.1 | 1361 | 1466 | 1800 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 212 | 227 | 275 | 5 | 11 | 12 | 14 | 0.0001986 | 0.00086199 | 0.0010143 | 0.0013535 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 174 | 188 | 231 | 0.98 | 0.98 | 0.98 | 137.368 | 148.4206 | 182.3679 | 30 | 32 | 39 | 0.0056701 | 0.0064044 | 0.0093062 | 0.7 | 6 | 6.7 | 9 |  | 1369 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 137.368 | 148.4206 | 182.3679 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901001110 | 80 | 10 | 3 | 90 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 1957 | 2109 | 2589 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 291 | 311 | 374 | 5 | 15 | 16 | 19 | 0.00035791 | 0.0027268 | 0.0030742 | 0.0042324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222 | 240 | 294 | 0.95 | 0.95 | 0.95 | 176.5356 | 190.8492 | 233.7903 | 38 | 41 | 50 | 0.015451 | 0.017816 | 0.025859 | 1.3 | 6 | 6.7 | 9 |  | 1758 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.5356 | 190.8492 | 233.7903 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901001510 | 80 | 10 | 3 | 90 | 100 | 15 | 16.5 | 0 | 26 | 30 | 43 | 1696 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 137 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00032186 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 6 | 6.7 | 9 |  | 2120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901001610 | 80 | 10 | 3 | 90 | 100 | 16 | 16.5 | 0 | 26 | 30 | 43 | 1765.28 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 142 | #VALUE! | #VALUE! | #VALUE! | 7 | #VALUE! | #VALUE! | #VALUE! | 0.00086899 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 2596 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901002010 | 80 | 10 | 3 | 90 | 100 | 20 | 21.5 | 0 | 26 | 30 | 43 | 2365.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.00048192 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3 | 6 | 6.7 | 9 |  | 2957 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901002110 | 80 | 10 | 3 | 90 | 100 | 21 | 21.5 | 0 | 26 | 30 | 43 | 3016 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 243 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0012062 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 3770 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901101010 | 80 | 10 | 3 | 90 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1355.4 | 1446 | 1558 | 1912 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 222 | 237 | 284 | 6 | 11 | 12 | 15 | 0.00029601 | 0.00091181 | 0.0010722 | 0.0016255 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 179 | 193 | 237 | 0.98 | 0.98 | 0.98 | 141.3154 | 152.368 | 187.1047 | 30 | 33 | 40 | 0.005954 | 0.0071223 | 0.01023 | 0.7 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 141.3154 | 152.368 | 187.1047 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901101110 | 80 | 10 | 3 | 90 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2129 | 2293 | 2815 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 310 | 329 | 392 | 5 | 16 | 17 | 20 | 0.00038328 | 0.0032651 | 0.0036531 | 0.0049377 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 225 | 243 | 298 | 0.95 | 0.95 | 0.95 | 178.9212 | 193.2349 | 236.9712 | 38 | 42 | 51 | 0.016306 | 0.019658 | 0.028265 | 1.5 | 6 | 6.7 | 9 |  | 1934 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 178.9212 | 193.2349 | 236.9712 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901101510 | 70 | 10 | 3 | 90 | 110 | 15 | 16.5 | 0 | 26 | 30 | 43.5 | 1865.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 150 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00043037 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1 | 6 | 6.7 | 9 |  | 2332 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3901101610 | 70 | 10 | 3 | 90 | 110 | 16 | 16.5 | 0 | 26 | 30 | 43.5 | 1942.08 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 157 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.001155 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 2856 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3901102010 | 70 | 10 | 3 | 90 | 110 | 20 | 21.5 | 0 | 26 | 30 | 43.5 | 2602.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 210 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00059509 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5 | 6 | 6.7 | 9 |  | 3253 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3901102110 | 70 | 10 | 3 | 90 | 110 | 21 | 21.5 | 0 | 26 | 30 | 43.5 | 3317.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 268 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0014376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 4147 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3901201010 | 80 | 10 | 3 | 90 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1478.7 | 1505 | 1626 | 2025 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 227 | 243 | 293 | 6 | 12 | 13 | 15 | 0.00031342 | 0.0011301 | 0.0013112 | 0.0017108 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 181 | 195 | 243 | 0.98 | 0.98 | 0.98 | 142.8943 | 153.9469 | 191.8416 | 31 | 33 | 41 | 0.0066329 | 0.0074572 | 0.011206 | 0.8 | 6 | 6.7 | 9 |  | 1643 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 142.8943 | 153.9469 | 191.8416 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901201110 | 80 | 10 | 3 | 90 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2260 | 2442 | 3041 | 1.5 | 1.1 | 1.1 | 1.1 | 116 | 324 | 344 | 410 | 6 | 17 | 18 | 21 | 0.00057024 | 0.0038651 | 0.0042954 | 0.0057116 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 225 | 243 | 302 | 0.95 | 0.95 | 0.95 | 178.9212 | 193.2349 | 240.152 | 38 | 42 | 52 | 0.017162 | 0.020676 | 0.030785 | 1.6 | 6 | 6.7 | 9 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 178.9212 | 193.2349 | 240.152 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901201510 | 80 | 10 | 3 | 90 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44 | 2035.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 164 | #VALUE! | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 0.00044509 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2 | 6 | 6.7 | 9 |  | 2544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901201610 | 80 | 10 | 3 | 90 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44 | 2118.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 171 | #VALUE! | #VALUE! | #VALUE! | 9 | #VALUE! | #VALUE! | #VALUE! | 0.0014865 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 3115 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901202010 | 80 | 10 | 3 | 90 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44 | 2838.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 229 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.00072203 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3548 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901202110 | 80 | 10 | 3 | 90 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44 | 3619.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 292 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.0016935 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4524 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901401010 | 80 | 10 | 3 | 90 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1725.3 | 1648 | 1784 | 2250 | 1.5 | 1.08 | 1.08 | 1.08 | 139 | 243 | 258 | 311 | 7 | 13 | 13 | 16 | 0.00046205 | 0.0014443 | 0.0014443 | 0.00212 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 187 | 203 | 255 | 0.98 | 0.98 | 0.98 | 147.6312 | 160.2627 | 201.3152 | 32 | 34 | 43 | 0.0076744 | 0.0085919 | 0.013314 | 0.9 | 6 | 6.7 | 9 |  | 1917 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 147.6312 | 160.2627 | 201.3152 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901401110 | 80 | 10 | 3 | 90 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 2558 | 2770 | 3494 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 356 | 377 | 447 | 7 | 18 | 19 | 23 | 0.00084707 | 0.0047635 | 0.0052608 | 0.0074751 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 227 | 246 | 310 | 0.95 | 0.95 | 0.95 | 180.5116 | 195.6205 | 246.5136 | 39 | 42 | 53 | 0.019802 | 0.022711 | 0.034947 | 1.9 | 6 | 6.7 | 9 |  | 2461 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.5116 | 195.6205 | 246.5136 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901401510 | 80 | 10 | 3 | 90 | 140 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2374.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 191 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0007242 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 | 6.7 | 9 |  | 2968 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901401610 | 80 | 10 | 3 | 90 | 140 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2471.12 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 199 | #VALUE! | #VALUE! | #VALUE! | 10 | #VALUE! | #VALUE! | #VALUE! | 0.0019081 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 3634 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901402010 | 80 | 10 | 3 | 90 | 140 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 3312 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 267 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.0010189 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9 | 6 | 6.7 | 9 |  | 4140 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901402110 | 80 | 10 | 3 | 90 | 140 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 4222.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 341 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0025438 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 5278 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901601010 | 80 | 10 | 3 | 90 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1971 | 1788 | 1941 | 2476 | 1.5 | 1.08 | 1.08 | 1.08 | 159 | 258 | 274 | 330 | 8 | 13 | 14 | 17 | 0.00064784 | 0.0015774 | 0.0018076 | 0.0025836 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 210 | 268 | 0.98 | 0.98 | 0.98 | 152.368 | 165.789 | 211.5784 | 33 | 36 | 45 | 0.008797 | 0.010337 | 0.015641 | 1.1 | 6 | 6.7 | 9 |  | 2190 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 165.789 | 211.5784 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901601110 | 80 | 10 | 3 | 90 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1912.84 | 2850 | 3094 | 3946 | 1.5 | 1.1 | 1.1 | 1.1 | 154 | 389 | 410 | 483 | 8 | 20 | 21 | 25 | 0.0011951 | 0.0063428 | 0.0069349 | 0.009543 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 230 | 249 | 318 | 0.95 | 0.95 | 0.95 | 182.8972 | 198.0061 | 252.8753 | 39 | 43 | 54 | 0.021592 | 0.025843 | 0.039327 | 2.1 | 6 | 6.7 | 9 |  | 2813 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 182.8972 | 198.0061 | 252.8753 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901601510 | 80 | 10 | 3 | 90 | 160 | 15 | 16.5 | 0 | 26 | 30 | 45.5 | 2713.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 219 | #VALUE! | #VALUE! | #VALUE! | 11 | #VALUE! | #VALUE! | #VALUE! | 0.00091872 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6 | 6 | 6.7 | 9 |  | 3392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901601610 | 80 | 10 | 3 | 90 | 160 | 16 | 16.5 | 0 | 26 | 30 | 45.5 | 2824.72 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 228 | #VALUE! | #VALUE! | #VALUE! | 12 | #VALUE! | #VALUE! | #VALUE! | 0.0028278 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 4154 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901602010 | 80 | 10 | 3 | 90 | 160 | 20 | 21.5 | 0 | 26 | 30 | 45.5 | 3784.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 305 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.001376 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | 6 | 6.7 | 9 |  | 4731 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901602110 | 80 | 10 | 3 | 90 | 160 | 21 | 21.5 | 0 | 26 | 30 | 45.5 | 4825.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 389 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.003282 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3 | 6 | 6.7 | 9 |  | 6032 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901801010 | 80 | 10 | 3 | 90 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2217.6 | 1951 | 2118 | 2701 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 276 | 292 | 348 | 9 | 14 | 15 | 18 | 0.00087401 | 0.0019589 | 0.0022227 | 0.0031046 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 202 | 220 | 280 | 0.98 | 0.98 | 0.98 | 159.4732 | 173.6837 | 221.052 | 34 | 37 | 48 | 0.010003 | 0.011692 | 0.018918 | 1.2 | 6 | 6.7 | 9 |  | 2464 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 159.4732 | 173.6837 | 221.052 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901801110 | 80 | 10 | 3 | 90 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 2151.52 | 3177 | 3449 | 4399 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 426 | 447 | 520 | 9 | 22 | 23 | 27 | 0.0016207 | 0.0082142 | 0.0089076 | 0.011935 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 236 | 256 | 326 | 0.95 | 0.95 | 0.95 | 187.6684 | 203.5725 | 259.2369 | 40 | 44 | 56 | 0.024492 | 0.029167 | 0.04541 | 2.4 | 6 | 6.7 | 9 |  | 3164 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 187.6684 | 203.5725 | 259.2369 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901801510 | 60 | 10 | 3 | 90 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46 | 3052.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 246 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0013278 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3901801610 | 60 | 10 | 3 | 90 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46 | 3177.64 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 256 | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | 0.0034326 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.6 | 6 | 6.7 | 9 |  | 4673 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3901802010 | 60 | 10 | 3 | 90 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46 | 4258.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 343 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0017965 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 5323 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3901802110 | 60 | 10 | 3 | 90 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46 | 5428.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 438 | #VALUE! | #VALUE! | #VALUE! | 23 | #VALUE! | #VALUE! | #VALUE! | 0.0044979 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 6786 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902001010 | 80 | 10 | 3 | 90 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2464.2 | 2064 | 2250 | 2927 | 1.5 | 1.08 | 1.08 | 1.08 | 199 | 290 | 307 | 366 | 10 | 15 | 16 | 19 | 0.0011436 | 0.0023933 | 0.0026924 | 0.0036854 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 206 | 225 | 293 | 0.98 | 0.98 | 0.98 | 162.6311 | 177.6311 | 231.3151 | 35 | 38 | 50 | 0.011294 | 0.013138 | 0.021781 | 1.3 | 6 | 6.7 | 9 |  | 2738 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.6311 | 177.6311 | 231.3151 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902001110 | 80 | 10 | 3 | 90 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2390.88 | 3422 | 3730 | 4852 | 1.5 | 1.1 | 1.1 | 1.1 | 193 | 457 | 478 | 556 | 10 | 24 | 25 | 29 | 0.0021301 | 0.010398 | 0.011198 | 0.014669 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 236 | 257 | 334 | 0.95 | 0.95 | 0.95 | 187.6684 | 204.3677 | 265.5985 | 40 | 44 | 57 | 0.026362 | 0.031373 | 0.050369 | 2.7 | 6 | 6.7 | 9 |  | 3516 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 187.6684 | 204.3677 | 265.5985 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902001510 | 80 | 10 | 3 | 90 | 200 | 15 | 16.5 | 0 | 26 | 30 | 46.5 | 3392 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 274 | #VALUE! | #VALUE! | #VALUE! | 14 | #VALUE! | #VALUE! | #VALUE! | 0.001604 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2 | 6 | 6.7 | 9 |  | 4240 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902001610 | 80 | 10 | 3 | 90 | 200 | 16 | 16.5 | 0 | 26 | 30 | 46.5 | 3530.56 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 285 | #VALUE! | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE! | #VALUE! | 0.004686 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 5192 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902002010 | 80 | 10 | 3 | 90 | 200 | 20 | 21.5 | 0 | 26 | 30 | 46.5 | 4731.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 382 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0022834 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 | 6.7 | 9 |  | 5914 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902002110 | 80 | 10 | 3 | 90 | 200 | 21 | 21.5 | 0 | 26 | 30 | 46.5 | 6032 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 486 | #VALUE! | #VALUE! | #VALUE! | 25 | #VALUE! | #VALUE! | #VALUE! | 0.0055199 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.3 | 6 | 6.7 | 9 |  | 7540 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902201010 | 80 | 10 | 3 | 90 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2710.8 | 2188 | 2391 | 3152 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 306 | 322 | 384 | 11 | 16 | 17 | 20 | 0.0014597 | 0.0028833 | 0.0032196 | 0.0043289 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 212 | 231 | 305 | 0.98 | 0.98 | 0.98 | 167.368 | 182.3679 | 240.7888 | 36 | 39 | 52 | 0.012674 | 0.014676 | 0.024889 | 1.5 | 6 | 6.7 | 9 |  | 3012 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 167.368 | 182.3679 | 240.7888 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902201110 | 80 | 10 | 3 | 90 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2630.24 | 3682 | 4023 | 5304 | 1.5 | 1.1 | 1.1 | 1.1 | 212 | 490 | 511 | 593 | 11 | 25 | 26 | 31 | 0.0027293 | 0.012026 | 0.012912 | 0.017765 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 238 | 260 | 342 | 0.95 | 0.95 | 0.95 | 189.2588 | 206.7534 | 271.9602 | 41 | 44 | 58 | 0.02953 | 0.03358 | 0.055562 | 2.9 | 6 | 6.7 | 9 |  | 3868 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 189.2588 | 206.7534 | 271.9602 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902201510 | 80 | 10 | 3 | 90 | 220 | 15 | 16.5 | 0 | 26 | 30 | 46.9 | 3731.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 301 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0021583 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2 | 6 | 6.7 | 9 |  | 4664 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902201610 | 80 | 10 | 3 | 90 | 220 | 16 | 16.5 | 0 | 26 | 30 | 46.9 | 3883.48 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 313 | #VALUE! | #VALUE! | #VALUE! | 16 | #VALUE! | #VALUE! | #VALUE! | 0.0054937 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4 | 6 | 6.7 | 9 |  | 5711 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902202010 | 80 | 10 | 3 | 90 | 220 | 20 | 21.5 | 0 | 26 | 30 | 46.9 | 5204 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 420 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.0028399 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.9 | 6 | 6.7 | 9 |  | 6505 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902202110 | 80 | 10 | 3 | 90 | 220 | 21 | 21.5 | 0 | 26 | 30 | 46.9 | 6635.2 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 535 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0071424 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9 | 6 | 6.7 | 9 |  | 8294 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902401010 | 80 | 10 | 3 | 90 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2957.4 | 2313 | 2534 | 3377 | 1.5 | 1.08 | 1.08 | 1.08 | 239 | 321 | 338 | 402 | 12 | 17 | 17 | 21 | 0.0018252 | 0.0034316 | 0.0034316 | 0.0050374 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 217 | 238 | 317 | 0.98 | 0.98 | 0.98 | 171.3153 | 187.8942 | 250.2625 | 37 | 40 | 54 | 0.014143 | 0.016309 | 0.028251 | 1.6 | 6 | 6.7 | 9 |  | 3286 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 171.3153 | 187.8942 | 250.2625 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902401110 | 80 | 10 | 3 | 90 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2868.92 | 3943 | 4319 | 5757 | 1.5 | 1.1 | 1.1 | 1.1 | 231 | 523 | 545 | 629 | 12 | 27 | 28 | 32 | 0.0034241 | 0.014772 | 0.015777 | 0.02009 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 240 | 263 | 350 | 0.95 | 0.95 | 0.95 | 190.8492 | 209.139 | 278.3218 | 41 | 45 | 60 | 0.031482 | 0.037277 | 0.062888 | 3.2 | 6 | 6.7 | 9 |  | 4219 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 209.139 | 278.3218 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902401510 | 80 | 10 | 3 | 90 | 240 | 15 | 16.5 | 0 | 26 | 30 | 47.2 | 4070.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 328 | #VALUE! | #VALUE! | #VALUE! | 17 | #VALUE! | #VALUE! | #VALUE! | 0.0025258 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 | 6.7 | 9 |  | 5088 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902401610 | 80 | 10 | 3 | 90 | 240 | 16 | 16.5 | 0 | 26 | 30 | 47.2 | 4236.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 342 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0071103 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.8 | 6 | 6.7 | 9 |  | 6230 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902402010 | 80 | 10 | 3 | 90 | 240 | 20 | 21.5 | 0 | 26 | 30 | 47.2 | 5677.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 458 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | #VALUE! | #VALUE! | 0.0034688 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2 | 6 | 6.7 | 9 |  | 7097 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902402110 | 80 | 10 | 3 | 90 | 240 | 21 | 21.5 | 0 | 26 | 30 | 47.2 | 7238.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 584 | #VALUE! | #VALUE! | #VALUE! | 30 | #VALUE! | #VALUE! | #VALUE! | 0.0084792 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | 6 | 6.7 | 9 |  | 9048 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902601010 | 80 | 10 | 3 | 90 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3203.1 | 2450 | 2702 | 3603 | 1.5 | 1.08 | 1.08 | 1.08 | 258 | 338 | 356 | 421 | 13 | 17 | 18 | 22 | 0.002243 | 0.0036436 | 0.0040409 | 0.0058137 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 224 | 247 | 330 | 0.98 | 0.98 | 0.98 | 176.8416 | 194.9995 | 260.5256 | 38 | 42 | 56 | 0.015705 | 0.018849 | 0.031876 | 1.7 | 6 | 6.7 | 9 |  | 3559 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 176.8416 | 194.9995 | 260.5256 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902601110 | 80 | 10 | 3 | 90 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3108.28 | 4222 | 4657 | 6209 | 1.5 | 1.1 | 1.1 | 1.1 | 251 | 558 | 581 | 666 | 13 | 29 | 30 | 34 | 0.0042203 | 0.017882 | 0.01901 | 0.023832 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 244 | 269 | 358 | 0.95 | 0.95 | 0.95 | 194.0301 | 213.9102 | 284.6835 | 42 | 46 | 61 | 0.034925 | 0.041178 | 0.068698 | 3.5 | 6 | 6.7 | 9 |  | 4571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 213.9102 | 284.6835 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902601510 | 60 | 10 | 3 | 90 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4409.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 356 | #VALUE! | #VALUE! | #VALUE! | 18 | #VALUE! | #VALUE! | #VALUE! | 0.0029295 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 | 6.7 | 9 |  | 5512 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3902601610 | 60 | 10 | 3 | 90 | 260 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4590 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 370 | #VALUE! | #VALUE! | #VALUE! | 19 | #VALUE! | #VALUE! | #VALUE! | 0.0081394 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2 | 6 | 6.7 | 9 |  | 6750 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902602010 | 60 | 10 | 3 | 90 | 260 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6150.4 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 496 | #VALUE! | #VALUE! | #VALUE! | 26 | #VALUE! | #VALUE! | #VALUE! | 0.0041729 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5 | 6 | 6.7 | 9 |  | 7688 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3902602110 | 60 | 10 | 3 | 90 | 260 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 7841.6 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 632 | #VALUE! | #VALUE! | #VALUE! | 33 | #VALUE! | #VALUE! | #VALUE! | 0.010547 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9 | 6 | 6.7 | 9 |  | 9802 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902801010 | 60 | 10 | 3 | 90 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3449.7 | 2411 | 2662 | 3546 | 1.5 | 1.08 | 1.08 | 1.08 | 278 | 318 | 331 | 374 | 14 | 16 | 17 | 19 | 0.0027158 | 0.0034557 | 0.0038556 | 0.0047138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193 | 213 | 284 | 0.98 | 0.98 | 0.98 | 152.368 | 168.1574 | 224.2099 | 33 | 36 | 48 | 0.012816 | 0.015011 | 0.025333 | 1.9 | 6 | 6.7 | 9 |  | 3833 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.368 | 168.1574 | 224.2099 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902801110 | 60 | 10 | 3 | 90 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3346.96 | 4369 | 4824 | 6426 | 1.5 | 1.1 | 1.1 | 1.1 | 270 | 557 | 573 | 630 | 14 | 29 | 30 | 33 | 0.0051235 | 0.018952 | 0.020146 | 0.02392 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 192 | 212 | 282 | 0.95 | 0.95 | 0.95 | 152.6794 | 168.5835 | 224.2479 | 33 | 36 | 48 | 0.02392 | 0.027984 | 0.047045 | 3.7 | 6 | 6.7 | 9 |  | 4922 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.6794 | 168.5835 | 224.2479 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3902801510 | 80 | 10 | 3 | 90 | 280 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 4748.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 383 | #VALUE! | #VALUE! | #VALUE! | 20 | #VALUE! | #VALUE! | #VALUE! | 0.0037077 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.8 | 6 | 6.7 | 9 |  | 5936 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902801610 | 80 | 10 | 3 | 90 | 280 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 4942.92 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 399 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.010147 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6 | 6 | 6.7 | 9 |  | 7269 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902802010 | 80 | 10 | 3 | 90 | 280 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 6624 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 534 | #VALUE! | #VALUE! | #VALUE! | 28 | #VALUE! | #VALUE! | #VALUE! | 0.0049551 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.7 | 6 | 6.7 | 9 |  | 8280 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902802110 | 80 | 10 | 3 | 90 | 280 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 8444.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 681 | #VALUE! | #VALUE! | #VALUE! | 35 | #VALUE! | #VALUE! | #VALUE! | 0.012228 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6 | 6.7 | 9 |  | 10556 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3903001010 | 40 | 10 | 3 | 90 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3696.3 | 2372 | 2619 | 3489 | 1.5 | 1.08 | 1.08 | 1.08 | 298 | 298 | 305 | 327 | 15 | 15 | 16 | 17 | 0.0032464 | 0.0032464 | 0.0036466 | 0.0040675 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 162 | 179 | 239 | 0.98 | 0.98 | 0.98 | 127.8944 | 141.3154 | 188.6837 | 27 | 30 | 41 | 0.0093781 | 0.011348 | 0.019991 | 2 | 6 | 6.7 | 9 |  | 4107 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 127.8944 | 141.3154 | 188.6837 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3903001110 | 40 | 10 | 3 | 90 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3586.32 | 4516 | 4986 | 6642 | 1.5 | 1.1 | 1.1 | 1.1 | 289 | 556 | 564 | 594 | 15 | 29 | 29 | 31 | 0.006139 | 0.020023 | 0.020023 | 0.022573 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 140 | 154 | 206 | 0.95 | 0.95 | 0.95 | 111.3287 | 122.4616 | 163.8123 | 24 | 26 | 35 | 0.014253 | 0.016456 | 0.028081 | 4 | 6 | 6.7 | 9 |  | 5274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 111.3287 | 122.4616 | 163.8123 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3903001510 | 60 | 10 | 3 | 90 | 300 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 5088 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 410 | #VALUE! | #VALUE! | #VALUE! | 21 | #VALUE! | #VALUE! | #VALUE! | 0.0042152 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 2 | 0.00046183 | #VALUE! | #VALUE! | #VALUE! | 1.01 | 1.01 | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3 | 6 | 6.7 | 9 |  | 6360 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1127 | 2539 | 352 | 62 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3903001610 | 60 | 10 | 3 | 90 | 300 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 5295.84 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.1 | 1.1 | 1.1 | 427 | #VALUE! | #VALUE! | #VALUE! | 22 | #VALUE! | #VALUE! | #VALUE! | 0.011415 | #VALUE! | #VALUE! | #VALUE! | 0.0002083 | 1.724 | 4 | 0.0013928 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | 6 | 6.7 | 9 |  | 7788 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2263 | 3445 | 577 | 50 | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3903002010 | 60 | 10 | 3 | 90 | 300 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 7096.8 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.08 | 1.08 | 1.08 | 572 | #VALUE! | #VALUE! | #VALUE! | 30 | #VALUE! | #VALUE! | #VALUE! | 0.0058181 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 2 | 0.00037661 | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0.95 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4 | 6 | 6.7 | 9 |  | 8871 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3301 | 508 | #VALUE! | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3903002110 | 60 | 10 | 3 | 90 | 300 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 9048 | #VALUE! | #VALUE! | #VALUE! | 1.5 | 1.05 | 1.05 | 1.05 | 730 | #VALUE! | #VALUE! | #VALUE! | 38 | #VALUE! | #VALUE! | #VALUE! | 0.014778 | #VALUE! | #VALUE! | #VALUE! | 0.0001276 | 1.7219 | 4 | 0.0005142 | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0.85 | 0.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8 | 6 | 6.7 | 9 |  | 11310 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4479 | 834 | #VALUE! | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
135601015 | 80 | 15 | 1 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 485.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 539 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
135601115 | 80 | 15 | 1 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 488.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 718 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
135601515 | 80 | 15 | 1 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 705.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 882 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135601615 | 80 | 15 | 1 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 650.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 956 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135602015 | 80 | 15 | 1 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 988.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1236 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
135602115 | 80 | 15 | 1 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1014.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1268 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135701015 | 80 | 15 | 1 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 566.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 629 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
135701115 | 80 | 15 | 1 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 569.16 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 837 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
135701515 | 70 | 15 | 1 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 193 | 208 | 275 | 3 | 10 | 11 | 14 | 5.5819e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1029 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | 1127 | 2539 | 352 | 62 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
135701615 | 70 | 15 | 1 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 758.2 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 273 | 294 | 389 | 3 | 14 | 15 | 20 | 0.00015302 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1115 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | 2263 | 3445 | 577 | 50 | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
135702015 | 70 | 15 | 1 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1153.6 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 93 | 269 | 288 | 345 | 5 | 14 | 15 | 18 | 0.00011449 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1442 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | #VALUE! | 3301 | 508 | #VALUE! | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
135702115 | 70 | 15 | 1 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1184 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 95 | 383 | 411 | 544 | 5 | 20 | 21 | 28 | 0.00017042 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1480 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | #VALUE! | 4479 | 834 | #VALUE! | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
135801015 | 80 | 15 | 1 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 646.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 718 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 3682 | 458 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
135801115 | 80 | 15 | 1 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 650.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 957 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 5340 | 750 | #VALUE! | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
135801515 | 80 | 15 | 1 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 940.8 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 228 | 244 | 328 | 4 | 12 | 13 | 17 | 0.00010164 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1176 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135801615 | 80 | 15 | 1 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 866.32 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 70 | 322 | 345 | 463 | 4 | 17 | 18 | 24 | 0.00027685 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135802015 | 80 | 15 | 1 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1318.4 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 106 | 317 | 341 | 411 | 5 | 16 | 18 | 21 | 0.00011849 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
135802115 | 80 | 15 | 1 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1352.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 109 | 451 | 484 | 649 | 6 | 23 | 25 | 33 | 0.00025318 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 1691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135901015 | 80 | 15 | 1 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 727.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 808 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
135901115 | 80 | 15 | 1 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 731.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00012974 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1076 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
135901515 | 80 | 15 | 1 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1058.4 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 238 | 254 | 341 | 4 | 12 | 13 | 18 | 0.0001061 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1323 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
135901615 | 80 | 15 | 1 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 975.12 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 344 | 366 | 489 | 4 | 18 | 19 | 25 | 0.00028576 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1434 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
135902015 | 80 | 15 | 1 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1483.2 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 120 | 332 | 356 | 430 | 6 | 17 | 18 | 22 | 0.00017422 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1854 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
135902115 | 80 | 15 | 1 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1522.4 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 123 | 465 | 497 | 669 | 6 | 24 | 26 | 35 | 0.00026412 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 1903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351001015 | 80 | 15 | 1 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 808.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.7174e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 898 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351001115 | 80 | 15 | 1 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 813.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.0001402 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1196 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351001515 | 80 | 15 | 1 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1176 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 95 | 248 | 264 | 354 | 5 | 13 | 14 | 18 | 0.00016918 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1470 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351001615 | 80 | 15 | 1 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1083.24 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 366 | 388 | 516 | 4 | 19 | 20 | 27 | 0.00029467 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1593 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351002015 | 80 | 15 | 1 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1648 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 133 | 348 | 372 | 448 | 7 | 18 | 19 | 23 | 0.00024191 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2060 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351002115 | 80 | 15 | 1 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 136 | 480 | 511 | 689 | 7 | 25 | 26 | 36 | 0.00036904 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 2114 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351101015 | 80 | 15 | 1 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 889.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 988 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351101115 | 80 | 15 | 1 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 894.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1316 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351101515 | 70 | 15 | 1 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1293.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 238 | 251 | 327 | 5 | 12 | 13 | 17 | 0.00017573 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1617 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1351101615 | 70 | 15 | 1 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1191.36 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 368 | 386 | 493 | 5 | 19 | 20 | 25 | 0.00046639 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 1752 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1351102015 | 70 | 15 | 1 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1812.8 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 146 | 335 | 355 | 419 | 8 | 17 | 18 | 22 | 0.00032203 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2266 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1351102115 | 70 | 15 | 1 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1860 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 150 | 449 | 475 | 625 | 8 | 23 | 25 | 32 | 0.00049415 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2325 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1351201015 | 80 | 15 | 1 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 970.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1078 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351201115 | 80 | 15 | 1 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 975.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.000272 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1435 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351201515 | 80 | 15 | 1 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1411.2 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 272 | 288 | 380 | 6 | 14 | 15 | 20 | 0.00025759 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1764 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351201615 | 80 | 15 | 1 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1300.16 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 105 | 415 | 437 | 568 | 5 | 21 | 23 | 29 | 0.00047948 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 1912 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351202015 | 80 | 15 | 1 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1977.6 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 159 | 380 | 404 | 485 | 8 | 20 | 21 | 25 | 0.00033101 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2472 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351202115 | 80 | 15 | 1 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2029.6 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 164 | 516 | 547 | 729 | 8 | 27 | 28 | 38 | 0.0005121 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 2537 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351401015 | 80 | 15 | 1 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1131.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00024935 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1257 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351401115 | 80 | 15 | 1 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1138.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 92 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00045941 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1674 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351401515 | 80 | 15 | 1 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1646.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 133 | 296 | 312 | 406 | 7 | 15 | 16 | 21 | 0.00036862 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2058 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351401615 | 80 | 15 | 1 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1516.4 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 465 | 487 | 620 | 6 | 24 | 25 | 32 | 0.00071654 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2230 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351402015 | 80 | 15 | 1 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2307.2 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 186 | 412 | 437 | 522 | 10 | 21 | 23 | 27 | 0.00053465 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 2884 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351402115 | 80 | 15 | 1 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2368 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 191 | 552 | 583 | 769 | 10 | 28 | 30 | 40 | 0.00083507 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 2960 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351601015 | 80 | 15 | 1 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1293.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00027473 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1437 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351601115 | 80 | 15 | 1 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1301.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00051016 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 1914 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351601515 | 80 | 15 | 1 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1881.6 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 152 | 319 | 334 | 432 | 8 | 16 | 17 | 22 | 0.00050396 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2352 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1351601615 | 80 | 15 | 1 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1733.32 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 140 | 513 | 534 | 672 | 7 | 26 | 28 | 35 | 0.0010093 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 2549 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351602015 | 80 | 15 | 1 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2636.8 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 213 | 445 | 471 | 559 | 11 | 23 | 24 | 29 | 0.00067276 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3296 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1351602115 | 80 | 15 | 1 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2705.6 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 218 | 587 | 616 | 809 | 11 | 30 | 32 | 42 | 0.0010621 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 3382 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351801015 | 80 | 15 | 1 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1454.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00041786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1616 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1351801115 | 80 | 15 | 1 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1464.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00077912 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2153 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1351801515 | 60 | 15 | 1 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2116.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 171 | 302 | 312 | 378 | 9 | 16 | 16 | 20 | 0.00066522 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 2646 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1351801615 | 60 | 15 | 1 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1949.56 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 520 | 534 | 627 | 8 | 27 | 28 | 32 | 0.001361 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 2867 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1351802015 | 60 | 15 | 1 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2966.4 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 239 | 423 | 441 | 501 | 12 | 22 | 23 | 26 | 0.00083029 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 3708 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1351802115 | 60 | 15 | 1 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3044 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 245 | 530 | 549 | 680 | 13 | 27 | 28 | 35 | 0.0015376 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 3805 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352001015 | 80 | 15 | 1 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1616.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00059851 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1796 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352001115 | 80 | 15 | 1 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1626.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00112 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2392 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352001515 | 80 | 15 | 1 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2352 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 190 | 372 | 383 | 484 | 10 | 19 | 20 | 25 | 0.00085394 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 2940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352001615 | 80 | 15 | 1 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2166.48 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 175 | 618 | 634 | 777 | 9 | 32 | 33 | 40 | 0.001775 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 3186 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352002015 | 80 | 15 | 1 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3296 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 266 | 512 | 538 | 633 | 14 | 26 | 28 | 33 | 0.0011601 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352002115 | 80 | 15 | 1 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3382.4 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 273 | 668 | 691 | 890 | 14 | 34 | 36 | 46 | 0.0018611 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 4228 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352201015 | 80 | 15 | 1 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1658.413 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00064399 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1842.6812 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352201115 | 80 | 15 | 1 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1668.7594 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.001211 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 2454.058 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352201515 | 80 | 15 | 1 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2413.3565 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 195 | 398 | 407 | 510 | 10 | 21 | 21 | 26 | 0.00089719 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3016.6957 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352201615 | 80 | 15 | 1 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2222.8806 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 179 | 670 | 683 | 829 | 9 | 35 | 35 | 43 | 0.0018471 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 3268.942 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352202015 | 80 | 15 | 1 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3381.9826 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 273 | 545 | 571 | 670 | 14 | 28 | 29 | 35 | 0.0012072 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 4227.4783 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352202115 | 80 | 15 | 1 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3470.9101 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 280 | 708 | 726 | 930 | 14 | 37 | 37 | 48 | 0.0019552 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 4338.6377 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352401015 | 80 | 15 | 1 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1939.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00087721 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2155 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352401115 | 80 | 15 | 1 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 1951.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0016538 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 2870 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352401515 | 80 | 15 | 1 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2822.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 228 | 424 | 432 | 536 | 12 | 22 | 22 | 28 | 0.0013198 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 3528 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352401615 | 80 | 15 | 1 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2599.64 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 210 | 723 | 734 | 881 | 11 | 37 | 38 | 45 | 0.0028015 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 3823 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352402015 | 80 | 15 | 1 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3955.2 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 319 | 578 | 605 | 708 | 16 | 30 | 31 | 37 | 0.0016129 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 4944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352402115 | 80 | 15 | 1 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4059.2 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 327 | 748 | 764 | 970 | 17 | 39 | 39 | 50 | 0.0029395 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 5074 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352601015 | 80 | 15 | 1 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2008.3753 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 162 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00093455 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2231.5281 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352601115 | 80 | 15 | 1 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2021.4413 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0017685 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 2972.7079 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1352601515 | 60 | 15 | 1 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2922.8225 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 236 | 407 | 412 | 482 | 12 | 21 | 21 | 25 | 0.001379 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 3653.5281 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1352601615 | 60 | 15 | 1 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2692.036 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 217 | 729 | 736 | 836 | 11 | 38 | 38 | 43 | 0.0029035 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 3958.8764 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352602015 | 60 | 15 | 1 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4095.9281 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 330 | 560 | 579 | 649 | 17 | 29 | 30 | 33 | 0.001874 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 5119.9101 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1352602115 | 60 | 15 | 1 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4203.1551 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 339 | 691 | 701 | 841 | 17 | 36 | 36 | 43 | 0.003071 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 5253.9438 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352801015 | 60 | 15 | 1 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2262.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0012257 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2514 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1352801115 | 60 | 15 | 1 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2277.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0023241 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3349 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1352801515 | 80 | 15 | 1 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3292.8 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 266 | 476 | 481 | 588 | 14 | 25 | 25 | 30 | 0.001913 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1352801615 | 80 | 15 | 1 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3032.8 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 245 | 827 | 834 | 986 | 13 | 43 | 43 | 51 | 0.0041124 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 4460 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1352802015 | 80 | 15 | 1 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4614.4 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 372 | 650 | 679 | 782 | 19 | 34 | 35 | 40 | 0.0023897 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 5768 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1352802115 | 80 | 15 | 1 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4735.2 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 382 | 829 | 838 | 1050 | 20 | 43 | 43 | 54 | 0.0043256 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 5919 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150601015 | 80 | 15 | 1 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 581.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 646 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150601115 | 80 | 15 | 1 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 565.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 832 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150601515 | 80 | 15 | 1 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 832 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1040 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150601615 | 80 | 15 | 1 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 774.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1139 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150602015 | 80 | 15 | 1 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1455 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150602115 | 80 | 15 | 1 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1549 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150701015 | 80 | 15 | 1 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 677.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 753 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150701115 | 80 | 15 | 1 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 659.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 970 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150701515 | 70 | 15 | 1 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 971.2 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1214 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
150701615 | 70 | 15 | 1 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1329 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
150702015 | 70 | 15 | 1 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 110 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1698 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
150702115 | 70 | 15 | 1 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 117 | 383 | 411 | 544 | 6 | 20 | 21 | 28 | 0.00024224 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1807 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
150801015 | 80 | 15 | 1 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 774.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 861 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150801115 | 80 | 15 | 1 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 754.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1109 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150801515 | 80 | 15 | 1 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150801615 | 80 | 15 | 1 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 83 | 322 | 345 | 463 | 4 | 17 | 18 | 24 | 0.00027685 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150802015 | 80 | 15 | 1 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 317 | 341 | 411 | 6 | 16 | 18 | 21 | 0.00016875 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150802115 | 80 | 15 | 1 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 133 | 451 | 484 | 649 | 7 | 23 | 25 | 33 | 0.00034051 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150901015 | 80 | 15 | 1 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 871.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 968 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
150901115 | 80 | 15 | 1 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 847.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1247 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
150901515 | 80 | 15 | 1 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 238 | 254 | 341 | 5 | 12 | 13 | 18 | 0.00016264 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1561 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
150901615 | 80 | 15 | 1 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 94 | 344 | 366 | 489 | 5 | 18 | 19 | 25 | 0.00044021 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1708 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
150902015 | 80 | 15 | 1 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 332 | 356 | 430 | 7 | 17 | 18 | 22 | 0.00023478 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2183 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
150902115 | 80 | 15 | 1 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 150 | 465 | 497 | 669 | 8 | 24 | 26 | 35 | 0.00045824 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 2324 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501001015 | 80 | 15 | 1 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 968.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1076 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501001115 | 80 | 15 | 1 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 942.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1386 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501001515 | 80 | 15 | 1 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 248 | 264 | 354 | 6 | 13 | 14 | 18 | 0.00023966 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1734 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501001615 | 80 | 15 | 1 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 104 | 366 | 388 | 516 | 5 | 19 | 20 | 27 | 0.0004533 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1898 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501002015 | 80 | 15 | 1 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 348 | 372 | 448 | 8 | 18 | 19 | 23 | 0.00031305 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2425 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501002115 | 80 | 15 | 1 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 167 | 480 | 511 | 689 | 9 | 25 | 26 | 36 | 0.00059642 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 2582 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501101015 | 80 | 15 | 1 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1065.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1184 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501101115 | 80 | 15 | 1 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1037 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1525 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501101515 | 70 | 15 | 1 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 238 | 251 | 327 | 6 | 12 | 13 | 17 | 0.00024862 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1907 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1501101615 | 70 | 15 | 1 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 368 | 386 | 493 | 6 | 19 | 20 | 25 | 0.00066276 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 2088 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1501102015 | 70 | 15 | 1 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 335 | 355 | 419 | 9 | 17 | 18 | 22 | 0.00040407 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1501102115 | 70 | 15 | 1 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 183 | 449 | 475 | 625 | 9 | 23 | 25 | 32 | 0.00061841 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1501201015 | 80 | 15 | 1 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1161.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501201115 | 80 | 15 | 1 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1130.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501201515 | 80 | 15 | 1 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 272 | 288 | 380 | 7 | 14 | 15 | 20 | 0.00034524 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2081 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501201615 | 80 | 15 | 1 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 125 | 415 | 437 | 568 | 6 | 21 | 23 | 29 | 0.00068069 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 2278 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501202015 | 80 | 15 | 1 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 188 | 380 | 404 | 485 | 10 | 20 | 21 | 25 | 0.00050829 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2910 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501202115 | 80 | 15 | 1 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 200 | 516 | 547 | 729 | 10 | 27 | 28 | 38 | 0.00078234 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 3098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501401015 | 80 | 15 | 1 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1355.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501401115 | 80 | 15 | 1 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1319.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00045941 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1940 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501401515 | 80 | 15 | 1 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 157 | 296 | 312 | 406 | 8 | 15 | 16 | 21 | 0.00047453 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2428 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501401615 | 80 | 15 | 1 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 146 | 465 | 487 | 620 | 8 | 24 | 25 | 32 | 0.0012433 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2657 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501402015 | 80 | 15 | 1 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 412 | 437 | 522 | 11 | 21 | 23 | 27 | 0.00064169 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3395 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501402115 | 80 | 15 | 1 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 233 | 552 | 583 | 769 | 12 | 28 | 30 | 40 | 0.0011789 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 3615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501601015 | 80 | 15 | 1 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1549.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1722 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501601115 | 80 | 15 | 1 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1508.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00070949 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2218 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501601515 | 80 | 15 | 1 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 319 | 334 | 432 | 9 | 16 | 17 | 22 | 0.00062916 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2774 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1501601615 | 80 | 15 | 1 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 167 | 513 | 534 | 672 | 9 | 26 | 28 | 35 | 0.0016307 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 3037 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501602015 | 80 | 15 | 1 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 250 | 445 | 471 | 559 | 13 | 23 | 24 | 29 | 0.0009253 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1501602115 | 80 | 15 | 1 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 267 | 587 | 616 | 809 | 14 | 30 | 32 | 42 | 0.0016729 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 4131 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501801015 | 80 | 15 | 1 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1743.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1937 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1501801115 | 80 | 15 | 1 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1696.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 137 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.001029 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2495 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1501801515 | 60 | 15 | 1 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 201 | 302 | 312 | 378 | 10 | 16 | 16 | 20 | 0.00081069 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1501801615 | 60 | 15 | 1 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 187 | 609 | 650 | 927 | 10 | 31 | 34 | 48 | 0.0020811 | 0.018154 | 0.021685 | 0.042151 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 3416 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1501802015 | 60 | 15 | 1 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 282 | 423 | 441 | 501 | 15 | 22 | 23 | 26 | 0.0012692 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4365 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1501802115 | 60 | 15 | 1 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 300 | 530 | 549 | 680 | 15 | 27 | 28 | 35 | 0.0020114 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 4648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502001015 | 80 | 15 | 1 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1936.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00076253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2152 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502001115 | 80 | 15 | 1 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1884.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0014244 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2772 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502001515 | 80 | 15 | 1 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 224 | 372 | 383 | 484 | 12 | 19 | 20 | 25 | 0.0012013 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3468 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502001615 | 80 | 15 | 1 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 208 | 618 | 634 | 777 | 11 | 32 | 33 | 40 | 0.0025976 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 3796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502002015 | 80 | 15 | 1 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 313 | 512 | 538 | 633 | 16 | 26 | 28 | 33 | 0.0014945 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4850 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502002115 | 80 | 15 | 1 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 333 | 668 | 691 | 890 | 17 | 34 | 36 | 46 | 0.0026765 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 5164 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502201015 | 80 | 15 | 1 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1987.0174 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00081987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2207.7971 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502201115 | 80 | 15 | 1 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1933.9003 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0015391 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 2843.971 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502201515 | 80 | 15 | 1 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2847.0493 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 230 | 398 | 407 | 510 | 12 | 21 | 21 | 26 | 0.0012605 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3558.8116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502201615 | 80 | 15 | 1 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2648.5014 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 214 | 670 | 683 | 829 | 11 | 35 | 35 | 43 | 0.0026996 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 3894.8551 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502202015 | 80 | 15 | 1 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3981.2174 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 321 | 545 | 571 | 670 | 17 | 28 | 29 | 35 | 0.0017425 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 4976.5217 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502202115 | 80 | 15 | 1 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4239.1072 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 342 | 708 | 726 | 930 | 18 | 37 | 37 | 48 | 0.0031242 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 5298.8841 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502401015 | 80 | 15 | 1 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2323.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0013125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2582 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502401115 | 80 | 15 | 1 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2261.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0020427 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502401515 | 80 | 15 | 1 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 269 | 424 | 432 | 536 | 14 | 22 | 22 | 28 | 0.0017585 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4162 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502401615 | 80 | 15 | 1 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 250 | 723 | 734 | 881 | 13 | 37 | 38 | 45 | 0.0038405 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 4555 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502402015 | 80 | 15 | 1 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 375 | 578 | 605 | 708 | 19 | 30 | 31 | 37 | 0.0022305 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 5820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502402115 | 80 | 15 | 1 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 400 | 748 | 764 | 970 | 21 | 39 | 39 | 50 | 0.0043563 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 6197 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502601015 | 80 | 15 | 1 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2407.0146 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.001397 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2674.4607 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502601115 | 80 | 15 | 1 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2342.5542 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 189 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0026367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3444.9326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1502601515 | 60 | 15 | 1 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3447.5955 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 278 | 407 | 412 | 482 | 14 | 21 | 21 | 25 | 0.0018357 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4309.4944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1502601615 | 60 | 15 | 1 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3207.5065 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 259 | 729 | 736 | 836 | 13 | 38 | 38 | 43 | 0.0039765 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 4716.9213 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502602015 | 60 | 15 | 1 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4821.6629 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 389 | 560 | 579 | 649 | 20 | 29 | 30 | 33 | 0.0025443 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 6027.0787 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1502602115 | 60 | 15 | 1 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5134.1124 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 414 | 691 | 701 | 841 | 21 | 36 | 36 | 43 | 0.0045455 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 6417.6404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502801015 | 60 | 15 | 1 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2711.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0017586 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3013 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1502801115 | 60 | 15 | 1 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2639.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.003327 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3881 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1502801515 | 80 | 15 | 1 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 313 | 476 | 481 | 588 | 16 | 25 | 25 | 30 | 0.0024501 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4855 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1502801615 | 80 | 15 | 1 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 291 | 827 | 834 | 986 | 15 | 43 | 43 | 51 | 0.005382 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 5314 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1502802015 | 80 | 15 | 1 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 438 | 650 | 679 | 782 | 23 | 34 | 35 | 40 | 0.0034217 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 6790 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1502802115 | 80 | 15 | 1 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5784 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 466 | 829 | 838 | 1050 | 24 | 43 | 43 | 54 | 0.0060645 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 7230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165601015 | 80 | 15 | 1 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 654.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 727 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165601115 | 80 | 15 | 1 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 629.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 926 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165601515 | 80 | 15 | 1 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 922.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1153 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165601615 | 80 | 15 | 1 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 886.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1304 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165602015 | 80 | 15 | 1 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1288.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1611 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165602115 | 80 | 15 | 1 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1454.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 117 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1818 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165701015 | 80 | 15 | 1 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 763.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 848 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165701115 | 80 | 15 | 1 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 734.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1080 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165701515 | 70 | 15 | 1 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1076 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 87 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1345 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
165701615 | 70 | 15 | 1 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1034.28 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 83 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 245 | 263 | 349 | 0.95 | 0.95 | 0.95 | 194.8253 | 209.139 | 277.5266 | 42 | 45 | 60 | 0.026932 | 0.030855 | 0.054417 | 1.4 | 6 | 6.7 | 9 |  | 1521 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.8253 | 209.139 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
165702015 | 70 | 15 | 1 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1504 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
165702115 | 70 | 15 | 1 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1696.8 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 137 | 383 | 411 | 544 | 7 | 20 | 21 | 28 | 0.00032624 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 268 | 287 | 380 | 0.85 | 0.85 | 0.85 | 218.3182 | 233.7959 | 309.5556 | 47 | 50 | 67 | 0.013237 | 0.01494 | 0.026498 | 1.9 | 6 | 6.7 | 9 |  | 2121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 218.3182 | 233.7959 | 309.5556 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
165801015 | 80 | 15 | 1 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 872.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 969 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165801115 | 80 | 15 | 1 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 839.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1234 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165801515 | 80 | 15 | 1 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1230.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1538 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165801615 | 80 | 15 | 1 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1181.84 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 95 | 322 | 345 | 463 | 5 | 17 | 18 | 24 | 0.00042712 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 289 | 310 | 416 | 0.95 | 0.95 | 0.95 | 229.8143 | 246.5136 | 330.8054 | 49 | 53 | 71 | 0.037165 | 0.043371 | 0.077133 | 1.6 | 6 | 6.7 | 9 |  | 1738 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 229.8143 | 246.5136 | 330.8054 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165802015 | 80 | 15 | 1 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1718.4 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 139 | 317 | 341 | 411 | 7 | 16 | 18 | 21 | 0.00022764 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2148 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165802115 | 80 | 15 | 1 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1939.2 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 156 | 451 | 484 | 649 | 8 | 23 | 25 | 33 | 0.00044029 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315 | 338 | 454 | 0.85 | 0.85 | 0.85 | 256.6053 | 275.3416 | 369.8375 | 55 | 59 | 80 | 0.0185 | 0.021216 | 0.038459 | 2.1 | 6 | 6.7 | 9 |  | 2424 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.6053 | 275.3416 | 369.8375 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165901015 | 80 | 15 | 1 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 981 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1090 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
165901115 | 80 | 15 | 1 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 944.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1389 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
165901515 | 80 | 15 | 1 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1384 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1730 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
165901615 | 80 | 15 | 1 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1330.08 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 107 | 344 | 366 | 489 | 6 | 18 | 19 | 25 | 0.00062691 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 290 | 310 | 423 | 0.95 | 0.95 | 0.95 | 230.6095 | 246.5136 | 336.3718 | 50 | 53 | 72 | 0.039366 | 0.044137 | 0.080588 | 1.8 | 6 | 6.7 | 9 |  | 1956 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 230.6095 | 246.5136 | 336.3718 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
165902015 | 80 | 15 | 1 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1933.6 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 332 | 356 | 430 | 8 | 17 | 18 | 22 | 0.00030408 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2417 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
165902115 | 80 | 15 | 1 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2181.6 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 176 | 465 | 497 | 669 | 9 | 24 | 26 | 35 | 0.00057443 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 317 | 339 | 462 | 0.85 | 0.85 | 0.85 | 258.2346 | 276.1562 | 376.3545 | 56 | 59 | 81 | 0.019674 | 0.021777 | 0.040371 | 2.4 | 6 | 6.7 | 9 |  | 2727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 258.2346 | 276.1562 | 376.3545 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651001015 | 80 | 15 | 1 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1089.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1211 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651001115 | 80 | 15 | 1 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1049.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1543 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651001515 | 80 | 15 | 1 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1537.6 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 124 | 248 | 264 | 354 | 6 | 13 | 14 | 18 | 0.00023966 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1922 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651001615 | 80 | 15 | 1 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1477.64 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 119 | 366 | 388 | 516 | 6 | 19 | 20 | 27 | 0.00064483 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 291 | 312 | 430 | 0.95 | 0.95 | 0.95 | 231.4047 | 248.104 | 341.9382 | 50 | 53 | 74 | 0.040059 | 0.044904 | 0.086412 | 2 | 6 | 6.7 | 9 |  | 2173 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 231.4047 | 248.104 | 341.9382 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651002015 | 80 | 15 | 1 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2148 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 173 | 348 | 372 | 448 | 9 | 18 | 19 | 23 | 0.00039308 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2685 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651002115 | 80 | 15 | 1 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2424 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 195 | 480 | 511 | 689 | 10 | 25 | 26 | 36 | 0.00072961 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 319 | 341 | 471 | 0.85 | 0.85 | 0.85 | 259.8638 | 277.7854 | 383.686 | 56 | 60 | 82 | 0.020186 | 0.023077 | 0.042336 | 2.7 | 6 | 6.7 | 9 |  | 3030 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 259.8638 | 277.7854 | 383.686 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651101015 | 80 | 15 | 1 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1198.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1332 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651101115 | 80 | 15 | 1 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1153.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1697 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651101515 | 70 | 15 | 1 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 136 | 238 | 251 | 327 | 7 | 12 | 13 | 17 | 0.00033355 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2114 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1651101615 | 70 | 15 | 1 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1625.2 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 368 | 386 | 493 | 7 | 19 | 20 | 25 | 0.00089237 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 255 | 273 | 376 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.091 | 298.9972 | 44 | 47 | 64 | 0.031743 | 0.03611 | 0.066054 | 2.2 | 6 | 6.7 | 9 |  | 2390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.091 | 298.9972 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1651102015 | 70 | 15 | 1 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2363.2 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 191 | 335 | 355 | 419 | 10 | 17 | 18 | 22 | 0.00049511 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2954 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1651102115 | 70 | 15 | 1 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2666.4 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 215 | 449 | 475 | 625 | 11 | 23 | 25 | 32 | 0.00090675 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 281 | 301 | 415 | 0.85 | 0.85 | 0.85 | 228.9082 | 245.2006 | 338.0673 | 49 | 53 | 73 | 0.015989 | 0.018608 | 0.034581 | 2.9 | 6 | 6.7 | 9 |  | 3333 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.9082 | 245.2006 | 338.0673 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1651201015 | 80 | 15 | 1 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1307.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1453 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651201115 | 80 | 15 | 1 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1259.36 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1852 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651201515 | 80 | 15 | 1 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 149 | 272 | 288 | 380 | 8 | 14 | 15 | 20 | 0.00044509 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651201615 | 80 | 15 | 1 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1773.44 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 143 | 415 | 437 | 568 | 7 | 21 | 23 | 29 | 0.00091576 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 298 | 319 | 444 | 0.95 | 0.95 | 0.95 | 236.9712 | 253.6705 | 353.0711 | 51 | 55 | 76 | 0.043079 | 0.04992 | 0.093911 | 2.4 | 6 | 6.7 | 9 |  | 2608 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.9712 | 253.6705 | 353.0711 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651202015 | 80 | 15 | 1 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2577.6 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 208 | 380 | 404 | 485 | 11 | 20 | 21 | 25 | 0.00061062 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3222 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651202115 | 80 | 15 | 1 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2908.8 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 235 | 516 | 547 | 729 | 12 | 27 | 28 | 38 | 0.0011067 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 327 | 351 | 488 | 0.85 | 0.85 | 0.85 | 266.3808 | 285.9316 | 397.5346 | 57 | 61 | 85 | 0.021947 | 0.025016 | 0.047501 | 3.2 | 6 | 6.7 | 9 |  | 3636 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3808 | 285.9316 | 397.5346 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651401015 | 80 | 15 | 1 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1525.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1695 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651401115 | 80 | 15 | 1 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1468.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00063987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2160 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651401515 | 80 | 15 | 1 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2152.8 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 174 | 296 | 312 | 406 | 9 | 15 | 16 | 21 | 0.00059309 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651401615 | 80 | 15 | 1 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2068.56 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 167 | 465 | 487 | 620 | 9 | 24 | 25 | 32 | 0.0015586 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 304 | 326 | 457 | 0.95 | 0.95 | 0.95 | 241.7424 | 259.2369 | 363.4088 | 52 | 56 | 78 | 0.046227 | 0.053393 | 0.10179 | 2.8 | 6 | 6.7 | 9 |  | 3042 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 259.2369 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651402015 | 80 | 15 | 1 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3007.2 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 243 | 412 | 437 | 522 | 13 | 21 | 23 | 27 | 0.00088388 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3759 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651402115 | 80 | 15 | 1 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3393.6 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 274 | 552 | 583 | 769 | 14 | 28 | 30 | 40 | 0.0015788 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 336 | 360 | 505 | 0.85 | 0.85 | 0.85 | 273.7123 | 293.2632 | 411.3831 | 59 | 63 | 88 | 0.024578 | 0.027878 | 0.05303 | 3.7 | 6 | 6.7 | 9 |  | 4242 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 273.7123 | 293.2632 | 411.3831 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651601015 | 80 | 15 | 1 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1744.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00050754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1938 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651601115 | 80 | 15 | 1 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1678.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00093804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2469 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651601515 | 80 | 15 | 1 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2460 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 319 | 334 | 432 | 10 | 16 | 17 | 22 | 0.00076744 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 3075 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1651601615 | 80 | 15 | 1 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2364.36 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 191 | 513 | 534 | 672 | 10 | 26 | 28 | 35 | 0.0019946 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 310 | 331 | 471 | 0.95 | 0.95 | 0.95 | 246.5136 | 263.2129 | 374.5417 | 53 | 57 | 81 | 0.049504 | 0.057002 | 0.11275 | 3.2 | 6 | 6.7 | 9 |  | 3477 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 246.5136 | 263.2129 | 374.5417 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651602015 | 80 | 15 | 1 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3436.8 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 277 | 445 | 471 | 559 | 14 | 23 | 24 | 29 | 0.001066 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 4296 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1651602115 | 80 | 15 | 1 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3878.4 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 313 | 587 | 616 | 809 | 16 | 30 | 32 | 42 | 0.0021524 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 343 | 366 | 522 | 0.85 | 0.85 | 0.85 | 279.4147 | 298.1509 | 425.2317 | 60 | 64 | 91 | 0.026537 | 0.030024 | 0.058931 | 4.3 | 6 | 6.7 | 9 |  | 4848 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 279.4147 | 298.1509 | 425.2317 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651801015 | 80 | 15 | 1 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1962 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00070519 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 2180 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1651801115 | 80 | 15 | 1 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1888.36 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0013098 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2777 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1651801515 | 60 | 15 | 1 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2768 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 223 | 302 | 312 | 378 | 12 | 16 | 16 | 20 | 0.0011421 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3460 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1651801615 | 60 | 15 | 1 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2659.48 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 214 | 520 | 534 | 627 | 11 | 27 | 28 | 32 | 0.0024957 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 240 | 256 | 365 | 0.95 | 0.95 | 0.95 | 190.8492 | 203.5725 | 290.2499 | 41 | 44 | 62 | 0.031101 | 0.035637 | 0.069107 | 3.6 | 6 | 6.7 | 9 |  | 3911 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 203.5725 | 290.2499 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1651802015 | 60 | 15 | 1 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3866.4 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 312 | 423 | 441 | 501 | 16 | 22 | 23 | 26 | 0.0014352 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4833 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1651802115 | 60 | 15 | 1 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4363.2 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 352 | 530 | 549 | 680 | 18 | 27 | 28 | 35 | 0.002834 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 269 | 287 | 409 | 0.85 | 0.85 | 0.85 | 219.1328 | 233.7959 | 333.1796 | 47 | 50 | 72 | 0.017403 | 0.019575 | 0.039195 | 4.8 | 6 | 6.7 | 9 |  | 5454 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.1328 | 233.7959 | 333.1796 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652001015 | 80 | 15 | 1 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 2179.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 176 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00094435 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2422 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652001115 | 80 | 15 | 1 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 2098.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 169 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0017614 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 3086 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652001515 | 80 | 15 | 1 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3075.2 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 248 | 372 | 383 | 484 | 13 | 19 | 20 | 25 | 0.0013958 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652001615 | 80 | 15 | 1 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2955.28 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 238 | 618 | 634 | 777 | 12 | 32 | 33 | 40 | 0.0030647 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 328 | 346 | 499 | 0.95 | 0.95 | 0.95 | 260.8273 | 275.141 | 396.8074 | 56 | 59 | 85 | 0.058451 | 0.064634 | 0.13074 | 4 | 6 | 6.7 | 9 |  | 4346 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 260.8273 | 275.141 | 396.8074 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652002015 | 80 | 15 | 1 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4296 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 346 | 512 | 538 | 633 | 18 | 26 | 28 | 33 | 0.001869 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 5370 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652002115 | 80 | 15 | 1 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4848 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 391 | 668 | 691 | 890 | 20 | 34 | 36 | 46 | 0.0036299 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 365 | 385 | 556 | 0.85 | 0.85 | 0.85 | 297.3363 | 313.6287 | 452.9287 | 64 | 67 | 97 | 0.032602 | 0.035564 | 0.071889 | 5.3 | 6 | 6.7 | 9 |  | 6060 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 297.3363 | 313.6287 | 452.9287 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652201015 | 80 | 15 | 1 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2236.3565 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0010147 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2484.8406 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652201115 | 80 | 15 | 1 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2153.1067 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001902 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3166.3333 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652201515 | 80 | 15 | 1 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3155.5594 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 254 | 398 | 407 | 510 | 13 | 21 | 21 | 26 | 0.0014638 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3944.4493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652201615 | 80 | 15 | 1 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3032.258 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 245 | 670 | 683 | 829 | 13 | 35 | 35 | 43 | 0.0037045 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 337 | 351 | 513 | 0.95 | 0.95 | 0.95 | 267.9842 | 279.117 | 407.9403 | 58 | 60 | 88 | 0.064331 | 0.06866 | 0.14348 | 4.4 | 6 | 6.7 | 9 |  | 4459.2029 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267.9842 | 279.117 | 407.9403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652202015 | 80 | 15 | 1 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4408.0696 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 355 | 545 | 571 | 670 | 18 | 28 | 29 | 35 | 0.0019415 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 5510.087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652202115 | 80 | 15 | 1 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4974.4696 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 401 | 708 | 726 | 930 | 21 | 37 | 37 | 48 | 0.0041671 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 377 | 392 | 573 | 0.85 | 0.85 | 0.85 | 307.1118 | 319.3311 | 466.7773 | 66 | 69 | 100 | 0.035922 | 0.039074 | 0.078965 | 5.9 | 6 | 6.7 | 9 |  | 6218.087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 307.1118 | 319.3311 | 466.7773 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652401015 | 80 | 15 | 1 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2615.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 211 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0015594 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2906 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652401115 | 80 | 15 | 1 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2518.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0024679 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3703 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652401515 | 80 | 15 | 1 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3690.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 298 | 424 | 432 | 536 | 15 | 22 | 22 | 28 | 0.0019998 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652401615 | 80 | 15 | 1 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3546.2 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 286 | 723 | 734 | 881 | 15 | 37 | 38 | 45 | 0.005034 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 347 | 359 | 527 | 0.95 | 0.95 | 0.95 | 275.9362 | 285.4787 | 419.0731 | 59 | 61 | 90 | 0.068323 | 0.07283 | 0.15366 | 4.8 | 6 | 6.7 | 9 |  | 5215 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 275.9362 | 285.4787 | 419.0731 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652402015 | 80 | 15 | 1 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5155.2 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 416 | 578 | 605 | 708 | 21 | 30 | 31 | 37 | 0.0026947 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 6444 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652402115 | 80 | 15 | 1 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5817.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 469 | 748 | 764 | 970 | 24 | 39 | 39 | 50 | 0.0055883 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 388 | 402 | 590 | 0.85 | 0.85 | 0.85 | 316.0726 | 327.4773 | 480.6258 | 68 | 70 | 103 | 0.03944 | 0.041657 | 0.08645 | 6.4 | 6 | 6.7 | 9 |  | 7272 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 316.0726 | 327.4773 | 480.6258 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652601015 | 80 | 15 | 1 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2708.9899 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 218 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.001659 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 3009.9888 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652601115 | 80 | 15 | 1 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2607.5326 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0031278 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3834.6067 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1652601515 | 60 | 15 | 1 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3821.8247 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 308 | 407 | 412 | 482 | 16 | 21 | 21 | 25 | 0.0023528 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4777.2809 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
1652601615 | 60 | 15 | 1 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3672.2751 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 296 | 729 | 736 | 836 | 15 | 38 | 38 | 43 | 0.005208 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277 | 287 | 420 | 0.95 | 0.95 | 0.95 | 220.2718 | 228.2239 | 333.9862 | 47 | 49 | 72 | 0.045459 | 0.04922 | 0.10269 | 5.2 | 6 | 6.7 | 9 |  | 5400.4045 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 228.2239 | 333.9862 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652602015 | 60 | 15 | 1 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5338.6247 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 431 | 560 | 579 | 649 | 22 | 29 | 30 | 33 | 0.0030448 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 6673.2809 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
1652602115 | 60 | 15 | 1 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6024.5933 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 486 | 691 | 701 | 841 | 25 | 36 | 36 | 43 | 0.0062862 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 314 | 326 | 478 | 0.85 | 0.85 | 0.85 | 255.7907 | 265.5661 | 389.3884 | 55 | 57 | 84 | 0.027436 | 0.029338 | 0.060837 | 6.9 | 6 | 6.7 | 9 |  | 7530.7416 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 255.7907 | 265.5661 | 389.3884 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652801015 | 60 | 15 | 1 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3051.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0023761 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3391 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
1652801115 | 60 | 15 | 1 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2937.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 237 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0038875 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 4320 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
1652801515 | 80 | 15 | 1 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4305.6 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 347 | 476 | 481 | 588 | 18 | 25 | 25 | 30 | 0.0030486 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 5382 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1652801615 | 80 | 15 | 1 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4137.12 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 334 | 827 | 834 | 986 | 17 | 43 | 43 | 51 | 0.0068121 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 373 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 296.6115 | 441.3389 | 62 | 64 | 95 | 0.079154 | 0.084096 | 0.17888 | 5.6 | 6 | 6.7 | 9 |  | 6084 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 296.6115 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1652802015 | 80 | 15 | 1 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6014.4 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 485 | 650 | 679 | 782 | 25 | 34 | 35 | 40 | 0.0040028 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 7518 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1652802115 | 80 | 15 | 1 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6787.2 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 547 | 829 | 838 | 1050 | 28 | 43 | 43 | 54 | 0.0080738 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 411 | 420 | 624 | 0.85 | 0.85 | 0.85 | 334.8088 | 342.1404 | 508.3229 | 72 | 74 | 109 | 0.047089 | 0.049573 | 0.10269 | 7.5 | 6 | 6.7 | 9 |  | 8484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 334.8088 | 342.1404 | 508.3229 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195601015 | 80 | 15 | 1 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 752.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 836 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195601115 | 80 | 15 | 1 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 733.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1078 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195601515 | 80 | 15 | 1 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1030.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1288 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195601615 | 80 | 15 | 1 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1092.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1606 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195602015 | 80 | 15 | 1 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1436 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1795 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195602115 | 80 | 15 | 1 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1881.6 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2352 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195701015 | 80 | 15 | 1 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 877.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 975 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195701115 | 80 | 15 | 1 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 854.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1257 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195701515 | 70 | 15 | 1 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1201.6 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 97 | 193 | 208 | 275 | 5 | 10 | 11 | 14 | 0.00014954 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1502 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
195701615 | 70 | 15 | 1 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1274.32 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 103 | 273 | 294 | 389 | 5 | 14 | 15 | 20 | 0.00041403 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 206 | 221 | 292 | 0.95 | 0.95 | 0.95 | 163.8123 | 175.7404 | 232.1999 | 35 | 38 | 50 | 0.018805 | 0.022112 | 0.037979 | 1.4 | 6 | 6.7 | 9 |  | 1874 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.8123 | 175.7404 | 232.1999 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
195702015 | 70 | 15 | 1 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1675.2 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 135 | 269 | 288 | 345 | 7 | 14 | 15 | 18 | 0.00022051 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 2094 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
195702115 | 70 | 15 | 1 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 2195.2 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 177 | 383 | 411 | 544 | 9 | 20 | 21 | 28 | 0.00053044 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 224 | 241 | 319 | 0.85 | 0.85 | 0.85 | 182.4749 | 196.3234 | 259.8638 | 39 | 42 | 56 | 0.0091917 | 0.010624 | 0.01865 | 1.9 | 6 | 6.7 | 9 |  | 2744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 182.4749 | 196.3234 | 259.8638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
195801015 | 80 | 15 | 1 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1002.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 1114 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195801115 | 80 | 15 | 1 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 977.16 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1437 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195801515 | 80 | 15 | 1 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1373.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 228 | 244 | 328 | 6 | 12 | 13 | 17 | 0.00022173 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1717 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195801615 | 80 | 15 | 1 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1456.56 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 117 | 322 | 345 | 463 | 6 | 17 | 18 | 24 | 0.00060898 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 242 | 260 | 348 | 0.95 | 0.95 | 0.95 | 192.4397 | 206.7534 | 276.7314 | 41 | 44 | 59 | 0.026176 | 0.030074 | 0.053565 | 1.6 | 6 | 6.7 | 9 |  | 2142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 192.4397 | 206.7534 | 276.7314 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195802015 | 80 | 15 | 1 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1915.2 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 317 | 341 | 411 | 8 | 16 | 18 | 21 | 0.0002951 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195802115 | 80 | 15 | 1 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2508.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 202 | 451 | 484 | 649 | 10 | 23 | 25 | 33 | 0.00067687 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264 | 283 | 380 | 0.85 | 0.85 | 0.85 | 215.0597 | 230.5375 | 309.5556 | 46 | 50 | 67 | 0.013057 | 0.015362 | 0.027195 | 2.1 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.0597 | 230.5375 | 309.5556 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195901015 | 80 | 15 | 1 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 1128.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1254 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
195901115 | 80 | 15 | 1 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 1098.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00033253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1616 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
195901515 | 80 | 15 | 1 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1544.8 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1931 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
195901615 | 80 | 15 | 1 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1638.12 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 132 | 344 | 366 | 489 | 7 | 18 | 19 | 25 | 0.00084561 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 243 | 260 | 354 | 0.95 | 0.95 | 0.95 | 193.2349 | 206.7534 | 281.5026 | 42 | 44 | 61 | 0.027959 | 0.030631 | 0.058175 | 1.8 | 6 | 6.7 | 9 |  | 2409 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.2349 | 206.7534 | 281.5026 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
195902015 | 80 | 15 | 1 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2154.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 174 | 332 | 356 | 430 | 9 | 17 | 18 | 22 | 0.00038208 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2693 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
195902115 | 80 | 15 | 1 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2822.4 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 228 | 465 | 497 | 669 | 12 | 24 | 26 | 35 | 0.00099848 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 265 | 284 | 387 | 0.85 | 0.85 | 0.85 | 215.8743 | 231.3521 | 315.258 | 46 | 50 | 68 | 0.013422 | 0.015783 | 0.028709 | 2.4 | 6 | 6.7 | 9 |  | 3528 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.8743 | 231.3521 | 315.258 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951001015 | 80 | 15 | 1 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1253.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1393 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951001115 | 80 | 15 | 1 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1221.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035791 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951001515 | 80 | 15 | 1 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1716.8 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 138 | 248 | 264 | 354 | 7 | 13 | 14 | 18 | 0.00032186 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 2146 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951001615 | 80 | 15 | 1 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1820.36 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 147 | 366 | 388 | 516 | 8 | 19 | 20 | 27 | 0.0011255 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 244 | 261 | 360 | 0.95 | 0.95 | 0.95 | 194.0301 | 207.5486 | 286.2739 | 42 | 45 | 62 | 0.028472 | 0.03259 | 0.061069 | 2 | 6 | 6.7 | 9 |  | 2677 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 207.5486 | 286.2739 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951002015 | 80 | 15 | 1 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2393.6 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 193 | 348 | 372 | 448 | 10 | 18 | 19 | 23 | 0.00048192 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2992 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951002115 | 80 | 15 | 1 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3136 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 253 | 480 | 511 | 689 | 13 | 25 | 26 | 36 | 0.0012062 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 267 | 286 | 394 | 0.85 | 0.85 | 0.85 | 217.5035 | 232.9813 | 320.9603 | 47 | 50 | 69 | 0.014373 | 0.016204 | 0.030271 | 2.7 | 6 | 6.7 | 9 |  | 3920 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.5035 | 232.9813 | 320.9603 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951101015 | 80 | 15 | 1 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1378.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1532 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951101115 | 80 | 15 | 1 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1343.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 108 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00053543 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1976 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951101515 | 70 | 15 | 1 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1888.8 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 152 | 238 | 251 | 327 | 8 | 12 | 13 | 17 | 0.00043037 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2361 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
1951101615 | 70 | 15 | 1 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2002.6 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 162 | 368 | 386 | 493 | 8 | 19 | 20 | 25 | 0.001155 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 229 | 315 | 0.95 | 0.95 | 0.95 | 170.1739 | 182.102 | 250.4896 | 37 | 39 | 54 | 0.022631 | 0.02508 | 0.047371 | 2.2 | 6 | 6.7 | 9 |  | 2945 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.1739 | 182.102 | 250.4896 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1951102015 | 70 | 15 | 1 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2632.8 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 212 | 335 | 355 | 419 | 11 | 17 | 18 | 22 | 0.00059509 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 3291 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
1951102115 | 70 | 15 | 1 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3449.6 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 278 | 449 | 475 | 625 | 14 | 23 | 25 | 32 | 0.0014376 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 235 | 252 | 347 | 0.85 | 0.85 | 0.85 | 191.4357 | 205.2842 | 282.6732 | 41 | 44 | 61 | 0.011333 | 0.012988 | 0.024423 | 2.9 | 6 | 6.7 | 9 |  | 4312 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 191.4357 | 205.2842 | 282.6732 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
1951201015 | 80 | 15 | 1 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1504.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1672 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951201115 | 80 | 15 | 1 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1465.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057024 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2155 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951201515 | 80 | 15 | 1 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2060 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 166 | 272 | 288 | 380 | 9 | 14 | 15 | 20 | 0.00055702 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2575 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951201615 | 80 | 15 | 1 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2184.16 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 176 | 415 | 437 | 568 | 9 | 21 | 23 | 29 | 0.0014865 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 249 | 267 | 372 | 0.95 | 0.95 | 0.95 | 198.0061 | 212.3198 | 295.8163 | 43 | 46 | 64 | 0.030884 | 0.035224 | 0.067115 | 2.4 | 6 | 6.7 | 9 |  | 3212 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 212.3198 | 295.8163 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951202015 | 80 | 15 | 1 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2872 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 232 | 380 | 404 | 485 | 12 | 20 | 21 | 25 | 0.00072203 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3590 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951202115 | 80 | 15 | 1 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3763.2 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 303 | 516 | 547 | 729 | 16 | 27 | 28 | 38 | 0.0019155 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 274 | 294 | 409 | 0.85 | 0.85 | 0.85 | 223.2059 | 239.4983 | 333.1796 | 48 | 51 | 72 | 0.015757 | 0.01771 | 0.034459 | 3.2 | 6 | 6.7 | 9 |  | 4704 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.2059 | 239.4983 | 333.1796 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951401015 | 80 | 15 | 1 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1755 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1950 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951401115 | 80 | 15 | 1 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1709.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 138 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084707 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2514 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
1951401515 | 80 | 15 | 1 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2403.2 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 194 | 296 | 312 | 406 | 10 | 15 | 16 | 21 | 0.0007242 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 3004 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
1951401615 | 80 | 15 | 1 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2548.64 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 206 | 465 | 487 | 620 | 11 | 24 | 25 | 32 | 0.0022918 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 255 | 273 | 383 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.091 | 304.5636 | 44 | 47 | 65 | 0.033412 | 0.03798 | 0.071359 | 2.8 | 6 | 6.7 | 9 |  | 3748 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.091 | 304.5636 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
1951402015 | 80 | 15 | 1 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3351.2 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 270 | 412 | 437 | 522 | 14 | 21 | 23 | 27 | 0.0010189 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 4189 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
1951402115 | 80 | 15 | 1 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4390.4 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 354 | 552 | 583 | 769 | 18 | 28 | 30 | 40 | 0.0025438 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 281 | 301 | 423 | 0.85 | 0.85 | 0.85 | 228.9082 | 245.2006 | 344.5843 | 49 | 53 | 74 | 0.01721 | 0.020005 | 0.037988 | 3.7 | 6 | 6.7 | 9 |  | 5488 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.9082 | 245.2006 | 344.5843 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220601015 | 80 | 15 | 2 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 306.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.1473e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 341 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
220601515 | 80 | 15 | 2 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 498.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 40 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4254e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 623 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
220602015 | 80 | 15 | 2 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 668.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4.0779e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 836 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
220701015 | 80 | 15 | 2 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 358.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.9253e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 398 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220701515 | 70 | 15 | 2 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 581.6 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 47 | 193 | 208 | 275 | 2 | 10 | 11 | 14 | 2.5603e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
220702015 | 70 | 15 | 2 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 780.8 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 269 | 288 | 345 | 3 | 14 | 15 | 18 | 4.2437e-05 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 976 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
220801015 | 80 | 15 | 2 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 408.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 33 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.1383e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 454 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
220801515 | 80 | 15 | 2 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 664 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 228 | 244 | 328 | 3 | 12 | 13 | 17 | 5.8533e-05 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 830 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
220802015 | 80 | 15 | 2 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 892 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 317 | 341 | 411 | 4 | 16 | 18 | 21 | 7.6905e-05 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1115 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
220901015 | 80 | 15 | 2 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 459.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 37 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.3972e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 511 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
220901515 | 80 | 15 | 2 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 747.2 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 60 | 238 | 254 | 341 | 3 | 12 | 13 | 18 | 6.1246e-05 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 934 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
220902015 | 80 | 15 | 2 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1004 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 332 | 356 | 430 | 4 | 17 | 18 | 22 | 7.9626e-05 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1255 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201001015 | 80 | 15 | 2 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 511.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 41 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.656e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 568 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201001515 | 80 | 15 | 2 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 830.4 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 248 | 264 | 354 | 3 | 13 | 14 | 18 | 6.3959e-05 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1038 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2201002015 | 80 | 15 | 2 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1115.2 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 90 | 348 | 372 | 448 | 5 | 18 | 19 | 23 | 0.00012648 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 1394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201101015 | 80 | 15 | 2 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 562.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 45 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.9149e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 625 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201101515 | 70 | 15 | 2 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 913.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 238 | 251 | 327 | 4 | 12 | 13 | 17 | 0.00011501 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1142 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
2201102015 | 70 | 15 | 2 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 335 | 355 | 419 | 5 | 17 | 18 | 22 | 0.00013047 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 1533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2201201015 | 80 | 15 | 2 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 613.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 50 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7635e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 682 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201201515 | 80 | 15 | 2 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 996.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 80 | 272 | 288 | 380 | 4 | 14 | 15 | 20 | 0.00011946 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1246 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201202015 | 80 | 15 | 2 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1338.4 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 108 | 380 | 404 | 485 | 6 | 20 | 21 | 25 | 0.00019063 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 1673 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201401015 | 80 | 15 | 2 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 715.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8096e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 795 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201401515 | 80 | 15 | 2 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1162.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 296 | 312 | 406 | 5 | 15 | 16 | 21 | 0.00019536 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 1453 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201402015 | 80 | 15 | 2 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1561.6 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 412 | 437 | 522 | 7 | 21 | 23 | 27 | 0.00027044 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 1952 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201601015 | 80 | 15 | 2 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 818.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010856 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 909 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201601515 | 80 | 15 | 2 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1328.8 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 107 | 319 | 334 | 432 | 6 | 16 | 17 | 22 | 0.00029344 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 1661 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2201602015 | 80 | 15 | 2 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1784 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 144 | 445 | 471 | 559 | 7 | 23 | 24 | 29 | 0.00028471 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 2230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2201801015 | 80 | 15 | 2 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 919.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020027 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1022 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2201801515 | 60 | 15 | 2 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1494.4 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 302 | 312 | 378 | 6 | 16 | 16 | 20 | 0.00031137 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 1868 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2201802015 | 60 | 15 | 2 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 162 | 423 | 441 | 501 | 8 | 22 | 23 | 26 | 0.00038487 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 2509 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2202001015 | 80 | 15 | 2 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1022.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0002175 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1136 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202001515 | 80 | 15 | 2 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1660.8 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 372 | 383 | 484 | 7 | 19 | 20 | 25 | 0.00043878 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 2076 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202002015 | 80 | 15 | 2 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2230.4 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 180 | 512 | 538 | 633 | 9 | 26 | 28 | 33 | 0.00050303 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 2788 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202201015 | 80 | 15 | 2 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1125 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035085 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1250 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202201515 | 80 | 15 | 2 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1827.2 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 147 | 398 | 407 | 510 | 8 | 21 | 21 | 26 | 0.00059228 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 2284 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202202015 | 80 | 15 | 2 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2453.6 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 545 | 571 | 670 | 10 | 28 | 29 | 35 | 0.00064012 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 3067 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202401015 | 80 | 15 | 2 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1226.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00037623 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1363 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202401515 | 80 | 15 | 2 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 1992.8 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 161 | 424 | 432 | 536 | 8 | 22 | 22 | 28 | 0.00062172 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 2491 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202402015 | 80 | 15 | 2 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2676.8 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 216 | 578 | 605 | 708 | 11 | 30 | 31 | 37 | 0.00079703 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 3346 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2202601015 | 80 | 15 | 2 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1329.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00055711 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 1477 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2202601515 | 60 | 15 | 2 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2159.2 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 174 | 407 | 412 | 482 | 9 | 21 | 21 | 25 | 0.00080948 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 2699 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2202602015 | 60 | 15 | 2 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2899.2 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 234 | 560 | 579 | 649 | 12 | 29 | 30 | 33 | 0.00097465 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 3624 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2202801015 | 60 | 15 | 2 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 1431.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00059192 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1591 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2202801515 | 80 | 15 | 2 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2324.8 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 476 | 481 | 588 | 10 | 25 | 25 | 30 | 0.0010269 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 2906 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2202802015 | 80 | 15 | 2 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3122.4 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 252 | 650 | 679 | 782 | 13 | 34 | 35 | 40 | 0.0011738 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 3903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235601015 | 80 | 15 | 2 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 494.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 40 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 549 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235601115 | 80 | 15 | 2 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 320.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 26 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.2723e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 471 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235601515 | 80 | 15 | 2 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 527.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4254e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 659 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235601615 | 80 | 15 | 2 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 537.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 6.6898e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 790 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235602015 | 80 | 15 | 2 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 780 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4.0779e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 975 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235602115 | 80 | 15 | 2 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 864.8 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1081 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235701015 | 80 | 15 | 2 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 1122.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016054 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1247 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235701115 | 80 | 15 | 2 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 374 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 30 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 550 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235701515 | 70 | 15 | 2 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 615.2 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 50 | 193 | 208 | 275 | 3 | 10 | 11 | 14 | 5.5819e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 769 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
235701615 | 70 | 15 | 2 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 626.96 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 51 | 273 | 294 | 389 | 3 | 14 | 15 | 20 | 0.00015302 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 922 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
235702015 | 70 | 15 | 2 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 910.4 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 73 | 269 | 288 | 345 | 4 | 14 | 15 | 18 | 7.4184e-05 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1138 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
235702115 | 70 | 15 | 2 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1008.8 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 81 | 383 | 411 | 544 | 4 | 20 | 21 | 28 | 0.00011089 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1261 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
235801015 | 80 | 15 | 2 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1309.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00017323 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 1455 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235801115 | 80 | 15 | 2 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 427.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 34 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.6478e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 628 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235801515 | 80 | 15 | 2 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 702.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 228 | 244 | 328 | 3 | 12 | 13 | 17 | 5.8533e-05 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 878 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235801615 | 80 | 15 | 2 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 716.72 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 58 | 322 | 345 | 463 | 3 | 17 | 18 | 24 | 0.00015844 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1054 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235802015 | 80 | 15 | 2 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1040 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 317 | 341 | 411 | 4 | 16 | 18 | 21 | 7.6905e-05 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1300 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235802115 | 80 | 15 | 2 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1152.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 93 | 451 | 484 | 649 | 5 | 23 | 25 | 33 | 0.00017841 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 1441 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235901015 | 80 | 15 | 2 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 1495.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002612 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1662 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
235901115 | 80 | 15 | 2 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 480.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 39 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 6.1655e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 707 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
235901515 | 80 | 15 | 2 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 790.4 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 64 | 238 | 254 | 341 | 3 | 12 | 13 | 18 | 6.1246e-05 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 988 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
235901615 | 80 | 15 | 2 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 805.8 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 344 | 366 | 489 | 3 | 18 | 19 | 25 | 0.00016387 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1185 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
235902015 | 80 | 15 | 2 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1170.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 332 | 356 | 430 | 5 | 17 | 18 | 22 | 0.00012248 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1463 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
235902115 | 80 | 15 | 2 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1296.8 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 105 | 465 | 497 | 669 | 5 | 24 | 26 | 35 | 0.0001864 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 1621 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351001015 | 80 | 15 | 2 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1683 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 136 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00037108 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1870 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351001115 | 80 | 15 | 2 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 533.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 6.6833e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 785 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351001515 | 80 | 15 | 2 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 878.4 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 248 | 264 | 354 | 4 | 13 | 14 | 18 | 0.00011055 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351001615 | 80 | 15 | 2 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 895.56 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 366 | 388 | 516 | 4 | 19 | 20 | 27 | 0.00029467 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1317 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351002015 | 80 | 15 | 2 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1300 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 348 | 372 | 448 | 5 | 18 | 19 | 23 | 0.00012648 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 1625 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351002115 | 80 | 15 | 2 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1440.8 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 116 | 480 | 511 | 689 | 6 | 25 | 26 | 36 | 0.00027506 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 1801 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351101015 | 80 | 15 | 2 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1870.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 151 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00050449 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 2078 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351101115 | 80 | 15 | 2 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 587.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 7.2011e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 864 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351101515 | 70 | 15 | 2 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 966.4 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 238 | 251 | 327 | 4 | 12 | 13 | 17 | 0.00011501 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1208 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2351101615 | 70 | 15 | 2 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 985.32 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 368 | 386 | 493 | 4 | 19 | 20 | 25 | 0.00030358 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 1449 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2351102015 | 70 | 15 | 2 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1430.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 115 | 335 | 355 | 419 | 6 | 17 | 18 | 22 | 0.00018516 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 1788 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2351102115 | 70 | 15 | 2 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1584.8 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 128 | 449 | 475 | 625 | 7 | 23 | 25 | 32 | 0.00038331 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 1981 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2351201015 | 80 | 15 | 2 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 2057.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00066299 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 2286 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351201115 | 80 | 15 | 2 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 640.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00016112 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 942 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351201515 | 80 | 15 | 2 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1054.4 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 272 | 288 | 380 | 4 | 14 | 15 | 20 | 0.00011946 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1318 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351201615 | 80 | 15 | 2 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1074.4 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 415 | 437 | 568 | 4 | 21 | 23 | 29 | 0.00031249 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 1580 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351202015 | 80 | 15 | 2 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1560 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 380 | 404 | 485 | 7 | 20 | 21 | 25 | 0.00025617 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 1950 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351202115 | 80 | 15 | 2 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1728.8 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 139 | 516 | 547 | 729 | 7 | 27 | 28 | 38 | 0.00039757 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 2161 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351401015 | 80 | 15 | 2 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 2244.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 181 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00073333 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 2494 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351401115 | 80 | 15 | 2 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 747.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00018204 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1099 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351401515 | 80 | 15 | 2 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1229.6 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 296 | 312 | 406 | 5 | 15 | 16 | 21 | 0.00019536 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 1537 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351401615 | 80 | 15 | 2 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1253.92 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 101 | 465 | 487 | 620 | 5 | 24 | 25 | 32 | 0.00050567 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 1844 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351402015 | 80 | 15 | 2 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1820 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 147 | 412 | 437 | 522 | 8 | 21 | 23 | 27 | 0.00034896 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 2275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351402115 | 80 | 15 | 2 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 1936.8 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 156 | 552 | 583 | 769 | 8 | 28 | 30 | 40 | 0.00054801 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 2421 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351601015 | 80 | 15 | 2 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 2618.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 211 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0011609 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 2909 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351601115 | 80 | 15 | 2 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 854.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00034093 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 1256 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351601515 | 80 | 15 | 2 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1405.6 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 113 | 319 | 334 | 432 | 6 | 16 | 17 | 22 | 0.00029344 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 1757 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2351601615 | 80 | 15 | 2 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1432.76 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 116 | 513 | 534 | 672 | 6 | 26 | 28 | 35 | 0.0007524 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 2107 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351602015 | 80 | 15 | 2 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2080 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 445 | 471 | 559 | 9 | 23 | 24 | 29 | 0.00045905 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 2600 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2351602115 | 80 | 15 | 2 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2305.6 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 186 | 587 | 616 | 809 | 10 | 30 | 32 | 42 | 0.0008878 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 2882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351801015 | 80 | 15 | 2 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 2992.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 241 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0014777 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 3325 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2351801115 | 80 | 15 | 2 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 960.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00037539 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 1413 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2351801515 | 60 | 15 | 2 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1580.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 302 | 312 | 378 | 7 | 16 | 16 | 20 | 0.00041539 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 1976 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2351801615 | 60 | 15 | 2 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1612.28 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 130 | 520 | 534 | 627 | 7 | 27 | 28 | 32 | 0.0010561 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 2371 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2351802015 | 60 | 15 | 2 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2340 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 189 | 423 | 441 | 501 | 10 | 22 | 23 | 26 | 0.00058739 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 2925 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2351802115 | 60 | 15 | 2 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2593.6 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 209 | 530 | 549 | 680 | 11 | 27 | 28 | 35 | 0.0011242 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 3242 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352001015 | 80 | 15 | 2 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 3366 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 271 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0021103 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 3740 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352001115 | 80 | 15 | 2 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1067.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00040985 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 1570 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352001515 | 80 | 15 | 2 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1756.8 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 372 | 383 | 484 | 7 | 19 | 20 | 25 | 0.00043878 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 2196 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352001615 | 80 | 15 | 2 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 1791.12 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 144 | 618 | 634 | 777 | 7 | 32 | 33 | 40 | 0.0011028 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 2634 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352002015 | 80 | 15 | 2 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2600 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 210 | 512 | 538 | 633 | 11 | 26 | 28 | 33 | 0.00073489 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 3250 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352002115 | 80 | 15 | 2 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 2881.6 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 232 | 668 | 691 | 890 | 12 | 34 | 36 | 46 | 0.0013955 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 3602 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352201015 | 80 | 15 | 2 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3740.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 302 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0.0028833 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 4156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352201115 | 80 | 15 | 2 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1174.36 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0006624 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 1727 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352201515 | 80 | 15 | 2 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1932.8 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 398 | 407 | 510 | 8 | 21 | 21 | 26 | 0.00059228 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 2416 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352201615 | 80 | 15 | 2 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 1969.96 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 159 | 670 | 683 | 829 | 8 | 35 | 35 | 43 | 0.0014788 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 2897 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352202015 | 80 | 15 | 2 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2860 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 231 | 545 | 571 | 670 | 12 | 28 | 29 | 35 | 0.00090247 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 3575 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352202115 | 80 | 15 | 2 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3169.6 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 256 | 708 | 726 | 930 | 13 | 37 | 37 | 48 | 0.0017033 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 3962 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352401015 | 80 | 15 | 2 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 4114.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 332 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0.0034316 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 4572 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352401115 | 80 | 15 | 2 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 1281.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00071315 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 1884 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352401515 | 80 | 15 | 2 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2108 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 170 | 424 | 432 | 536 | 9 | 22 | 22 | 28 | 0.00077342 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 2635 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352401615 | 80 | 15 | 2 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2149.48 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 173 | 723 | 734 | 881 | 9 | 37 | 38 | 45 | 0.0019192 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 3161 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352402015 | 80 | 15 | 2 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3120 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 252 | 578 | 605 | 708 | 13 | 30 | 31 | 37 | 0.001091 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 3900 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352402115 | 80 | 15 | 2 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3457.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 279 | 748 | 764 | 970 | 14 | 39 | 39 | 50 | 0.0020494 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 4322 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352601015 | 80 | 15 | 2 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 4488.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 362 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0.0044567 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 4987 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352601115 | 80 | 15 | 2 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 1387.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0010576 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 2041 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2352601515 | 60 | 15 | 2 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2284 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 184 | 407 | 412 | 482 | 9 | 21 | 21 | 25 | 0.00080948 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 2855 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2352601615 | 60 | 15 | 2 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2328.32 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 188 | 729 | 736 | 836 | 10 | 38 | 38 | 43 | 0.0024271 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 3424 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352602015 | 60 | 15 | 2 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3404 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 275 | 560 | 579 | 649 | 14 | 29 | 30 | 33 | 0.0013013 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 4255 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2352602115 | 60 | 15 | 2 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3746.4 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 302 | 691 | 701 | 841 | 16 | 36 | 36 | 43 | 0.0027446 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 4683 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352801015 | 60 | 15 | 2 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 4862.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 392 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0.0051719 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 5403 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2352801115 | 60 | 15 | 2 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 1494.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 121 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0011273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 2198 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2352801515 | 80 | 15 | 2 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2459.2 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 476 | 481 | 588 | 10 | 25 | 25 | 30 | 0.0010269 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 3074 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2352801615 | 80 | 15 | 2 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 2507.84 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 202 | 827 | 834 | 986 | 10 | 43 | 43 | 51 | 0.0025136 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 3688 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2352802015 | 80 | 15 | 2 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3640 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 294 | 650 | 679 | 782 | 15 | 34 | 35 | 40 | 0.0015342 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 4550 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2352802115 | 80 | 15 | 2 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4034.4 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 325 | 829 | 838 | 1050 | 17 | 43 | 43 | 54 | 0.0032024 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 5043 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250601015 | 80 | 15 | 2 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 5236.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 422 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0.0024983 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 5818 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250601115 | 80 | 15 | 2 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 533.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250601515 | 80 | 15 | 2 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 736 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 920 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250601615 | 80 | 15 | 2 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 796.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 64 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1171 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250602015 | 80 | 15 | 2 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1017.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1272 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250602115 | 80 | 15 | 2 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1230.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1538 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250701015 | 80 | 15 | 2 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 607.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 675 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250701115 | 80 | 15 | 2 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 622.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 50 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 916 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250701515 | 70 | 15 | 2 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 858.4 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 69 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1073 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
250701615 | 70 | 15 | 2 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 928.88 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 75 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1366 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
250702015 | 70 | 15 | 2 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1187.2 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 269 | 288 | 345 | 5 | 14 | 15 | 18 | 0.00011449 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
250702115 | 70 | 15 | 2 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1436 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 116 | 383 | 411 | 544 | 6 | 20 | 21 | 28 | 0.00024224 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1795 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
250801015 | 80 | 15 | 2 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 693.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 771 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250801115 | 80 | 15 | 2 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 711.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1047 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250801515 | 80 | 15 | 2 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 228 | 244 | 328 | 4 | 12 | 13 | 17 | 0.00010164 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250801615 | 80 | 15 | 2 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1061.48 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 322 | 345 | 463 | 4 | 17 | 18 | 24 | 0.00027685 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1561 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250802015 | 80 | 15 | 2 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1356.8 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 317 | 341 | 411 | 6 | 16 | 18 | 21 | 0.00016875 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250802115 | 80 | 15 | 2 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1640.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 132 | 451 | 484 | 649 | 7 | 23 | 25 | 33 | 0.00034051 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 2051 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250901015 | 80 | 15 | 2 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 781.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 868 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
250901115 | 80 | 15 | 2 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 801.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00012974 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1178 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
250901515 | 80 | 15 | 2 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1104 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 238 | 254 | 341 | 5 | 12 | 13 | 18 | 0.00016264 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1380 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
250901615 | 80 | 15 | 2 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1194.08 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 344 | 366 | 489 | 5 | 18 | 19 | 25 | 0.00044021 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1756 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
250902015 | 80 | 15 | 2 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1526.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 332 | 356 | 430 | 6 | 17 | 18 | 22 | 0.00017422 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1908 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
250902115 | 80 | 15 | 2 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1846.4 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 149 | 465 | 497 | 669 | 8 | 24 | 26 | 35 | 0.00045824 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 2308 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501001015 | 80 | 15 | 2 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 867.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 964 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501001115 | 80 | 15 | 2 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 890.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1309 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501001515 | 80 | 15 | 2 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 248 | 264 | 354 | 5 | 13 | 14 | 18 | 0.00016918 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501001615 | 80 | 15 | 2 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1326.68 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 107 | 366 | 388 | 516 | 6 | 19 | 20 | 27 | 0.00064483 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1951 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501002015 | 80 | 15 | 2 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1696 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 137 | 348 | 372 | 448 | 7 | 18 | 19 | 23 | 0.00024191 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501002115 | 80 | 15 | 2 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2051.2 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 165 | 480 | 511 | 689 | 9 | 25 | 26 | 36 | 0.00059642 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 2564 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501101015 | 80 | 15 | 2 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 954 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1060 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501101115 | 80 | 15 | 2 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 979.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1440 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501101515 | 70 | 15 | 2 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1348.8 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 238 | 251 | 327 | 6 | 12 | 13 | 17 | 0.00024862 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1686 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2501101615 | 70 | 15 | 2 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1459.28 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 368 | 386 | 493 | 6 | 19 | 20 | 25 | 0.00066276 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 2146 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2501102015 | 70 | 15 | 2 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1865.6 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 150 | 335 | 355 | 419 | 8 | 17 | 18 | 22 | 0.00032203 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2332 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2501102115 | 70 | 15 | 2 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2256 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 182 | 449 | 475 | 625 | 9 | 23 | 25 | 32 | 0.00061841 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2501201015 | 80 | 15 | 2 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1041.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1157 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501201115 | 80 | 15 | 2 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1068.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.000272 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501201515 | 80 | 15 | 2 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1472 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 272 | 288 | 380 | 6 | 14 | 15 | 20 | 0.00025759 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501201615 | 80 | 15 | 2 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1591.88 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 128 | 415 | 437 | 568 | 7 | 21 | 23 | 29 | 0.00091576 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 2341 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501202015 | 80 | 15 | 2 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 164 | 380 | 404 | 485 | 8 | 20 | 21 | 25 | 0.00033101 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501202115 | 80 | 15 | 2 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2461.6 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 199 | 516 | 547 | 729 | 10 | 27 | 28 | 38 | 0.00078234 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 3077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501401015 | 80 | 15 | 2 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1215 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00024935 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1350 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501401115 | 80 | 15 | 2 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1246.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00045941 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1833 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501401515 | 80 | 15 | 2 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1716.8 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 138 | 296 | 312 | 406 | 7 | 15 | 16 | 21 | 0.00036862 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2146 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501401615 | 80 | 15 | 2 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1857.08 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 150 | 465 | 487 | 620 | 8 | 24 | 25 | 32 | 0.0012433 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2731 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501402015 | 80 | 15 | 2 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 191 | 412 | 437 | 522 | 10 | 21 | 23 | 27 | 0.00053465 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 2968 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501402115 | 80 | 15 | 2 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2872 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 232 | 552 | 583 | 769 | 12 | 28 | 30 | 40 | 0.0011789 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 3590 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501601015 | 80 | 15 | 2 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1387.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1542 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501601115 | 80 | 15 | 2 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1423.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00070949 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2094 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501601515 | 80 | 15 | 2 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1962.4 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 158 | 319 | 334 | 432 | 8 | 16 | 17 | 22 | 0.00050396 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2453 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2501601615 | 80 | 15 | 2 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2122.96 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 171 | 513 | 534 | 672 | 9 | 26 | 28 | 35 | 0.0016307 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 3122 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501602015 | 80 | 15 | 2 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 445 | 471 | 559 | 11 | 23 | 24 | 29 | 0.00067276 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2501602115 | 80 | 15 | 2 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3281.6 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 265 | 587 | 616 | 809 | 14 | 30 | 32 | 42 | 0.0016729 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 4102 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501801015 | 80 | 15 | 2 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1561.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1735 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2501801115 | 80 | 15 | 2 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1602.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 129 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.001029 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2356 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2501801515 | 60 | 15 | 2 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2207.2 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 178 | 302 | 312 | 378 | 9 | 16 | 16 | 20 | 0.00066522 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 2759 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2501801615 | 60 | 15 | 2 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.16 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 193 | 520 | 534 | 627 | 10 | 27 | 28 | 32 | 0.0020811 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 3512 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2501802015 | 60 | 15 | 2 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 423 | 441 | 501 | 13 | 22 | 23 | 26 | 0.00096672 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2501802115 | 60 | 15 | 2 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3692 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 298 | 530 | 549 | 680 | 15 | 27 | 28 | 35 | 0.0020114 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 4615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502001015 | 80 | 15 | 2 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1735.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00059851 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1928 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502001115 | 80 | 15 | 2 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1780.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00112 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2618 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502001515 | 80 | 15 | 2 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2452.8 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 372 | 383 | 484 | 10 | 19 | 20 | 25 | 0.00085394 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502001615 | 80 | 15 | 2 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2653.36 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 214 | 618 | 634 | 777 | 11 | 32 | 33 | 40 | 0.0025976 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 3902 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502002015 | 80 | 15 | 2 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3392 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 274 | 512 | 538 | 633 | 14 | 26 | 28 | 33 | 0.0011601 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4240 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502002115 | 80 | 15 | 2 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4102.4 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 331 | 668 | 691 | 890 | 17 | 34 | 36 | 46 | 0.0026765 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 5128 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502201015 | 80 | 15 | 2 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1908.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00081987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2121 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502201115 | 80 | 15 | 2 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1958.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0015391 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 2880 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502201515 | 80 | 15 | 2 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2698.4 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 218 | 398 | 407 | 510 | 11 | 21 | 21 | 26 | 0.0010716 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3373 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502201615 | 80 | 15 | 2 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2918.56 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 235 | 670 | 683 | 829 | 12 | 35 | 35 | 43 | 0.0031831 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 4292 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502202015 | 80 | 15 | 2 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 301 | 545 | 571 | 670 | 16 | 28 | 29 | 35 | 0.0015537 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 4664 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502202115 | 80 | 15 | 2 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4512.8 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 364 | 708 | 726 | 930 | 19 | 37 | 37 | 48 | 0.0034561 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 5641 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502401015 | 80 | 15 | 2 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2082.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001085 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2314 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502401115 | 80 | 15 | 2 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2136.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0020427 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502401515 | 80 | 15 | 2 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2943.2 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 237 | 424 | 432 | 536 | 12 | 22 | 22 | 28 | 0.0013198 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 3679 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502401615 | 80 | 15 | 2 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3183.76 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 257 | 723 | 734 | 881 | 13 | 37 | 38 | 45 | 0.0038405 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 4682 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502402015 | 80 | 15 | 2 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 328 | 578 | 605 | 708 | 17 | 30 | 31 | 37 | 0.0018082 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 5088 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502402115 | 80 | 15 | 2 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4923.2 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 397 | 748 | 764 | 970 | 20 | 39 | 39 | 50 | 0.0039778 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 6154 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502601015 | 80 | 15 | 2 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2255.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011554 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502601115 | 80 | 15 | 2 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2314.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 187 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0026367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3403 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2502601515 | 60 | 15 | 2 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3188.8 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 257 | 407 | 412 | 482 | 13 | 21 | 21 | 25 | 0.0015997 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 3986 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2502601615 | 60 | 15 | 2 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3449.64 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 278 | 729 | 736 | 836 | 14 | 38 | 38 | 43 | 0.0045725 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 5073 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502602015 | 60 | 15 | 2 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 356 | 560 | 579 | 649 | 18 | 29 | 30 | 33 | 0.0020866 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 5512 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2502602115 | 60 | 15 | 2 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5332.8 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 430 | 691 | 701 | 841 | 22 | 36 | 36 | 43 | 0.004956 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 6666 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502801015 | 60 | 15 | 2 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2429.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 196 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014814 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2699 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2502801115 | 60 | 15 | 2 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2492.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 201 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0028056 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3665 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2502801515 | 80 | 15 | 2 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3433.6 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 277 | 476 | 481 | 588 | 14 | 25 | 25 | 30 | 0.001913 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4292 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2502801615 | 80 | 15 | 2 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3714.84 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 300 | 827 | 834 | 986 | 15 | 43 | 43 | 51 | 0.005382 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 5463 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2502802015 | 80 | 15 | 2 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 383 | 650 | 679 | 782 | 20 | 34 | 35 | 40 | 0.0026313 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 5936 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2502802115 | 80 | 15 | 2 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5743.2 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 463 | 829 | 838 | 1050 | 24 | 43 | 43 | 54 | 0.0060645 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 7179 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265601015 | 80 | 15 | 2 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 605.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 673 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265601115 | 80 | 15 | 2 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 605.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 890 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265601515 | 80 | 15 | 2 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1029 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265601615 | 80 | 15 | 2 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 908.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1336 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265602015 | 80 | 15 | 2 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1148 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1435 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265602115 | 80 | 15 | 2 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1442.4 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1803 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265701015 | 80 | 15 | 2 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 706.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265701115 | 80 | 15 | 2 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 705.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1038 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265701515 | 70 | 15 | 2 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 960.8 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1201 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
265701615 | 70 | 15 | 2 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1060.12 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 85 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 245 | 263 | 349 | 0.95 | 0.95 | 0.95 | 194.8253 | 209.139 | 277.5266 | 42 | 45 | 60 | 0.026932 | 0.030855 | 0.054417 | 1.4 | 6 | 6.7 | 9 |  | 1559 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.8253 | 209.139 | 277.5266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
265702015 | 70 | 15 | 2 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1339.2 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 108 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1674 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
265702115 | 70 | 15 | 2 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1683.2 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 136 | 383 | 411 | 544 | 7 | 20 | 21 | 28 | 0.00032624 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 268 | 287 | 380 | 0.85 | 0.85 | 0.85 | 218.3182 | 233.7959 | 309.5556 | 47 | 50 | 67 | 0.013237 | 0.01494 | 0.026498 | 1.9 | 6 | 6.7 | 9 |  | 2104 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 218.3182 | 233.7959 | 309.5556 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
265801015 | 80 | 15 | 2 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 807.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 897 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265801115 | 80 | 15 | 2 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 806.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1186 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265801515 | 80 | 15 | 2 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1097.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1372 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265801615 | 80 | 15 | 2 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1211.76 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 322 | 345 | 463 | 5 | 17 | 18 | 24 | 0.00042712 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 289 | 310 | 416 | 0.95 | 0.95 | 0.95 | 229.8143 | 246.5136 | 330.8054 | 49 | 53 | 71 | 0.037165 | 0.043371 | 0.077133 | 1.6 | 6 | 6.7 | 9 |  | 1782 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 229.8143 | 246.5136 | 330.8054 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265802015 | 80 | 15 | 2 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1530.4 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 317 | 341 | 411 | 6 | 16 | 18 | 21 | 0.00016875 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1913 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265802115 | 80 | 15 | 2 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1923.2 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 155 | 451 | 484 | 649 | 8 | 23 | 25 | 33 | 0.00044029 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315 | 338 | 454 | 0.85 | 0.85 | 0.85 | 256.6053 | 275.3416 | 369.8375 | 55 | 59 | 80 | 0.0185 | 0.021216 | 0.038459 | 2.1 | 6 | 6.7 | 9 |  | 2404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.6053 | 275.3416 | 369.8375 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265901015 | 80 | 15 | 2 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 908.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1009 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
265901115 | 80 | 15 | 2 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 907.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1335 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
265901515 | 80 | 15 | 2 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1235.2 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 100 | 238 | 254 | 341 | 5 | 12 | 13 | 18 | 0.00016264 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
265901615 | 80 | 15 | 2 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1362.72 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 110 | 344 | 366 | 489 | 6 | 18 | 19 | 25 | 0.00062691 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 290 | 310 | 423 | 0.95 | 0.95 | 0.95 | 230.6095 | 246.5136 | 336.3718 | 50 | 53 | 72 | 0.039366 | 0.044137 | 0.080588 | 1.8 | 6 | 6.7 | 9 |  | 2004 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 230.6095 | 246.5136 | 336.3718 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
265902015 | 80 | 15 | 2 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1721.6 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 139 | 332 | 356 | 430 | 7 | 17 | 18 | 22 | 0.00023478 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2152 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
265902115 | 80 | 15 | 2 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2164 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 175 | 465 | 497 | 669 | 9 | 24 | 26 | 35 | 0.00057443 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 317 | 339 | 462 | 0.85 | 0.85 | 0.85 | 258.2346 | 276.1562 | 376.3545 | 56 | 59 | 81 | 0.019674 | 0.021777 | 0.040371 | 2.4 | 6 | 6.7 | 9 |  | 2705 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 258.2346 | 276.1562 | 376.3545 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651001015 | 80 | 15 | 2 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1008.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1121 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651001115 | 80 | 15 | 2 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1008.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 81 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1483 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651001515 | 80 | 15 | 2 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1372 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 248 | 264 | 354 | 6 | 13 | 14 | 18 | 0.00023966 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1715 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651001615 | 80 | 15 | 2 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1514.36 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 366 | 388 | 516 | 6 | 19 | 20 | 27 | 0.00064483 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 291 | 312 | 430 | 0.95 | 0.95 | 0.95 | 231.4047 | 248.104 | 341.9382 | 50 | 53 | 74 | 0.040059 | 0.044904 | 0.086412 | 2 | 6 | 6.7 | 9 |  | 2227 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 231.4047 | 248.104 | 341.9382 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651002015 | 80 | 15 | 2 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1912.8 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 348 | 372 | 448 | 8 | 18 | 19 | 23 | 0.00031305 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2391 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651002115 | 80 | 15 | 2 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2404 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 194 | 480 | 511 | 689 | 10 | 25 | 26 | 36 | 0.00072961 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 319 | 341 | 471 | 0.85 | 0.85 | 0.85 | 259.8638 | 277.7854 | 383.686 | 56 | 60 | 82 | 0.020186 | 0.023077 | 0.042336 | 2.7 | 6 | 6.7 | 9 |  | 3005 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 259.8638 | 277.7854 | 383.686 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651101015 | 80 | 15 | 2 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1109.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1233 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651101115 | 80 | 15 | 2 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1109.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1631 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651101515 | 70 | 15 | 2 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1509.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 122 | 238 | 251 | 327 | 6 | 12 | 13 | 17 | 0.00024862 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1887 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2651101615 | 70 | 15 | 2 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1666 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 134 | 368 | 386 | 493 | 7 | 19 | 20 | 25 | 0.00089237 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 255 | 273 | 376 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.091 | 298.9972 | 44 | 47 | 64 | 0.031743 | 0.03611 | 0.066054 | 2.2 | 6 | 6.7 | 9 |  | 2450 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.091 | 298.9972 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2651102015 | 70 | 15 | 2 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2104 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 170 | 335 | 355 | 419 | 9 | 17 | 18 | 22 | 0.00040407 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2630 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2651102115 | 70 | 15 | 2 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2644.8 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 213 | 449 | 475 | 625 | 11 | 23 | 25 | 32 | 0.00090675 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 281 | 301 | 415 | 0.85 | 0.85 | 0.85 | 228.9082 | 245.2006 | 338.0673 | 49 | 53 | 73 | 0.015989 | 0.018608 | 0.034581 | 2.9 | 6 | 6.7 | 9 |  | 3306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.9082 | 245.2006 | 338.0673 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2651201015 | 80 | 15 | 2 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1210.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1345 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651201115 | 80 | 15 | 2 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1210.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651201515 | 80 | 15 | 2 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1646.4 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 133 | 272 | 288 | 380 | 7 | 14 | 15 | 20 | 0.00034524 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2058 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651201615 | 80 | 15 | 2 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1816.96 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 147 | 415 | 437 | 568 | 8 | 21 | 23 | 29 | 0.0011844 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 298 | 319 | 444 | 0.95 | 0.95 | 0.95 | 236.9712 | 253.6705 | 353.0711 | 51 | 55 | 76 | 0.043079 | 0.04992 | 0.093911 | 2.4 | 6 | 6.7 | 9 |  | 2672 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.9712 | 253.6705 | 353.0711 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651202015 | 80 | 15 | 2 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2295.2 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 185 | 380 | 404 | 485 | 10 | 20 | 21 | 25 | 0.00050829 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2869 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651202115 | 80 | 15 | 2 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2884.8 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 233 | 516 | 547 | 729 | 12 | 27 | 28 | 38 | 0.0011067 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 327 | 351 | 488 | 0.85 | 0.85 | 0.85 | 266.3808 | 285.9316 | 397.5346 | 57 | 61 | 85 | 0.021947 | 0.025016 | 0.047501 | 3.2 | 6 | 6.7 | 9 |  | 3606 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3808 | 285.9316 | 397.5346 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651401015 | 80 | 15 | 2 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1412.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1569 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651401115 | 80 | 15 | 2 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1411.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00063987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2076 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651401515 | 80 | 15 | 2 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1920.8 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 155 | 296 | 312 | 406 | 8 | 15 | 16 | 21 | 0.00047453 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2401 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651401615 | 80 | 15 | 2 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2120.24 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 171 | 465 | 487 | 620 | 9 | 24 | 25 | 32 | 0.0015586 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 304 | 326 | 457 | 0.95 | 0.95 | 0.95 | 241.7424 | 259.2369 | 363.4088 | 52 | 56 | 78 | 0.046227 | 0.053393 | 0.10179 | 2.8 | 6 | 6.7 | 9 |  | 3118 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.7424 | 259.2369 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651402015 | 80 | 15 | 2 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2677.6 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 216 | 412 | 437 | 522 | 11 | 21 | 23 | 27 | 0.00064169 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3347 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651402115 | 80 | 15 | 2 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3365.6 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 271 | 552 | 583 | 769 | 14 | 28 | 30 | 40 | 0.0015788 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 336 | 360 | 505 | 0.85 | 0.85 | 0.85 | 273.7123 | 293.2632 | 411.3831 | 59 | 63 | 88 | 0.024578 | 0.027878 | 0.05303 | 3.7 | 6 | 6.7 | 9 |  | 4207 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 273.7123 | 293.2632 | 411.3831 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651601015 | 80 | 15 | 2 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1614.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00050754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1794 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651601115 | 80 | 15 | 2 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1613.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 130 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00093804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2373 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651601515 | 80 | 15 | 2 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2195.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 177 | 319 | 334 | 432 | 9 | 16 | 17 | 22 | 0.00062916 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2651601615 | 80 | 15 | 2 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2422.84 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 195 | 513 | 534 | 672 | 10 | 26 | 28 | 35 | 0.0019946 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 310 | 331 | 471 | 0.95 | 0.95 | 0.95 | 246.5136 | 263.2129 | 374.5417 | 53 | 57 | 81 | 0.049504 | 0.057002 | 0.11275 | 3.2 | 6 | 6.7 | 9 |  | 3563 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 246.5136 | 263.2129 | 374.5417 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651602015 | 80 | 15 | 2 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3060.8 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 247 | 445 | 471 | 559 | 13 | 23 | 24 | 29 | 0.0009253 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3826 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2651602115 | 80 | 15 | 2 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3846.4 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 310 | 587 | 616 | 809 | 16 | 30 | 32 | 42 | 0.0021524 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 343 | 366 | 522 | 0.85 | 0.85 | 0.85 | 279.4147 | 298.1509 | 425.2317 | 60 | 64 | 91 | 0.026537 | 0.030024 | 0.058931 | 4.3 | 6 | 6.7 | 9 |  | 4808 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 279.4147 | 298.1509 | 425.2317 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651801015 | 80 | 15 | 2 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1816.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00070519 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 2018 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2651801115 | 80 | 15 | 2 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1814.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0013098 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2669 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2651801515 | 60 | 15 | 2 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2469.6 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 199 | 302 | 312 | 378 | 10 | 16 | 16 | 20 | 0.00081069 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2651801615 | 60 | 15 | 2 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2726.12 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 220 | 520 | 534 | 627 | 11 | 27 | 28 | 32 | 0.0024957 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 240 | 256 | 365 | 0.95 | 0.95 | 0.95 | 190.8492 | 203.5725 | 290.2499 | 41 | 44 | 62 | 0.031101 | 0.035637 | 0.069107 | 3.6 | 6 | 6.7 | 9 |  | 4009 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 203.5725 | 290.2499 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2651802015 | 60 | 15 | 2 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3443.2 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 278 | 423 | 441 | 501 | 14 | 22 | 23 | 26 | 0.0011131 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4304 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2651802115 | 60 | 15 | 2 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4327.2 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 349 | 530 | 549 | 680 | 18 | 27 | 28 | 35 | 0.002834 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 269 | 287 | 409 | 0.85 | 0.85 | 0.85 | 219.1328 | 233.7959 | 333.1796 | 47 | 50 | 72 | 0.017403 | 0.019575 | 0.039195 | 4.8 | 6 | 6.7 | 9 |  | 5409 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.1328 | 233.7959 | 333.1796 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652001015 | 80 | 15 | 2 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 2017.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00076253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2242 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652001115 | 80 | 15 | 2 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 2016.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0014244 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2966 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652001515 | 80 | 15 | 2 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2744 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 221 | 372 | 383 | 484 | 11 | 19 | 20 | 25 | 0.0010207 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3430 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652001615 | 80 | 15 | 2 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3028.72 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 244 | 618 | 634 | 777 | 13 | 32 | 33 | 40 | 0.0035686 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 328 | 346 | 499 | 0.95 | 0.95 | 0.95 | 260.8273 | 275.141 | 396.8074 | 56 | 59 | 85 | 0.058451 | 0.064634 | 0.13074 | 4 | 6 | 6.7 | 9 |  | 4454 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 260.8273 | 275.141 | 396.8074 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652002015 | 80 | 15 | 2 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3825.6 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 309 | 512 | 538 | 633 | 16 | 26 | 28 | 33 | 0.0014945 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4782 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652002115 | 80 | 15 | 2 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4808 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 388 | 668 | 691 | 890 | 20 | 34 | 36 | 46 | 0.0036299 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 365 | 385 | 556 | 0.85 | 0.85 | 0.85 | 297.3363 | 313.6287 | 452.9287 | 64 | 67 | 97 | 0.032602 | 0.035564 | 0.071889 | 5.3 | 6 | 6.7 | 9 |  | 6010 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 297.3363 | 313.6287 | 452.9287 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652201015 | 80 | 15 | 2 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2219.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0010147 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2466 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652201115 | 80 | 15 | 2 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2218.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001902 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3263 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652201515 | 80 | 15 | 2 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3018.4 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 243 | 398 | 407 | 510 | 13 | 21 | 21 | 26 | 0.0014638 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3773 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652201615 | 80 | 15 | 2 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3331.32 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 269 | 670 | 683 | 829 | 14 | 35 | 35 | 43 | 0.0042635 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 337 | 351 | 513 | 0.95 | 0.95 | 0.95 | 267.9842 | 279.117 | 407.9403 | 58 | 60 | 88 | 0.064331 | 0.06866 | 0.14348 | 4.4 | 6 | 6.7 | 9 |  | 4899 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267.9842 | 279.117 | 407.9403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652202015 | 80 | 15 | 2 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4208 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 339 | 545 | 571 | 670 | 17 | 28 | 29 | 35 | 0.0017425 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 5260 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652202115 | 80 | 15 | 2 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5288.8 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 427 | 708 | 726 | 930 | 22 | 37 | 37 | 48 | 0.004546 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 377 | 392 | 573 | 0.85 | 0.85 | 0.85 | 307.1118 | 319.3311 | 466.7773 | 66 | 69 | 100 | 0.035922 | 0.039074 | 0.078965 | 5.9 | 6 | 6.7 | 9 |  | 6611 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 307.1118 | 319.3311 | 466.7773 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652401015 | 80 | 15 | 2 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2421 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0013125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2690 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652401115 | 80 | 15 | 2 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2420.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 195 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0024679 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3559 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652401515 | 80 | 15 | 2 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3292.8 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 266 | 424 | 432 | 536 | 14 | 22 | 22 | 28 | 0.0017585 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4116 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652401615 | 80 | 15 | 2 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3634.6 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 293 | 723 | 734 | 881 | 15 | 37 | 38 | 45 | 0.005034 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 347 | 359 | 527 | 0.95 | 0.95 | 0.95 | 275.9362 | 285.4787 | 419.0731 | 59 | 61 | 90 | 0.068323 | 0.07283 | 0.15366 | 4.8 | 6 | 6.7 | 9 |  | 5345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 275.9362 | 285.4787 | 419.0731 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652402015 | 80 | 15 | 2 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4590.4 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 370 | 578 | 605 | 708 | 19 | 30 | 31 | 37 | 0.0022305 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 5738 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652402115 | 80 | 15 | 2 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5769.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 465 | 748 | 764 | 970 | 24 | 39 | 39 | 50 | 0.0055883 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 388 | 402 | 590 | 0.85 | 0.85 | 0.85 | 316.0726 | 327.4773 | 480.6258 | 68 | 70 | 103 | 0.03944 | 0.041657 | 0.08645 | 6.4 | 6 | 6.7 | 9 |  | 7212 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 316.0726 | 327.4773 | 480.6258 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652601015 | 80 | 15 | 2 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2623.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.001659 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2915 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652601115 | 80 | 15 | 2 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2622.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 211 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0031278 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3856 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2652601515 | 60 | 15 | 2 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3567.2 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 288 | 407 | 412 | 482 | 15 | 21 | 21 | 25 | 0.0020868 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4459 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
2652601615 | 60 | 15 | 2 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3937.2 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 318 | 729 | 736 | 836 | 16 | 38 | 38 | 43 | 0.0058826 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277 | 287 | 420 | 0.95 | 0.95 | 0.95 | 220.2718 | 228.2239 | 333.9862 | 47 | 49 | 72 | 0.045459 | 0.04922 | 0.10269 | 5.2 | 6 | 6.7 | 9 |  | 5790 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 220.2718 | 228.2239 | 333.9862 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652602015 | 60 | 15 | 2 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4973.6 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 401 | 560 | 579 | 649 | 21 | 29 | 30 | 33 | 0.0027893 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 6217 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
2652602115 | 60 | 15 | 2 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6250.4 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 504 | 691 | 701 | 841 | 26 | 36 | 36 | 43 | 0.0067624 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 314 | 326 | 478 | 0.85 | 0.85 | 0.85 | 255.7907 | 265.5661 | 389.3884 | 55 | 57 | 84 | 0.027436 | 0.029338 | 0.060837 | 6.9 | 6 | 6.7 | 9 |  | 7813 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 255.7907 | 265.5661 | 389.3884 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652801015 | 60 | 15 | 2 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2825.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002057 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3139 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
2652801115 | 60 | 15 | 2 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2823.36 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0038875 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 4152 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
2652801515 | 80 | 15 | 2 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3841.6 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 310 | 476 | 481 | 588 | 16 | 25 | 25 | 30 | 0.0024501 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4802 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2652801615 | 80 | 15 | 2 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4240.48 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 342 | 827 | 834 | 986 | 18 | 43 | 43 | 51 | 0.0075868 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 373 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 296.6115 | 441.3389 | 62 | 64 | 95 | 0.079154 | 0.084096 | 0.17888 | 5.6 | 6 | 6.7 | 9 |  | 6236 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 296.6115 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2652802015 | 80 | 15 | 2 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5356 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 432 | 650 | 679 | 782 | 22 | 34 | 35 | 40 | 0.0031473 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 6695 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2652802115 | 80 | 15 | 2 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6731.2 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 543 | 829 | 838 | 1050 | 28 | 43 | 43 | 54 | 0.0080738 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 411 | 420 | 624 | 0.85 | 0.85 | 0.85 | 334.8088 | 342.1404 | 508.3229 | 72 | 74 | 109 | 0.047089 | 0.049573 | 0.10269 | 7.5 | 6 | 6.7 | 9 |  | 8414 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 334.8088 | 342.1404 | 508.3229 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295601015 | 80 | 15 | 2 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 754.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 838 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295601115 | 80 | 15 | 2 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 717.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1055 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295601515 | 80 | 15 | 2 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 968 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1210 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295601615 | 80 | 15 | 2 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1093.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040093 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1608 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295602015 | 80 | 15 | 2 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1364.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 110 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1706 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295602115 | 80 | 15 | 2 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1832 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2290 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295701015 | 80 | 15 | 2 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 879.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 977 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295701115 | 80 | 15 | 2 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 837.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1231 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295701515 | 70 | 15 | 2 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1128.8 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 193 | 208 | 275 | 5 | 10 | 11 | 14 | 0.00014954 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1411 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
295701615 | 70 | 15 | 2 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1275.68 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 103 | 273 | 294 | 389 | 5 | 14 | 15 | 20 | 0.00041403 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 206 | 221 | 292 | 0.95 | 0.95 | 0.95 | 163.8123 | 175.7404 | 232.1999 | 35 | 38 | 50 | 0.018805 | 0.022112 | 0.037979 | 1.4 | 6 | 6.7 | 9 |  | 1876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.8123 | 175.7404 | 232.1999 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
295702015 | 70 | 15 | 2 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1592.8 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 128 | 269 | 288 | 345 | 7 | 14 | 15 | 18 | 0.00022051 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1991 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
295702115 | 70 | 15 | 2 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 2136.8 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 172 | 383 | 411 | 544 | 9 | 20 | 21 | 28 | 0.00053044 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 224 | 241 | 319 | 0.85 | 0.85 | 0.85 | 182.4749 | 196.3234 | 259.8638 | 39 | 42 | 56 | 0.0091917 | 0.010624 | 0.01865 | 1.9 | 6 | 6.7 | 9 |  | 2671 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 182.4749 | 196.3234 | 259.8638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
295801015 | 80 | 15 | 2 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1005.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 1117 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295801115 | 80 | 15 | 2 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 956.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1406 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295801515 | 80 | 15 | 2 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1290.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 104 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295801615 | 80 | 15 | 2 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1457.92 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 118 | 322 | 345 | 463 | 6 | 17 | 18 | 24 | 0.00060898 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 242 | 260 | 348 | 0.95 | 0.95 | 0.95 | 192.4397 | 206.7534 | 276.7314 | 41 | 44 | 59 | 0.026176 | 0.030074 | 0.053565 | 1.6 | 6 | 6.7 | 9 |  | 2144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 192.4397 | 206.7534 | 276.7314 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295802015 | 80 | 15 | 2 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1820 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 147 | 317 | 341 | 411 | 8 | 16 | 18 | 21 | 0.0002951 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295802115 | 80 | 15 | 2 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2442.4 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 197 | 451 | 484 | 649 | 10 | 23 | 25 | 33 | 0.00067687 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264 | 283 | 380 | 0.85 | 0.85 | 0.85 | 215.0597 | 230.5375 | 309.5556 | 46 | 50 | 67 | 0.013057 | 0.015362 | 0.027195 | 2.1 | 6 | 6.7 | 9 |  | 3053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.0597 | 230.5375 | 309.5556 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295901015 | 80 | 15 | 2 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 1130.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1256 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
295901115 | 80 | 15 | 2 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 1075.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
295901515 | 80 | 15 | 2 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1451.2 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 117 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1814 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
295901615 | 80 | 15 | 2 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1640.16 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 132 | 344 | 366 | 489 | 7 | 18 | 19 | 25 | 0.00084561 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 243 | 260 | 354 | 0.95 | 0.95 | 0.95 | 193.2349 | 206.7534 | 281.5026 | 42 | 44 | 61 | 0.027959 | 0.030631 | 0.058175 | 1.8 | 6 | 6.7 | 9 |  | 2412 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.2349 | 206.7534 | 281.5026 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
295902015 | 80 | 15 | 2 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2048 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 165 | 332 | 356 | 430 | 9 | 17 | 18 | 22 | 0.00038208 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2560 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
295902115 | 80 | 15 | 2 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2747.2 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 222 | 465 | 497 | 669 | 11 | 24 | 26 | 35 | 0.00084461 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 265 | 284 | 387 | 0.85 | 0.85 | 0.85 | 215.8743 | 231.3521 | 315.258 | 46 | 50 | 68 | 0.013422 | 0.015783 | 0.028709 | 2.4 | 6 | 6.7 | 9 |  | 3434 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.8743 | 231.3521 | 315.258 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951001015 | 80 | 15 | 2 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1256.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1396 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951001115 | 80 | 15 | 2 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1195.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035791 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1758 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951001515 | 80 | 15 | 2 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1612.8 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 130 | 248 | 264 | 354 | 7 | 13 | 14 | 18 | 0.00032186 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 2016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951001615 | 80 | 15 | 2 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1822.4 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 147 | 366 | 388 | 516 | 8 | 19 | 20 | 27 | 0.0011255 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 244 | 261 | 360 | 0.95 | 0.95 | 0.95 | 194.0301 | 207.5486 | 286.2739 | 42 | 45 | 62 | 0.028472 | 0.03259 | 0.061069 | 2 | 6 | 6.7 | 9 |  | 2680 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 207.5486 | 286.2739 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951002015 | 80 | 15 | 2 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2275.2 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 183 | 348 | 372 | 448 | 9 | 18 | 19 | 23 | 0.00039308 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951002115 | 80 | 15 | 2 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3052.8 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 246 | 480 | 511 | 689 | 13 | 25 | 26 | 36 | 0.0012062 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 267 | 286 | 394 | 0.85 | 0.85 | 0.85 | 217.5035 | 232.9813 | 320.9603 | 47 | 50 | 69 | 0.014373 | 0.016204 | 0.030271 | 2.7 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 217.5035 | 232.9813 | 320.9603 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951101015 | 80 | 15 | 2 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1382.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1536 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951101115 | 80 | 15 | 2 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1315.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1934 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951101515 | 70 | 15 | 2 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1774.4 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 143 | 238 | 251 | 327 | 7 | 12 | 13 | 17 | 0.00033355 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2218 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
2951101615 | 70 | 15 | 2 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2004.64 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 162 | 368 | 386 | 493 | 8 | 19 | 20 | 25 | 0.001155 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 229 | 315 | 0.95 | 0.95 | 0.95 | 170.1739 | 182.102 | 250.4896 | 37 | 39 | 54 | 0.022631 | 0.02508 | 0.047371 | 2.2 | 6 | 6.7 | 9 |  | 2948 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 170.1739 | 182.102 | 250.4896 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2951102015 | 70 | 15 | 2 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2502.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 202 | 335 | 355 | 419 | 10 | 17 | 18 | 22 | 0.00049511 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 3128 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
2951102115 | 70 | 15 | 2 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3356.8 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 271 | 449 | 475 | 625 | 14 | 23 | 25 | 32 | 0.0014376 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 235 | 252 | 347 | 0.85 | 0.85 | 0.85 | 191.4357 | 205.2842 | 282.6732 | 41 | 44 | 61 | 0.011333 | 0.012988 | 0.024423 | 2.9 | 6 | 6.7 | 9 |  | 4196 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 191.4357 | 205.2842 | 282.6732 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
2951201015 | 80 | 15 | 2 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1507.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1675 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951201115 | 80 | 15 | 2 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1434.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057024 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951201515 | 80 | 15 | 2 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1935.2 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 272 | 288 | 380 | 8 | 14 | 15 | 20 | 0.00044509 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2419 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951201615 | 80 | 15 | 2 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2186.88 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 176 | 415 | 437 | 568 | 9 | 21 | 23 | 29 | 0.0014865 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 249 | 267 | 372 | 0.95 | 0.95 | 0.95 | 198.0061 | 212.3198 | 295.8163 | 43 | 46 | 64 | 0.030884 | 0.035224 | 0.067115 | 2.4 | 6 | 6.7 | 9 |  | 3216 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 212.3198 | 295.8163 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951202015 | 80 | 15 | 2 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2730.4 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 220 | 380 | 404 | 485 | 11 | 20 | 21 | 25 | 0.00061062 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3413 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951202115 | 80 | 15 | 2 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3663.2 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 295 | 516 | 547 | 729 | 15 | 27 | 28 | 38 | 0.0016935 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 274 | 294 | 409 | 0.85 | 0.85 | 0.85 | 223.2059 | 239.4983 | 333.1796 | 48 | 51 | 72 | 0.015757 | 0.01771 | 0.034459 | 3.2 | 6 | 6.7 | 9 |  | 4579 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.2059 | 239.4983 | 333.1796 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951401015 | 80 | 15 | 2 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1758.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1954 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951401115 | 80 | 15 | 2 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1673.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084707 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2461 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
2951401515 | 80 | 15 | 2 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2257.6 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 296 | 312 | 406 | 9 | 15 | 16 | 21 | 0.00059309 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
2951401615 | 80 | 15 | 2 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2551.36 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 206 | 465 | 487 | 620 | 11 | 24 | 25 | 32 | 0.0022918 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 255 | 273 | 383 | 0.95 | 0.95 | 0.95 | 202.7773 | 217.091 | 304.5636 | 44 | 47 | 65 | 0.033412 | 0.03798 | 0.071359 | 2.8 | 6 | 6.7 | 9 |  | 3752 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 217.091 | 304.5636 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
2951402015 | 80 | 15 | 2 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3185.6 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 257 | 412 | 437 | 522 | 13 | 21 | 23 | 27 | 0.00088388 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3982 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
2951402115 | 80 | 15 | 2 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4273.6 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 345 | 552 | 583 | 769 | 18 | 28 | 30 | 40 | 0.0025438 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 281 | 301 | 423 | 0.85 | 0.85 | 0.85 | 228.9082 | 245.2006 | 344.5843 | 49 | 53 | 74 | 0.01721 | 0.020005 | 0.037988 | 3.7 | 6 | 6.7 | 9 |  | 5342 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.9082 | 245.2006 | 344.5843 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320601015 | 80 | 15 | 3 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 353.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.1473e-06 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 393 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
320601515 | 80 | 15 | 3 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 523.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4254e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 654 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
320602015 | 80 | 15 | 3 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 735.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4.0779e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 919 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
320701015 | 80 | 15 | 3 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 413.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 33 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 459 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320701515 | 70 | 15 | 3 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 610.4 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 193 | 208 | 275 | 3 | 10 | 11 | 14 | 5.5819e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 763 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
320702015 | 70 | 15 | 3 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 857.6 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 69 | 269 | 288 | 345 | 4 | 14 | 15 | 18 | 7.4184e-05 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1072 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
320801015 | 80 | 15 | 3 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 471.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 38 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.1383e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 524 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
320801515 | 80 | 15 | 3 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 697.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 56 | 228 | 244 | 328 | 3 | 12 | 13 | 17 | 5.8533e-05 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 872 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
320802015 | 80 | 15 | 3 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 317 | 341 | 411 | 4 | 16 | 18 | 21 | 7.6905e-05 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
320901015 | 80 | 15 | 3 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 531 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.3972e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 590 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
320901515 | 80 | 15 | 3 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 784.8 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 238 | 254 | 341 | 3 | 12 | 13 | 18 | 6.1246e-05 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 981 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
320902015 | 80 | 15 | 3 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1103.2 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 332 | 356 | 430 | 5 | 17 | 18 | 22 | 0.00012248 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1379 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201001015 | 80 | 15 | 3 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 589.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 48 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.656e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 655 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201001515 | 80 | 15 | 3 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 872 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 248 | 264 | 354 | 4 | 13 | 14 | 18 | 0.00011055 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1090 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3201002015 | 80 | 15 | 3 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1225.6 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 348 | 372 | 448 | 5 | 18 | 19 | 23 | 0.00012648 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 1532 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201101015 | 80 | 15 | 3 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 648.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.2405e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 721 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201101515 | 70 | 15 | 3 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 959.2 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 238 | 251 | 327 | 4 | 12 | 13 | 17 | 0.00011501 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1199 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
3201102015 | 70 | 15 | 3 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1348 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 335 | 355 | 419 | 6 | 17 | 18 | 22 | 0.00018516 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 1685 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3201201015 | 80 | 15 | 3 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 707.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.7635e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 786 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201201515 | 80 | 15 | 3 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1046.4 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 272 | 288 | 380 | 4 | 14 | 15 | 20 | 0.00011946 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1308 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201202015 | 80 | 15 | 3 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1470.4 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 380 | 404 | 485 | 6 | 20 | 21 | 25 | 0.00019063 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 1838 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201401015 | 80 | 15 | 3 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 825.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8096e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 917 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201401515 | 80 | 15 | 3 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1220.8 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 296 | 312 | 406 | 5 | 15 | 16 | 21 | 0.00019536 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 1526 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201402015 | 80 | 15 | 3 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1716 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 138 | 412 | 437 | 522 | 7 | 21 | 23 | 27 | 0.00027044 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 2145 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201601015 | 80 | 15 | 3 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 943.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1048 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201601515 | 80 | 15 | 3 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1395.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 113 | 319 | 334 | 432 | 6 | 16 | 17 | 22 | 0.00029344 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 1744 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3201602015 | 80 | 15 | 3 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1960.8 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 158 | 445 | 471 | 559 | 8 | 23 | 24 | 29 | 0.00036692 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 2451 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3201801015 | 80 | 15 | 3 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1061.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020027 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1179 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3201801515 | 60 | 15 | 3 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1569.6 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 302 | 312 | 378 | 7 | 16 | 16 | 20 | 0.00041539 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 1962 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3201802015 | 60 | 15 | 3 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2206.4 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 178 | 423 | 441 | 501 | 9 | 22 | 23 | 26 | 0.00048104 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 2758 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3202001015 | 80 | 15 | 3 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1179 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 95 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00032548 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1310 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202001515 | 80 | 15 | 3 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1744 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 372 | 383 | 484 | 7 | 19 | 20 | 25 | 0.00043878 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 2180 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202002015 | 80 | 15 | 3 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2451.2 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 512 | 538 | 633 | 10 | 26 | 28 | 33 | 0.00061375 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 3064 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202201015 | 80 | 15 | 3 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1296.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035085 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1441 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202201515 | 80 | 15 | 3 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1918.4 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 155 | 398 | 407 | 510 | 8 | 21 | 21 | 26 | 0.00059228 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 2398 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202202015 | 80 | 15 | 3 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2696 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 217 | 545 | 571 | 670 | 11 | 28 | 29 | 35 | 0.00076596 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 3370 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202401015 | 80 | 15 | 3 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1414.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0005223 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1572 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202401515 | 80 | 15 | 3 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2092.8 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 169 | 424 | 432 | 536 | 9 | 22 | 22 | 28 | 0.00077342 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 2616 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202402015 | 80 | 15 | 3 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2941.6 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 237 | 578 | 605 | 708 | 12 | 30 | 31 | 37 | 0.00093856 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 3677 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3202601015 | 80 | 15 | 3 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1532.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 124 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00055711 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 1703 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3202601515 | 60 | 15 | 3 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2267.2 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 183 | 407 | 412 | 482 | 9 | 21 | 21 | 25 | 0.00080948 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 2834 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3202602015 | 60 | 15 | 3 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3186.4 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 257 | 560 | 579 | 649 | 13 | 29 | 30 | 33 | 0.0011324 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 3983 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3202801015 | 60 | 15 | 3 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 1650.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 133 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00078045 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1834 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3202801515 | 80 | 15 | 3 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2441.6 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 197 | 476 | 481 | 588 | 10 | 25 | 25 | 30 | 0.0010269 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 3052 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3202802015 | 80 | 15 | 3 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3432 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 277 | 650 | 679 | 782 | 14 | 34 | 35 | 40 | 0.0013484 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 4290 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330601015 | 80 | 15 | 3 | 30 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 446.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 36 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 496 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330601115 | 80 | 15 | 3 | 30 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 457.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 37 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 673 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330601515 | 80 | 15 | 3 | 30 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 652 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 815 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330601615 | 80 | 15 | 3 | 30 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 603.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 888 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330602015 | 80 | 15 | 3 | 30 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 915.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1144 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330602115 | 80 | 15 | 3 | 30 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 935.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 75 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00010545 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1169 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330701015 | 80 | 15 | 3 | 30 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 520.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.8794e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 578 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330701115 | 80 | 15 | 3 | 30 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 533.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 43 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5.13e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 785 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330701515 | 70 | 15 | 3 | 30 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 760.8 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 193 | 208 | 275 | 3 | 10 | 11 | 14 | 5.5819e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 951 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
330701615 | 70 | 15 | 3 | 30 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 704.48 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 273 | 294 | 389 | 3 | 14 | 15 | 20 | 0.00015302 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1036 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
330702015 | 70 | 15 | 3 | 30 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1067.2 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 269 | 288 | 345 | 4 | 14 | 15 | 18 | 7.4184e-05 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1334 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 10
330702115 | 70 | 15 | 3 | 30 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 88 | 383 | 411 | 544 | 5 | 20 | 21 | 28 | 0.00017042 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1364 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
330801015 | 80 | 15 | 3 | 30 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 594.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 48 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3.1383e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 661 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330801115 | 80 | 15 | 3 | 30 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 609.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 897 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330801515 | 80 | 15 | 3 | 30 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 869.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 228 | 244 | 328 | 4 | 12 | 13 | 17 | 0.00010164 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330801615 | 80 | 15 | 3 | 30 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 805.12 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 322 | 345 | 463 | 3 | 17 | 18 | 24 | 0.00015844 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1184 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330802015 | 80 | 15 | 3 | 30 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1220 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 317 | 341 | 411 | 5 | 16 | 18 | 21 | 0.00011849 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1525 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330802115 | 80 | 15 | 3 | 30 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1246.4 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 101 | 451 | 484 | 649 | 5 | 23 | 25 | 33 | 0.00017841 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 1558 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330901015 | 80 | 15 | 3 | 30 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 668.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 743 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
330901115 | 80 | 15 | 3 | 30 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 686.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00012974 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1009 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
330901515 | 80 | 15 | 3 | 30 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 978.4 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 238 | 254 | 341 | 4 | 12 | 13 | 18 | 0.0001061 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1223 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
330901615 | 80 | 15 | 3 | 30 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 905.76 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 344 | 366 | 489 | 4 | 18 | 19 | 25 | 0.00028576 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1332 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
330902015 | 80 | 15 | 3 | 30 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1372 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 332 | 356 | 430 | 6 | 17 | 18 | 22 | 0.00017422 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1715 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
330902115 | 80 | 15 | 3 | 30 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1402.4 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 113 | 465 | 497 | 669 | 6 | 24 | 26 | 35 | 0.00026412 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 1753 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301001015 | 80 | 15 | 3 | 30 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 743.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.7174e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 826 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301001115 | 80 | 15 | 3 | 30 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 762.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.0001402 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1121 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301001515 | 80 | 15 | 3 | 30 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1087.2 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 88 | 248 | 264 | 354 | 5 | 13 | 14 | 18 | 0.00016918 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1359 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301001615 | 80 | 15 | 3 | 30 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1006.4 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 81 | 366 | 388 | 516 | 4 | 19 | 20 | 27 | 0.00029467 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1480 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301002015 | 80 | 15 | 3 | 30 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1524.8 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 348 | 372 | 448 | 6 | 18 | 19 | 23 | 0.00017969 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 1906 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301002115 | 80 | 15 | 3 | 30 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1558.4 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 126 | 480 | 511 | 689 | 7 | 25 | 26 | 36 | 0.00036904 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 1948 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301101015 | 80 | 15 | 3 | 30 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 818.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8.2405e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 909 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301101115 | 80 | 15 | 3 | 30 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 838.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1233 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301101515 | 70 | 15 | 3 | 30 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1196 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 238 | 251 | 327 | 5 | 12 | 13 | 17 | 0.00017573 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1495 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3301101615 | 70 | 15 | 3 | 30 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1107.04 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 89 | 368 | 386 | 493 | 5 | 19 | 20 | 25 | 0.00046639 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 1628 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3301102015 | 70 | 15 | 3 | 30 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1677.6 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 135 | 335 | 355 | 419 | 7 | 17 | 18 | 22 | 0.00024904 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2097 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3301102115 | 70 | 15 | 3 | 30 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1714.4 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 138 | 449 | 475 | 625 | 7 | 23 | 25 | 32 | 0.00038331 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2143 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3301201015 | 80 | 15 | 3 | 30 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 891.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 991 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301201115 | 80 | 15 | 3 | 30 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 914.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.000272 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301201515 | 80 | 15 | 3 | 30 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1304.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 105 | 272 | 288 | 380 | 5 | 14 | 15 | 20 | 0.00018227 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1631 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301201615 | 80 | 15 | 3 | 30 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1207.68 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 97 | 415 | 437 | 568 | 5 | 21 | 23 | 29 | 0.00047948 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 1776 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301202015 | 80 | 15 | 3 | 30 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1829.6 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 148 | 380 | 404 | 485 | 8 | 20 | 21 | 25 | 0.00033101 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2287 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301202115 | 80 | 15 | 3 | 30 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1870.4 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 151 | 516 | 547 | 729 | 8 | 27 | 28 | 38 | 0.0005121 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 2338 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301401015 | 80 | 15 | 3 | 30 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1040.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00016581 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301401115 | 80 | 15 | 3 | 30 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1066.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00030646 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1569 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301401515 | 80 | 15 | 3 | 30 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1522.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 296 | 312 | 406 | 6 | 15 | 16 | 21 | 0.00027551 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 1903 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301401615 | 80 | 15 | 3 | 30 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1408.96 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 114 | 465 | 487 | 620 | 6 | 24 | 25 | 32 | 0.00071654 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2072 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301402015 | 80 | 15 | 3 | 30 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2134.4 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 412 | 437 | 522 | 9 | 21 | 23 | 27 | 0.00043706 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301402115 | 80 | 15 | 3 | 30 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2181.6 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 176 | 552 | 583 | 769 | 9 | 28 | 30 | 40 | 0.00068438 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 2727 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301601015 | 80 | 15 | 3 | 30 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1189.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00027473 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1322 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301601115 | 80 | 15 | 3 | 30 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1219.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00051016 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 1794 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301601515 | 80 | 15 | 3 | 30 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1739.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 319 | 334 | 432 | 7 | 16 | 17 | 22 | 0.00039201 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2174 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3301601615 | 80 | 15 | 3 | 30 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1610.24 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 130 | 513 | 534 | 672 | 7 | 26 | 28 | 35 | 0.0010093 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 2368 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301602015 | 80 | 15 | 3 | 30 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2440 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 197 | 445 | 471 | 559 | 10 | 23 | 24 | 29 | 0.00056102 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3050 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3301602115 | 80 | 15 | 3 | 30 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2493.6 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 201 | 587 | 616 | 809 | 10 | 30 | 32 | 42 | 0.0008878 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 3117 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301801015 | 80 | 15 | 3 | 30 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1338.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 108 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00041786 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1487 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3301801115 | 80 | 15 | 3 | 30 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1372.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00077912 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2018 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3301801515 | 60 | 15 | 3 | 30 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1956.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 158 | 302 | 312 | 378 | 8 | 16 | 16 | 20 | 0.0005334 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 2446 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3301801615 | 60 | 15 | 3 | 30 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1811.52 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 146 | 520 | 534 | 627 | 8 | 27 | 28 | 32 | 0.001361 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 2664 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3301802015 | 60 | 15 | 3 | 30 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2744.8 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 221 | 423 | 441 | 501 | 11 | 22 | 23 | 26 | 0.00070383 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 3431 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3301802115 | 60 | 15 | 3 | 30 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2804.8 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 226 | 530 | 549 | 680 | 12 | 27 | 28 | 35 | 0.0013233 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 3506 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302001015 | 80 | 15 | 3 | 30 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1486.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00045267 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1652 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302001115 | 80 | 15 | 3 | 30 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1524.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00084875 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2242 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302001515 | 80 | 15 | 3 | 30 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2174.4 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 175 | 372 | 383 | 484 | 9 | 19 | 20 | 25 | 0.00070129 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 2718 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302001615 | 80 | 15 | 3 | 30 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2012.8 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 162 | 618 | 634 | 777 | 8 | 32 | 33 | 40 | 0.0014199 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 2960 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302002015 | 80 | 15 | 3 | 30 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3049.6 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 512 | 538 | 633 | 13 | 26 | 28 | 33 | 0.0010081 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 3812 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302002115 | 80 | 15 | 3 | 30 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3116.8 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 251 | 668 | 691 | 890 | 13 | 34 | 36 | 46 | 0.0016204 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 3896 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302201015 | 80 | 15 | 3 | 30 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1635.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00064399 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1817 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302201115 | 80 | 15 | 3 | 30 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1676.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.001211 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 2466 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302201515 | 80 | 15 | 3 | 30 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2392 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 193 | 398 | 407 | 510 | 10 | 21 | 21 | 26 | 0.00089719 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 2990 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302201615 | 80 | 15 | 3 | 30 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2214.08 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 179 | 670 | 683 | 829 | 9 | 35 | 35 | 43 | 0.0018471 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 3256 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302202015 | 80 | 15 | 3 | 30 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3354.4 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 271 | 545 | 571 | 670 | 14 | 28 | 29 | 35 | 0.0012072 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 4193 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302202115 | 80 | 15 | 3 | 30 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3428.8 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 277 | 708 | 726 | 930 | 14 | 37 | 37 | 48 | 0.0019552 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 4286 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302401015 | 80 | 15 | 3 | 30 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1783.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00068948 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1982 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302401115 | 80 | 15 | 3 | 30 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 1829.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 148 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0016538 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 2690 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302401515 | 80 | 15 | 3 | 30 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2609.6 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 210 | 424 | 432 | 536 | 11 | 22 | 22 | 28 | 0.0011226 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 3262 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302401615 | 80 | 15 | 3 | 30 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2415.36 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 195 | 723 | 734 | 881 | 10 | 37 | 38 | 45 | 0.0023406 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 3552 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302402015 | 80 | 15 | 3 | 30 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3659.2 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 295 | 578 | 605 | 708 | 15 | 30 | 31 | 37 | 0.0014282 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 4574 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302402115 | 80 | 15 | 3 | 30 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3740 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 302 | 748 | 764 | 970 | 16 | 39 | 39 | 50 | 0.0026262 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 4675 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302601015 | 80 | 15 | 3 | 30 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 1933.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00093455 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2148 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302601115 | 80 | 15 | 3 | 30 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 1982.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 160 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0017685 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 2915 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3302601515 | 60 | 15 | 3 | 30 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2826.4 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 228 | 407 | 412 | 482 | 12 | 21 | 21 | 25 | 0.001379 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 3533 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3302601615 | 60 | 15 | 3 | 30 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2616.64 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 211 | 729 | 736 | 836 | 11 | 38 | 38 | 43 | 0.0029035 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 3848 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302602015 | 60 | 15 | 3 | 30 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3964.8 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 320 | 560 | 579 | 649 | 17 | 29 | 30 | 33 | 0.001874 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 4956 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3302602115 | 60 | 15 | 3 | 30 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4052 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 327 | 691 | 701 | 841 | 17 | 36 | 36 | 43 | 0.003071 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 5065 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302801015 | 60 | 15 | 3 | 30 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2081.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0012257 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2313 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3302801115 | 60 | 15 | 3 | 30 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2134.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0023241 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3139 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3302801515 | 80 | 15 | 3 | 30 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3044 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 245 | 476 | 481 | 588 | 13 | 25 | 25 | 30 | 0.0016677 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 3805 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3302801615 | 80 | 15 | 3 | 30 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 2817.92 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 227 | 827 | 834 | 986 | 12 | 43 | 43 | 51 | 0.0035385 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 4144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3302802015 | 80 | 15 | 3 | 30 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4269.6 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 344 | 650 | 679 | 782 | 18 | 34 | 35 | 40 | 0.0021592 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 5337 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3302802115 | 80 | 15 | 3 | 30 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4363.2 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 352 | 829 | 838 | 1050 | 18 | 43 | 43 | 54 | 0.0035594 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 5454 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3303001015 | 40 | 15 | 3 | 30 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2230.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001296 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 2478 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3303001115 | 40 | 15 | 3 | 30 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2286.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 184 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0024648 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 3363 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3303001515 | 60 | 15 | 3 | 30 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3261.6 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 263 | 459 | 462 | 535 | 14 | 24 | 24 | 28 | 0.0019902 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 4077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3303001615 | 60 | 15 | 3 | 30 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3019.2 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 243 | 833 | 838 | 941 | 13 | 43 | 43 | 49 | 0.0042484 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 319 | 326 | 485 | 0.95 | 0.95 | 0.95 | 253.6705 | 259.2369 | 385.6745 | 55 | 56 | 83 | 0.06463 | 0.066882 | 0.14148 | 6 | 6 | 6.7 | 9 |  | 4440 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 253.6705 | 259.2369 | 385.6745 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3303002015 | 60 | 15 | 3 | 30 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4574.4 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 369 | 634 | 654 | 723 | 19 | 33 | 34 | 37 | 0.0024693 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 5718 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3303002115 | 60 | 15 | 3 | 30 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4675.2 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 377 | 771 | 778 | 921 | 19 | 40 | 40 | 48 | 0.0040931 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 364 | 372 | 553 | 0.85 | 0.85 | 0.85 | 296.5217 | 303.0387 | 450.4849 | 64 | 65 | 97 | 0.039046 | 0.040194 | 0.085077 | 8 | 6 | 6.7 | 9 |  | 5844 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 296.5217 | 303.0387 | 450.4849 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
340601015 | 80 | 15 | 3 | 40 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 520.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 578 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340601115 | 80 | 15 | 3 | 40 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 515.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 42 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 758 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340601515 | 80 | 15 | 3 | 40 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 752.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 941 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340601615 | 80 | 15 | 3 | 40 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 693.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1020 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340602015 | 80 | 15 | 3 | 40 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1054.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 7.1462e-05 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1318 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340602115 | 80 | 15 | 3 | 40 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 88 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1364 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340701015 | 80 | 15 | 3 | 40 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 606.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 674 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340701115 | 80 | 15 | 3 | 40 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 601.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 885 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340701515 | 70 | 15 | 3 | 40 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 878.4 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 71 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
340701615 | 70 | 15 | 3 | 40 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 809.2 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 65 | 273 | 294 | 389 | 3 | 14 | 15 | 20 | 0.00015302 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1190 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
340702015 | 70 | 15 | 3 | 40 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1229.6 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 269 | 288 | 345 | 5 | 14 | 15 | 18 | 0.00011449 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1537 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
340702115 | 70 | 15 | 3 | 40 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1273.6 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 103 | 383 | 411 | 544 | 5 | 20 | 21 | 28 | 0.00017042 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1592 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
340801015 | 80 | 15 | 3 | 40 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 693 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 56 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 770 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340801115 | 80 | 15 | 3 | 40 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 687.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1011 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340801515 | 80 | 15 | 3 | 40 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1003.2 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 81 | 228 | 244 | 328 | 4 | 12 | 13 | 17 | 0.00010164 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1254 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340801615 | 80 | 15 | 3 | 40 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 924.8 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 75 | 322 | 345 | 463 | 4 | 17 | 18 | 24 | 0.00027685 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1360 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340802015 | 80 | 15 | 3 | 40 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1405.6 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 113 | 317 | 341 | 411 | 6 | 16 | 18 | 21 | 0.00016875 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1757 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340802115 | 80 | 15 | 3 | 40 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1455.2 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 117 | 451 | 484 | 649 | 6 | 23 | 25 | 33 | 0.00025318 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 1819 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340901015 | 80 | 15 | 3 | 40 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 780.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 7.1943e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 867 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
340901115 | 80 | 15 | 3 | 40 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 773.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00012974 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1138 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
340901515 | 80 | 15 | 3 | 40 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1128.8 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 238 | 254 | 341 | 5 | 12 | 13 | 18 | 0.00016264 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1411 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
340901615 | 80 | 15 | 3 | 40 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1040.4 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 344 | 366 | 489 | 4 | 18 | 19 | 25 | 0.00028576 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1530 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
340902015 | 80 | 15 | 3 | 40 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1580.8 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 332 | 356 | 430 | 7 | 17 | 18 | 22 | 0.00023478 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 1976 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
340902115 | 80 | 15 | 3 | 40 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1637.6 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 132 | 465 | 497 | 669 | 7 | 24 | 26 | 35 | 0.00035477 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 2047 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401001015 | 80 | 15 | 3 | 40 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 866.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 963 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401001115 | 80 | 15 | 3 | 40 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 859.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1264 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401001515 | 80 | 15 | 3 | 40 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1254.4 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 248 | 264 | 354 | 5 | 13 | 14 | 18 | 0.00016918 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1568 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401001615 | 80 | 15 | 3 | 40 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1156 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 93 | 366 | 388 | 516 | 5 | 19 | 20 | 27 | 0.0004533 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1700 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401002015 | 80 | 15 | 3 | 40 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1756.8 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 348 | 372 | 448 | 7 | 18 | 19 | 23 | 0.00024191 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2196 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401002115 | 80 | 15 | 3 | 40 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1819.2 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 147 | 480 | 511 | 689 | 8 | 25 | 26 | 36 | 0.0004762 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 2274 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401101015 | 80 | 15 | 3 | 40 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 953.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1059 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401101115 | 80 | 15 | 3 | 40 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 945.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401101515 | 70 | 15 | 3 | 40 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1380 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 111 | 238 | 251 | 327 | 6 | 12 | 13 | 17 | 0.00024862 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1725 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3401101615 | 70 | 15 | 3 | 40 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1271.6 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 103 | 368 | 386 | 493 | 5 | 19 | 20 | 25 | 0.00046639 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 1870 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3401102015 | 70 | 15 | 3 | 40 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1932.8 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 335 | 355 | 419 | 8 | 17 | 18 | 22 | 0.00032203 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2416 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3401102115 | 70 | 15 | 3 | 40 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2000.8 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 161 | 449 | 475 | 625 | 8 | 23 | 25 | 32 | 0.00049415 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2501 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3401201015 | 80 | 15 | 3 | 40 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1040.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00014858 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401201115 | 80 | 15 | 3 | 40 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1031.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.000272 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1517 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401201515 | 80 | 15 | 3 | 40 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1505.6 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 121 | 272 | 288 | 380 | 6 | 14 | 15 | 20 | 0.00025759 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 1882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401201615 | 80 | 15 | 3 | 40 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1387.2 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 112 | 415 | 437 | 568 | 6 | 21 | 23 | 29 | 0.00068069 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 2040 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401202015 | 80 | 15 | 3 | 40 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2108 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 170 | 380 | 404 | 485 | 9 | 20 | 21 | 25 | 0.00041507 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2635 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401202115 | 80 | 15 | 3 | 40 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2183.2 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 176 | 516 | 547 | 729 | 9 | 27 | 28 | 38 | 0.0006404 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 2729 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401401015 | 80 | 15 | 3 | 40 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1213.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00024935 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1348 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401401115 | 80 | 15 | 3 | 40 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1203.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 97 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00045941 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1770 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401401515 | 80 | 15 | 3 | 40 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1756 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 296 | 312 | 406 | 7 | 15 | 16 | 21 | 0.00036862 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2195 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401401615 | 80 | 15 | 3 | 40 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1618.4 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 465 | 487 | 620 | 7 | 24 | 25 | 32 | 0.00096253 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2380 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401402015 | 80 | 15 | 3 | 40 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2459.2 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 198 | 412 | 437 | 522 | 10 | 21 | 23 | 27 | 0.00053465 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3074 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401402115 | 80 | 15 | 3 | 40 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2547.2 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 205 | 552 | 583 | 769 | 11 | 28 | 30 | 40 | 0.00099995 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 3184 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401601015 | 80 | 15 | 3 | 40 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1386.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1541 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401601115 | 80 | 15 | 3 | 40 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1374.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 111 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00070949 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2022 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401601515 | 80 | 15 | 3 | 40 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 162 | 319 | 334 | 432 | 8 | 16 | 17 | 22 | 0.00050396 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2509 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3401601615 | 80 | 15 | 3 | 40 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1849.6 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 149 | 513 | 534 | 672 | 8 | 26 | 28 | 35 | 0.0013022 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 2720 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401602015 | 80 | 15 | 3 | 40 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2811.2 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 227 | 445 | 471 | 559 | 12 | 23 | 24 | 29 | 0.0007942 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3514 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3401602115 | 80 | 15 | 3 | 40 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2910.4 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 235 | 587 | 616 | 809 | 12 | 30 | 32 | 42 | 0.0012511 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 3638 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401801015 | 80 | 15 | 3 | 40 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1559.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 126 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1733 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3401801115 | 80 | 15 | 3 | 40 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1547 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00077912 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2275 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3401801515 | 60 | 15 | 3 | 40 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2257.6 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 302 | 312 | 378 | 9 | 16 | 16 | 20 | 0.00066522 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 2822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3401801615 | 60 | 15 | 3 | 40 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2080.8 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 168 | 520 | 534 | 627 | 9 | 27 | 28 | 32 | 0.0017028 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 3060 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3401802015 | 60 | 15 | 3 | 40 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3162.4 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 255 | 423 | 441 | 501 | 13 | 22 | 23 | 26 | 0.00096672 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 3953 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3401802115 | 60 | 15 | 3 | 40 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3274.4 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 264 | 530 | 549 | 680 | 14 | 27 | 28 | 35 | 0.001767 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 4093 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402001015 | 80 | 15 | 3 | 40 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1733.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00059851 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1926 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402001115 | 80 | 15 | 3 | 40 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1719.04 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00112 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2528 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402001515 | 80 | 15 | 3 | 40 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2508.8 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 202 | 372 | 383 | 484 | 10 | 19 | 20 | 25 | 0.00085394 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402001615 | 80 | 15 | 3 | 40 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2312 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 186 | 618 | 634 | 777 | 10 | 32 | 33 | 40 | 0.0021676 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 3400 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402002015 | 80 | 15 | 3 | 40 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3513.6 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 283 | 512 | 538 | 633 | 15 | 26 | 28 | 33 | 0.0013222 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402002115 | 80 | 15 | 3 | 40 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3638.4 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 293 | 668 | 691 | 890 | 15 | 34 | 36 | 46 | 0.0021174 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 4548 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402201015 | 80 | 15 | 3 | 40 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1907.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00081987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2119 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402201115 | 80 | 15 | 3 | 40 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1891.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0015391 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 2781 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402201515 | 80 | 15 | 3 | 40 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2760 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 223 | 398 | 407 | 510 | 12 | 21 | 21 | 26 | 0.0012605 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3450 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402201615 | 80 | 15 | 3 | 40 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2543.2 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 205 | 670 | 683 | 829 | 11 | 35 | 35 | 43 | 0.0026996 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 3740 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402202015 | 80 | 15 | 3 | 40 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3864.8 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 312 | 545 | 571 | 670 | 16 | 28 | 29 | 35 | 0.0015537 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 4831 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402202115 | 80 | 15 | 3 | 40 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4002.4 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 323 | 708 | 726 | 930 | 17 | 37 | 37 | 48 | 0.002808 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 5003 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402401015 | 80 | 15 | 3 | 40 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2079.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001085 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2311 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402401115 | 80 | 15 | 3 | 40 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2063.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 166 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0020427 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3034 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402401515 | 80 | 15 | 3 | 40 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3010.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 243 | 424 | 432 | 536 | 13 | 22 | 22 | 28 | 0.0015318 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 3763 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402401615 | 80 | 15 | 3 | 40 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2774.4 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 224 | 723 | 734 | 881 | 12 | 37 | 38 | 45 | 0.0033016 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 4080 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402402015 | 80 | 15 | 3 | 40 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4216 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 340 | 578 | 605 | 708 | 18 | 30 | 31 | 37 | 0.0020141 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 5270 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402402115 | 80 | 15 | 3 | 40 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4366.4 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 352 | 748 | 764 | 970 | 18 | 39 | 39 | 50 | 0.0032692 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 5458 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402601015 | 80 | 15 | 3 | 40 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2253.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0011554 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2504 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402601115 | 80 | 15 | 3 | 40 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2234.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0021834 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3286 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3402601515 | 60 | 15 | 3 | 40 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3261.6 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 263 | 407 | 412 | 482 | 14 | 21 | 21 | 25 | 0.0018357 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4077 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3402601615 | 60 | 15 | 3 | 40 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3005.6 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 242 | 729 | 736 | 836 | 12 | 38 | 38 | 43 | 0.00342 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 4420 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402602015 | 60 | 15 | 3 | 40 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4568 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 368 | 560 | 579 | 649 | 19 | 29 | 30 | 33 | 0.0023101 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 5710 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3402602115 | 60 | 15 | 3 | 40 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4729.6 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 381 | 691 | 701 | 841 | 20 | 36 | 36 | 43 | 0.0041517 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 5912 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402801015 | 60 | 15 | 3 | 40 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2426.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 196 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0014814 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2696 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3402801115 | 60 | 15 | 3 | 40 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2406.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 194 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0028056 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3539 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3402801515 | 80 | 15 | 3 | 40 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3512 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 283 | 476 | 481 | 588 | 15 | 25 | 25 | 30 | 0.0021738 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4390 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3402801615 | 80 | 15 | 3 | 40 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3236.8 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 261 | 827 | 834 | 986 | 13 | 43 | 43 | 51 | 0.0041124 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 4760 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3402802015 | 80 | 15 | 3 | 40 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4919.2 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 397 | 650 | 679 | 782 | 20 | 34 | 35 | 40 | 0.0026313 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 6149 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3402802115 | 80 | 15 | 3 | 40 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5093.6 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 411 | 829 | 838 | 1050 | 21 | 43 | 43 | 54 | 0.0047347 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 6367 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3403001015 | 40 | 15 | 3 | 40 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2600.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 210 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0018582 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 2889 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3403001115 | 40 | 15 | 3 | 40 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2578.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 208 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0035263 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 3792 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3403001515 | 60 | 15 | 3 | 40 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3763.2 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 303 | 459 | 462 | 535 | 16 | 24 | 24 | 28 | 0.0025473 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 4704 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3403001615 | 60 | 15 | 3 | 40 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3468 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 280 | 833 | 838 | 941 | 14 | 43 | 43 | 49 | 0.0048816 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 319 | 326 | 485 | 0.95 | 0.95 | 0.95 | 253.6705 | 259.2369 | 385.6745 | 55 | 56 | 83 | 0.06463 | 0.066882 | 0.14148 | 6 | 6 | 6.7 | 9 |  | 5100 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 253.6705 | 259.2369 | 385.6745 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3403002015 | 60 | 15 | 3 | 40 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5270.4 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 425 | 634 | 654 | 723 | 22 | 33 | 34 | 37 | 0.0032498 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 6588 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3403002115 | 60 | 15 | 3 | 40 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5457.6 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 440 | 771 | 778 | 921 | 23 | 40 | 40 | 48 | 0.0058255 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 364 | 372 | 553 | 0.85 | 0.85 | 0.85 | 296.5217 | 303.0387 | 450.4849 | 64 | 65 | 97 | 0.039046 | 0.040194 | 0.085077 | 8 | 6 | 6.7 | 9 |  | 6822 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 296.5217 | 303.0387 | 450.4849 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
350601015 | 80 | 15 | 3 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 581.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.6205e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 646 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350601115 | 80 | 15 | 3 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 565.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4.6122e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 832 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350601515 | 80 | 15 | 3 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 832 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 67 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.3106e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1040 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350601615 | 80 | 15 | 3 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 774.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00014759 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1139 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350602015 | 80 | 15 | 3 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1455 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350602115 | 80 | 15 | 3 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00016243 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1549 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350701015 | 80 | 15 | 3 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 677.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 55 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 753 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350701115 | 80 | 15 | 3 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 659.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 53 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 970 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350701515 | 70 | 15 | 3 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 971.2 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1214 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
350701615 | 70 | 15 | 3 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 73 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 265 | 285 | 377 | 0.95 | 0.95 | 0.95 | 210.7294 | 226.6335 | 299.7924 | 45 | 49 | 64 | 0.030855 | 0.036496 | 0.061809 | 1.4 | 6 | 6.7 | 9 |  | 1329 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 210.7294 | 226.6335 | 299.7924 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
350702015 | 70 | 15 | 3 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 110 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1698 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
350702115 | 70 | 15 | 3 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 117 | 383 | 411 | 544 | 6 | 20 | 21 | 28 | 0.00024224 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 411 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 334.8088 | 51 | 54 | 72 | 0.015531 | 0.017369 | 0.030512 | 1.9 | 6 | 6.7 | 9 |  | 1807 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 334.8088 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
350801015 | 80 | 15 | 3 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 774.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 62 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.6713e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 861 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350801115 | 80 | 15 | 3 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 754.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1109 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350801515 | 80 | 15 | 3 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350801615 | 80 | 15 | 3 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 83 | 322 | 345 | 463 | 4 | 17 | 18 | 24 | 0.00027685 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 248.104 | 266.3937 | 357.8423 | 53 | 57 | 77 | 0.043371 | 0.050049 | 0.090503 | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.104 | 266.3937 | 357.8423 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350802015 | 80 | 15 | 3 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 317 | 341 | 411 | 6 | 16 | 18 | 21 | 0.00016875 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350802115 | 80 | 15 | 3 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 133 | 451 | 484 | 649 | 7 | 23 | 25 | 33 | 0.00034051 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 341 | 366 | 490 | 0.85 | 0.85 | 0.85 | 277.7854 | 298.1509 | 399.1638 | 60 | 64 | 86 | 0.021924 | 0.024868 | 0.044301 | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 277.7854 | 298.1509 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350901015 | 80 | 15 | 3 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 871.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 968 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
350901115 | 80 | 15 | 3 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 847.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1247 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
350901515 | 80 | 15 | 3 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 238 | 254 | 341 | 5 | 12 | 13 | 18 | 0.00016264 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1561 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
350901615 | 80 | 15 | 3 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 94 | 344 | 366 | 489 | 5 | 18 | 19 | 25 | 0.00044021 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 336 | 457 | 0.95 | 0.95 | 0.95 | 248.8992 | 267.1889 | 363.4088 | 54 | 57 | 78 | 0.045788 | 0.050918 | 0.094327 | 1.8 | 6 | 6.7 | 9 |  | 1708 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 267.1889 | 363.4088 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
350902015 | 80 | 15 | 3 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 332 | 356 | 430 | 7 | 17 | 18 | 22 | 0.00023478 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2183 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
350902115 | 80 | 15 | 3 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 150 | 465 | 497 | 669 | 8 | 24 | 26 | 35 | 0.00045824 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 342 | 367 | 500 | 0.85 | 0.85 | 0.85 | 278.6001 | 298.9656 | 407.31 | 60 | 64 | 88 | 0.022501 | 0.025513 | 0.047454 | 2.4 | 6 | 6.7 | 9 |  | 2324 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 278.6001 | 298.9656 | 407.31 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501001015 | 80 | 15 | 3 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 968.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1076 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501001115 | 80 | 15 | 3 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 942.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1386 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501001515 | 80 | 15 | 3 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 112 | 248 | 264 | 354 | 6 | 13 | 14 | 18 | 0.00023966 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1734 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501001615 | 80 | 15 | 3 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 104 | 366 | 388 | 516 | 5 | 19 | 20 | 27 | 0.0004533 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 315 | 337 | 465 | 0.95 | 0.95 | 0.95 | 250.4896 | 267.9842 | 369.7704 | 54 | 58 | 80 | 0.04658 | 0.053583 | 0.1007 | 2 | 6 | 6.7 | 9 |  | 1898 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.4896 | 267.9842 | 369.7704 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501002015 | 80 | 15 | 3 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 348 | 372 | 448 | 8 | 18 | 19 | 23 | 0.00031305 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2425 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501002115 | 80 | 15 | 3 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 167 | 480 | 511 | 689 | 9 | 25 | 26 | 36 | 0.00059642 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 509 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 414.6416 | 60 | 65 | 89 | 0.023077 | 0.026956 | 0.049649 | 2.7 | 6 | 6.7 | 9 |  | 2582 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 414.6416 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501101015 | 80 | 15 | 3 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1065.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 86 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013996 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1184 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501101115 | 80 | 15 | 3 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1037 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 84 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025477 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1525 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501101515 | 70 | 15 | 3 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 238 | 251 | 327 | 6 | 12 | 13 | 17 | 0.00024862 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 1907 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3501101615 | 70 | 15 | 3 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 368 | 386 | 493 | 6 | 19 | 20 | 25 | 0.00066276 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 276 | 295 | 407 | 0.95 | 0.95 | 0.95 | 219.4766 | 234.5855 | 323.6485 | 47 | 50 | 70 | 0.03611 | 0.040753 | 0.078723 | 2.2 | 6 | 6.7 | 9 |  | 2088 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 219.4766 | 234.5855 | 323.6485 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3501102015 | 70 | 15 | 3 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 335 | 355 | 419 | 9 | 17 | 18 | 22 | 0.00040407 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2668 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3501102115 | 70 | 15 | 3 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 183 | 449 | 475 | 625 | 9 | 23 | 25 | 32 | 0.00061841 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 304 | 325 | 448 | 0.85 | 0.85 | 0.85 | 247.6445 | 264.7515 | 364.9498 | 53 | 57 | 78 | 0.018608 | 0.021419 | 0.03932 | 2.9 | 6 | 6.7 | 9 |  | 2840 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 247.6445 | 264.7515 | 364.9498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3501201015 | 80 | 15 | 3 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1161.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 94 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501201115 | 80 | 15 | 3 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1130.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501201515 | 80 | 15 | 3 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 272 | 288 | 380 | 7 | 14 | 15 | 20 | 0.00034524 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2081 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501201615 | 80 | 15 | 3 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 125 | 415 | 437 | 568 | 6 | 21 | 23 | 29 | 0.00068069 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322 | 345 | 480 | 0.95 | 0.95 | 0.95 | 256.0561 | 274.3458 | 381.6985 | 55 | 59 | 82 | 0.04992 | 0.057254 | 0.10896 | 2.4 | 6 | 6.7 | 9 |  | 2278 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 256.0561 | 274.3458 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501202015 | 80 | 15 | 3 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 188 | 380 | 404 | 485 | 10 | 20 | 21 | 25 | 0.00050829 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 2910 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501202115 | 80 | 15 | 3 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 200 | 516 | 547 | 729 | 10 | 27 | 28 | 38 | 0.00078234 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 354 | 379 | 527 | 0.85 | 0.85 | 0.85 | 288.3755 | 308.741 | 429.3048 | 62 | 66 | 92 | 0.025814 | 0.029126 | 0.055365 | 3.2 | 6 | 6.7 | 9 |  | 3098 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 288.3755 | 308.741 | 429.3048 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501401015 | 80 | 15 | 3 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1355.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501401115 | 80 | 15 | 3 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1319.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00045941 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 1940 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501401515 | 80 | 15 | 3 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 157 | 296 | 312 | 406 | 8 | 15 | 16 | 21 | 0.00047453 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2428 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501401615 | 80 | 15 | 3 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 146 | 465 | 487 | 620 | 8 | 24 | 25 | 32 | 0.0012433 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 329 | 352 | 495 | 0.95 | 0.95 | 0.95 | 261.6225 | 279.9122 | 393.6266 | 56 | 60 | 85 | 0.053393 | 0.061064 | 0.12036 | 2.8 | 6 | 6.7 | 9 |  | 2657 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 261.6225 | 279.9122 | 393.6266 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501402015 | 80 | 15 | 3 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 412 | 437 | 522 | 11 | 21 | 23 | 27 | 0.00064169 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3395 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501402115 | 80 | 15 | 3 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 233 | 552 | 583 | 769 | 12 | 28 | 30 | 40 | 0.0011789 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 363 | 389 | 546 | 0.85 | 0.85 | 0.85 | 295.7071 | 316.8872 | 444.7825 | 64 | 68 | 96 | 0.028735 | 0.032286 | 0.062711 | 3.7 | 6 | 6.7 | 9 |  | 3615 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 295.7071 | 316.8872 | 444.7825 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501601015 | 80 | 15 | 3 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1549.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 125 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00038304 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1722 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501601115 | 80 | 15 | 3 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1508.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00070949 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2218 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501601515 | 80 | 15 | 3 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 319 | 334 | 432 | 9 | 16 | 17 | 22 | 0.00062916 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2774 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3501601615 | 80 | 15 | 3 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 167 | 513 | 534 | 672 | 9 | 26 | 28 | 35 | 0.0016307 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 335 | 357 | 510 | 0.95 | 0.95 | 0.95 | 266.3937 | 283.8883 | 405.5547 | 57 | 61 | 87 | 0.057002 | 0.065014 | 0.12955 | 3.2 | 6 | 6.7 | 9 |  | 3037 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3937 | 283.8883 | 405.5547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501602015 | 80 | 15 | 3 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 250 | 445 | 471 | 559 | 13 | 23 | 24 | 29 | 0.0009253 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 3880 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3501602115 | 80 | 15 | 3 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 267 | 587 | 616 | 809 | 14 | 30 | 32 | 42 | 0.0016729 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 371 | 396 | 564 | 0.85 | 0.85 | 0.85 | 302.224 | 322.5895 | 459.4457 | 65 | 69 | 99 | 0.030928 | 0.034672 | 0.069277 | 4.3 | 6 | 6.7 | 9 |  | 4131 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 302.224 | 322.5895 | 459.4457 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501801015 | 80 | 15 | 3 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1743.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 141 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00055302 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1937 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3501801115 | 80 | 15 | 3 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1696.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 137 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.001029 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2495 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3501801515 | 60 | 15 | 3 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 201 | 302 | 312 | 378 | 10 | 16 | 16 | 20 | 0.00081069 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3121 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3501801615 | 60 | 15 | 3 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 187 | 520 | 534 | 627 | 10 | 27 | 28 | 32 | 0.0020811 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 259 | 277 | 395 | 0.95 | 0.95 | 0.95 | 205.9581 | 220.2718 | 314.1061 | 44 | 47 | 68 | 0.035637 | 0.040473 | 0.082626 | 3.6 | 6 | 6.7 | 9 |  | 3416 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 205.9581 | 220.2718 | 314.1061 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3501802015 | 60 | 15 | 3 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 282 | 423 | 441 | 501 | 15 | 22 | 23 | 26 | 0.0012692 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4365 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3501802115 | 60 | 15 | 3 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 300 | 530 | 549 | 680 | 15 | 27 | 28 | 35 | 0.0020114 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 311 | 443 | 0.85 | 0.85 | 0.85 | 237.0544 | 253.3468 | 360.8767 | 51 | 54 | 78 | 0.020326 | 0.02266 | 0.045662 | 4.8 | 6 | 6.7 | 9 |  | 4648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 253.3468 | 360.8767 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502001015 | 80 | 15 | 3 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 1936.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 156 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00076253 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2152 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502001115 | 80 | 15 | 3 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 1884.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 152 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0014244 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2772 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502001515 | 80 | 15 | 3 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 224 | 372 | 383 | 484 | 12 | 19 | 20 | 25 | 0.0012013 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3468 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502001615 | 80 | 15 | 3 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 208 | 618 | 634 | 777 | 11 | 32 | 33 | 40 | 0.0025976 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 374 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 297.4067 | 429.4108 | 61 | 64 | 92 | 0.068922 | 0.075605 | 0.15235 | 4 | 6 | 6.7 | 9 |  | 3796 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 297.4067 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502002015 | 80 | 15 | 3 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 313 | 512 | 538 | 633 | 16 | 26 | 28 | 33 | 0.0014945 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 4850 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502002115 | 80 | 15 | 3 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 333 | 668 | 691 | 890 | 17 | 34 | 36 | 46 | 0.0026765 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395 | 416 | 601 | 0.85 | 0.85 | 0.85 | 321.7749 | 338.8819 | 489.5866 | 69 | 73 | 105 | 0.037607 | 0.041856 | 0.083611 | 5.3 | 6 | 6.7 | 9 |  | 5164 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 321.7749 | 338.8819 | 489.5866 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502201015 | 80 | 15 | 3 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2130.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0010147 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2367 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502201115 | 80 | 15 | 3 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2073.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 167 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001902 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3049 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502201515 | 80 | 15 | 3 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3052 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 398 | 407 | 510 | 13 | 21 | 21 | 26 | 0.0014638 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 3815 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502201615 | 80 | 15 | 3 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2839.68 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 229 | 670 | 683 | 829 | 12 | 35 | 35 | 43 | 0.0031831 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 365 | 380 | 555 | 0.95 | 0.95 | 0.95 | 290.2499 | 302.178 | 441.3389 | 62 | 65 | 95 | 0.073126 | 0.08008 | 0.1663 | 4.4 | 6 | 6.7 | 9 |  | 4176 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.2499 | 302.178 | 441.3389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502202015 | 80 | 15 | 3 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4268 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 344 | 545 | 571 | 670 | 18 | 28 | 29 | 35 | 0.0019415 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 5335 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502202115 | 80 | 15 | 3 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4544 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 366 | 708 | 726 | 930 | 19 | 37 | 37 | 48 | 0.0034561 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 407 | 424 | 619 | 0.85 | 0.85 | 0.85 | 331.5504 | 345.3989 | 504.2498 | 71 | 74 | 108 | 0.041246 | 0.044608 | 0.091399 | 5.9 | 6 | 6.7 | 9 |  | 5680 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 331.5504 | 345.3989 | 504.2498 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502401015 | 80 | 15 | 3 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2323.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0013125 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2582 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502401115 | 80 | 15 | 3 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2261.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 182 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0020427 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3326 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502401515 | 80 | 15 | 3 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 269 | 424 | 432 | 536 | 14 | 22 | 22 | 28 | 0.0017585 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4162 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502401615 | 80 | 15 | 3 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 250 | 723 | 734 | 881 | 13 | 37 | 38 | 45 | 0.0038405 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 388 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 308.5396 | 453.267 | 64 | 66 | 97 | 0.07985 | 0.084704 | 0.17746 | 4.8 | 6 | 6.7 | 9 |  | 4555 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 308.5396 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502402015 | 80 | 15 | 3 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 375 | 578 | 605 | 708 | 19 | 30 | 31 | 37 | 0.0022305 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 5820 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502402115 | 80 | 15 | 3 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 400 | 748 | 764 | 970 | 21 | 39 | 39 | 50 | 0.0043563 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 420 | 435 | 638 | 0.85 | 0.85 | 0.85 | 342.1404 | 354.3597 | 519.7276 | 74 | 76 | 112 | 0.046263 | 0.048652 | 0.10132 | 6.4 | 6 | 6.7 | 9 |  | 6197 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 342.1404 | 354.3597 | 519.7276 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502601015 | 80 | 15 | 3 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2518.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 203 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.001397 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 2798 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502601115 | 80 | 15 | 3 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2450.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 198 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0026367 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3604 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3502601515 | 60 | 15 | 3 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3606.4 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 291 | 407 | 412 | 482 | 15 | 21 | 21 | 25 | 0.0020868 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4508 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3502601615 | 60 | 15 | 3 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3355.8 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 271 | 729 | 736 | 836 | 14 | 38 | 38 | 43 | 0.0045725 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 310 | 455 | 0.95 | 0.95 | 0.95 | 237.7664 | 246.5136 | 361.8184 | 51 | 53 | 78 | 0.053124 | 0.057171 | 0.1197 | 5.2 | 6 | 6.7 | 9 |  | 4935 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 246.5136 | 361.8184 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502602015 | 60 | 15 | 3 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5044 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 407 | 560 | 579 | 649 | 21 | 29 | 30 | 33 | 0.0027893 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 6305 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3502602115 | 60 | 15 | 3 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5370.4 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 433 | 691 | 701 | 841 | 22 | 36 | 36 | 43 | 0.004956 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340 | 352 | 516 | 0.85 | 0.85 | 0.85 | 276.9708 | 286.7463 | 420.3439 | 60 | 62 | 90 | 0.032304 | 0.034357 | 0.069286 | 6.9 | 6 | 6.7 | 9 |  | 6713 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 276.9708 | 286.7463 | 420.3439 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502801015 | 60 | 15 | 3 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2711.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0017586 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3013 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3502801115 | 60 | 15 | 3 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2639.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.003327 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 3881 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3502801515 | 80 | 15 | 3 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 313 | 476 | 481 | 588 | 16 | 25 | 25 | 30 | 0.0024501 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 4855 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3502801615 | 80 | 15 | 3 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 291 | 827 | 834 | 986 | 15 | 43 | 43 | 51 | 0.005382 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 395 | 403 | 600 | 0.95 | 0.95 | 0.95 | 314.1061 | 320.4677 | 477.1231 | 68 | 69 | 103 | 0.094408 | 0.097076 | 0.20883 | 5.6 | 6 | 6.7 | 9 |  | 5314 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 314.1061 | 320.4677 | 477.1231 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3502802015 | 80 | 15 | 3 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 438 | 650 | 679 | 782 | 23 | 34 | 35 | 40 | 0.0034217 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 6790 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3502802115 | 80 | 15 | 3 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5784 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 466 | 829 | 838 | 1050 | 24 | 43 | 43 | 54 | 0.0060645 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 444 | 454 | 674 | 0.85 | 0.85 | 0.85 | 361.6913 | 369.8375 | 549.0539 | 78 | 80 | 118 | 0.054722 | 0.057387 | 0.11925 | 7.5 | 6 | 6.7 | 9 |  | 7230 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 361.6913 | 369.8375 | 549.0539 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3503001015 | 40 | 15 | 3 | 50 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2905.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 234 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0021728 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 3228 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3503001115 | 40 | 15 | 3 | 50 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2827.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 228 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0041193 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 4158 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3503001515 | 60 | 15 | 3 | 50 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4161.6 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 336 | 459 | 462 | 535 | 17 | 24 | 24 | 28 | 0.0028497 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 5202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3503001615 | 60 | 15 | 3 | 50 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3871.92 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 312 | 833 | 838 | 941 | 16 | 43 | 43 | 49 | 0.0062716 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 319 | 326 | 485 | 0.95 | 0.95 | 0.95 | 253.6705 | 259.2369 | 385.6745 | 55 | 56 | 83 | 0.06463 | 0.066882 | 0.14148 | 6 | 6 | 6.7 | 9 |  | 5694 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 253.6705 | 259.2369 | 385.6745 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3503002015 | 60 | 15 | 3 | 50 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5820 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 469 | 634 | 654 | 723 | 24 | 33 | 34 | 37 | 0.0038259 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 7275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3503002115 | 60 | 15 | 3 | 50 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6196.8 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 500 | 771 | 778 | 921 | 26 | 40 | 40 | 48 | 0.0073089 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 364 | 372 | 553 | 0.85 | 0.85 | 0.85 | 296.5217 | 303.0387 | 450.4849 | 64 | 65 | 97 | 0.039046 | 0.040194 | 0.085077 | 8 | 6 | 6.7 | 9 |  | 7746 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 296.5217 | 303.0387 | 450.4849 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
360601015 | 80 | 15 | 3 | 60 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 631.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 51 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 702 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360601115 | 80 | 15 | 3 | 60 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 609.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 49 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 896 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360601515 | 80 | 15 | 3 | 60 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 896 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1120 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360601615 | 80 | 15 | 3 | 60 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 850 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 69 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1250 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360602015 | 80 | 15 | 3 | 60 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1252 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00011049 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1565 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360602115 | 80 | 15 | 3 | 60 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1383.2 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 112 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1729 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360701015 | 80 | 15 | 3 | 60 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 737.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 59 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 819 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360701115 | 80 | 15 | 3 | 60 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 711.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1046 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360701515 | 70 | 15 | 3 | 60 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1044.8 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 84 | 193 | 208 | 275 | 4 | 10 | 11 | 14 | 9.7187e-05 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
360701615 | 70 | 15 | 3 | 60 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 992.12 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 80 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 252 | 271 | 358 | 0.95 | 0.95 | 0.95 | 200.3917 | 215.5006 | 284.6835 | 43 | 46 | 61 | 0.02821 | 0.032221 | 0.056221 | 1.4 | 6 | 6.7 | 9 |  | 1459 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 200.3917 | 215.5006 | 284.6835 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
360702015 | 70 | 15 | 3 | 60 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1460.8 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 118 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1826 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
360702115 | 70 | 15 | 3 | 60 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1613.6 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 130 | 383 | 411 | 544 | 7 | 20 | 21 | 28 | 0.00032624 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 275 | 295 | 391 | 0.85 | 0.85 | 0.85 | 224.0205 | 240.3129 | 318.5164 | 48 | 52 | 68 | 0.013794 | 0.016132 | 0.027279 | 1.9 | 6 | 6.7 | 9 |  | 2017 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.0205 | 240.3129 | 318.5164 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
360801015 | 80 | 15 | 3 | 60 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 842.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 936 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360801115 | 80 | 15 | 3 | 60 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 812.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 66 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00011928 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1195 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360801515 | 80 | 15 | 3 | 60 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1194.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360801615 | 80 | 15 | 3 | 60 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1133.56 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 91 | 322 | 345 | 463 | 5 | 17 | 18 | 24 | 0.00042712 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 297 | 318 | 427 | 0.95 | 0.95 | 0.95 | 236.1759 | 252.8753 | 339.5526 | 51 | 54 | 73 | 0.040209 | 0.044996 | 0.081472 | 1.6 | 6 | 6.7 | 9 |  | 1667 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.1759 | 252.8753 | 339.5526 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360802015 | 80 | 15 | 3 | 60 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1668.8 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 135 | 317 | 341 | 411 | 7 | 16 | 18 | 21 | 0.00022764 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2086 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360802115 | 80 | 15 | 3 | 60 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1844.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 149 | 451 | 484 | 649 | 8 | 23 | 25 | 33 | 0.00044029 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 324 | 347 | 466 | 0.85 | 0.85 | 0.85 | 263.9369 | 282.6732 | 379.6129 | 57 | 61 | 82 | 0.019835 | 0.022643 | 0.040361 | 2.1 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 263.9369 | 282.6732 | 379.6129 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360901015 | 80 | 15 | 3 | 60 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 947.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1053 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
360901115 | 80 | 15 | 3 | 60 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 914.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
360901515 | 80 | 15 | 3 | 60 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1343.2 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 108 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1679 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
360901615 | 80 | 15 | 3 | 60 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1275.68 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 103 | 344 | 366 | 489 | 5 | 18 | 19 | 25 | 0.00044021 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 298 | 319 | 434 | 0.95 | 0.95 | 0.95 | 236.9712 | 253.6705 | 345.1191 | 51 | 55 | 74 | 0.040926 | 0.047468 | 0.085049 | 1.8 | 6 | 6.7 | 9 |  | 1876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.9712 | 253.6705 | 345.1191 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
360902015 | 80 | 15 | 3 | 60 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1877.6 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 151 | 332 | 356 | 430 | 8 | 17 | 18 | 22 | 0.00030408 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2347 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
360902115 | 80 | 15 | 3 | 60 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2075.2 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 167 | 465 | 497 | 669 | 9 | 24 | 26 | 35 | 0.00057443 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 325 | 349 | 475 | 0.85 | 0.85 | 0.85 | 264.7515 | 284.3024 | 386.9445 | 57 | 61 | 83 | 0.020363 | 0.023236 | 0.042338 | 2.4 | 6 | 6.7 | 9 |  | 2594 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 264.7515 | 284.3024 | 386.9445 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601001015 | 80 | 15 | 3 | 60 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1053 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00013135 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1170 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601001115 | 80 | 15 | 3 | 60 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1015.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1494 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601001515 | 80 | 15 | 3 | 60 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1492.8 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 120 | 248 | 264 | 354 | 6 | 13 | 14 | 18 | 0.00023966 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1866 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601001615 | 80 | 15 | 3 | 60 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1417.12 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 114 | 366 | 388 | 516 | 6 | 19 | 20 | 27 | 0.00064483 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 299 | 320 | 441 | 0.95 | 0.95 | 0.95 | 237.7664 | 254.4657 | 350.6855 | 51 | 55 | 75 | 0.041644 | 0.048285 | 0.088719 | 2 | 6 | 6.7 | 9 |  | 2084 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 254.4657 | 350.6855 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601002015 | 80 | 15 | 3 | 60 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2086.4 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 168 | 348 | 372 | 448 | 9 | 18 | 19 | 23 | 0.00039308 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2608 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601002115 | 80 | 15 | 3 | 60 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2305.6 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 186 | 480 | 511 | 689 | 10 | 25 | 26 | 36 | 0.00072961 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 327 | 351 | 483 | 0.85 | 0.85 | 0.85 | 266.3808 | 285.9316 | 393.4615 | 57 | 61 | 85 | 0.020891 | 0.02383 | 0.0454 | 2.7 | 6 | 6.7 | 9 |  | 2882 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3808 | 285.9316 | 393.4615 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601101015 | 80 | 15 | 3 | 60 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1158.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 93 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1287 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601101115 | 80 | 15 | 3 | 60 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1117.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1643 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601101515 | 70 | 15 | 3 | 60 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1642.4 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 132 | 238 | 251 | 327 | 7 | 12 | 13 | 17 | 0.00033355 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3601101615 | 70 | 15 | 3 | 60 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1558.56 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 126 | 368 | 386 | 493 | 7 | 19 | 20 | 25 | 0.00089237 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 262 | 280 | 387 | 0.95 | 0.95 | 0.95 | 208.3438 | 222.6575 | 307.7444 | 45 | 48 | 66 | 0.033168 | 0.037627 | 0.070155 | 2.2 | 6 | 6.7 | 9 |  | 2292 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 222.6575 | 307.7444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3601102015 | 70 | 15 | 3 | 60 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2295.2 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 185 | 335 | 355 | 419 | 10 | 17 | 18 | 22 | 0.00049511 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 2869 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3601102115 | 70 | 15 | 3 | 60 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2536 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 205 | 449 | 475 | 625 | 11 | 23 | 25 | 32 | 0.00090675 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 288 | 309 | 426 | 0.85 | 0.85 | 0.85 | 234.6106 | 251.7176 | 347.0281 | 50 | 54 | 75 | 0.016626 | 0.019293 | 0.036441 | 2.9 | 6 | 6.7 | 9 |  | 3170 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 234.6106 | 251.7176 | 347.0281 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3601201015 | 80 | 15 | 3 | 60 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1263.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00022398 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1404 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601201115 | 80 | 15 | 3 | 60 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1219.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 98 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1793 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601201515 | 80 | 15 | 3 | 60 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1791.2 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 144 | 272 | 288 | 380 | 7 | 14 | 15 | 20 | 0.00034524 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2239 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601201615 | 80 | 15 | 3 | 60 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1700.68 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 137 | 415 | 437 | 568 | 7 | 21 | 23 | 29 | 0.00091576 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 306 | 327 | 456 | 0.95 | 0.95 | 0.95 | 243.3328 | 260.0321 | 362.6136 | 52 | 56 | 78 | 0.044743 | 0.051707 | 0.098805 | 2.4 | 6 | 6.7 | 9 |  | 2501 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 243.3328 | 260.0321 | 362.6136 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601202015 | 80 | 15 | 3 | 60 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2504 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 202 | 380 | 404 | 485 | 10 | 20 | 21 | 25 | 0.00050829 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3130 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601202115 | 80 | 15 | 3 | 60 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2766.4 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 223 | 516 | 547 | 729 | 12 | 27 | 28 | 38 | 0.0011067 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 336 | 360 | 501 | 0.85 | 0.85 | 0.85 | 273.7123 | 293.2632 | 408.1246 | 59 | 63 | 88 | 0.023457 | 0.026624 | 0.0508 | 3.2 | 6 | 6.7 | 9 |  | 3458 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 273.7123 | 293.2632 | 408.1246 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601401015 | 80 | 15 | 3 | 60 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1474.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00034823 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1638 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601401115 | 80 | 15 | 3 | 60 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1422.56 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00063987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2092 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601401515 | 80 | 15 | 3 | 60 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2089.6 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 169 | 296 | 312 | 406 | 9 | 15 | 16 | 21 | 0.00059309 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2612 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601401615 | 80 | 15 | 3 | 60 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1984.24 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 160 | 465 | 487 | 620 | 8 | 24 | 25 | 32 | 0.0012433 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 313 | 335 | 470 | 0.95 | 0.95 | 0.95 | 248.8992 | 266.3937 | 373.7464 | 54 | 57 | 80 | 0.049747 | 0.055264 | 0.10694 | 2.8 | 6 | 6.7 | 9 |  | 2918 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 248.8992 | 266.3937 | 373.7464 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601402015 | 80 | 15 | 3 | 60 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2920.8 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 236 | 412 | 437 | 522 | 12 | 21 | 23 | 27 | 0.00075811 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3651 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601402115 | 80 | 15 | 3 | 60 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3228 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 260 | 552 | 583 | 769 | 13 | 28 | 30 | 40 | 0.0013719 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345 | 369 | 518 | 0.85 | 0.85 | 0.85 | 281.0439 | 300.5948 | 421.9732 | 60 | 65 | 91 | 0.025384 | 0.029604 | 0.056568 | 3.7 | 6 | 6.7 | 9 |  | 4035 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.0439 | 300.5948 | 421.9732 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601601015 | 80 | 15 | 3 | 60 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1684.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 136 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00050754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1872 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601601115 | 80 | 15 | 3 | 60 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1625.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 131 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00093804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2390 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601601515 | 80 | 15 | 3 | 60 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.8 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 193 | 319 | 334 | 432 | 10 | 16 | 17 | 22 | 0.00076744 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 2986 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3601601615 | 80 | 15 | 3 | 60 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2267.12 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 183 | 513 | 534 | 672 | 9 | 26 | 28 | 35 | 0.0016307 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 318 | 340 | 484 | 0.95 | 0.95 | 0.95 | 252.8753 | 270.3698 | 384.8793 | 54 | 58 | 83 | 0.05133 | 0.058957 | 0.11822 | 3.2 | 6 | 6.7 | 9 |  | 3334 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 270.3698 | 384.8793 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601602015 | 80 | 15 | 3 | 60 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3338.4 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 269 | 445 | 471 | 559 | 14 | 23 | 24 | 29 | 0.001066 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 4173 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3601602115 | 80 | 15 | 3 | 60 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3688.8 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 297 | 587 | 616 | 809 | 15 | 30 | 32 | 42 | 0.0019054 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 352 | 376 | 536 | 0.85 | 0.85 | 0.85 | 286.7463 | 306.2971 | 436.6363 | 62 | 66 | 94 | 0.028255 | 0.031845 | 0.062716 | 4.3 | 6 | 6.7 | 9 |  | 4611 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 286.7463 | 306.2971 | 436.6363 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601801015 | 80 | 15 | 3 | 60 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1895.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 153 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00070519 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 2106 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3601801115 | 80 | 15 | 3 | 60 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1828.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 147 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0013098 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2689 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3601801515 | 60 | 15 | 3 | 60 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2687.2 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 217 | 302 | 312 | 378 | 11 | 16 | 16 | 20 | 0.00096969 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3359 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3601801615 | 60 | 15 | 3 | 60 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2550.68 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 206 | 520 | 534 | 627 | 11 | 27 | 28 | 32 | 0.0024957 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 246 | 263 | 375 | 0.95 | 0.95 | 0.95 | 195.6205 | 209.139 | 298.202 | 42 | 45 | 64 | 0.032579 | 0.037216 | 0.073483 | 3.6 | 6 | 6.7 | 9 |  | 3751 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 195.6205 | 209.139 | 298.202 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3601802015 | 60 | 15 | 3 | 60 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3755.2 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 303 | 423 | 441 | 501 | 16 | 22 | 23 | 26 | 0.0014352 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4694 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3601802115 | 60 | 15 | 3 | 60 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4150.4 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 335 | 530 | 549 | 680 | 17 | 27 | 28 | 35 | 0.002545 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 276 | 295 | 420 | 0.85 | 0.85 | 0.85 | 224.8351 | 240.3129 | 342.1404 | 48 | 52 | 74 | 0.018113 | 0.02109 | 0.041298 | 4.8 | 6 | 6.7 | 9 |  | 5188 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.8351 | 240.3129 | 342.1404 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602001015 | 80 | 15 | 3 | 60 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 2106 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 170 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00094435 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2340 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602001115 | 80 | 15 | 3 | 60 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 2031.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 164 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0014244 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 2988 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602001515 | 80 | 15 | 3 | 60 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2985.6 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 241 | 372 | 383 | 484 | 12 | 19 | 20 | 25 | 0.0012013 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3732 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602001615 | 80 | 15 | 3 | 60 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2834.24 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 229 | 618 | 634 | 777 | 12 | 32 | 33 | 40 | 0.0030647 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 337 | 355 | 513 | 0.95 | 0.95 | 0.95 | 267.9842 | 282.2978 | 407.9403 | 58 | 61 | 88 | 0.062539 | 0.068922 | 0.13981 | 4 | 6 | 6.7 | 9 |  | 4168 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267.9842 | 282.2978 | 407.9403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602002015 | 80 | 15 | 3 | 60 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4172.8 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 337 | 512 | 538 | 633 | 17 | 26 | 28 | 33 | 0.0016767 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 5216 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602002115 | 80 | 15 | 3 | 60 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4611.2 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 372 | 668 | 691 | 890 | 19 | 34 | 36 | 46 | 0.0032969 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 375 | 396 | 571 | 0.85 | 0.85 | 0.85 | 305.4825 | 322.5895 | 465.148 | 66 | 69 | 100 | 0.034563 | 0.037607 | 0.076185 | 5.3 | 6 | 6.7 | 9 |  | 5764 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 305.4825 | 322.5895 | 465.148 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602201015 | 80 | 15 | 3 | 60 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2316.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 187 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0012281 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2574 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602201115 | 80 | 15 | 3 | 60 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2235.16 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.001902 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3287 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602201515 | 80 | 15 | 3 | 60 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3284 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 265 | 398 | 407 | 510 | 14 | 21 | 21 | 26 | 0.0016812 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 4105 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602201615 | 80 | 15 | 3 | 60 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3117.8 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 251 | 670 | 683 | 829 | 13 | 35 | 35 | 43 | 0.0037045 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 347 | 361 | 527 | 0.95 | 0.95 | 0.95 | 275.9362 | 287.0691 | 419.0731 | 59 | 62 | 90 | 0.066478 | 0.073126 | 0.14983 | 4.4 | 6 | 6.7 | 9 |  | 4585 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 275.9362 | 287.0691 | 419.0731 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602202015 | 80 | 15 | 3 | 60 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4590.4 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 370 | 545 | 571 | 670 | 19 | 28 | 29 | 35 | 0.0021509 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 5738 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602202115 | 80 | 15 | 3 | 60 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5072 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 409 | 708 | 726 | 930 | 21 | 37 | 37 | 48 | 0.0041671 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 387 | 403 | 588 | 0.85 | 0.85 | 0.85 | 315.258 | 328.2919 | 478.9966 | 68 | 71 | 103 | 0.038009 | 0.041246 | 0.083526 | 5.9 | 6 | 6.7 | 9 |  | 6340 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 315.258 | 328.2919 | 478.9966 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602401015 | 80 | 15 | 3 | 60 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2527.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 204 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0015594 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2808 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602401115 | 80 | 15 | 3 | 60 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2438.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 197 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0024679 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3586 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602401515 | 80 | 15 | 3 | 60 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3582.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 289 | 424 | 432 | 536 | 15 | 22 | 22 | 28 | 0.0019998 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4478 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602401615 | 80 | 15 | 3 | 60 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3401.36 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 274 | 723 | 734 | 881 | 14 | 37 | 38 | 45 | 0.004418 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 356 | 369 | 541 | 0.95 | 0.95 | 0.95 | 283.0931 | 293.4307 | 430.206 | 61 | 63 | 92 | 0.07283 | 0.077476 | 0.16029 | 4.8 | 6 | 6.7 | 9 |  | 5002 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 283.0931 | 293.4307 | 430.206 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602402015 | 80 | 15 | 3 | 60 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5007.2 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 404 | 578 | 605 | 708 | 21 | 30 | 31 | 37 | 0.0026947 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 6259 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602402115 | 80 | 15 | 3 | 60 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5533.6 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 446 | 748 | 764 | 970 | 23 | 39 | 39 | 50 | 0.0051617 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 399 | 413 | 606 | 0.85 | 0.85 | 0.85 | 325.0334 | 336.4381 | 493.6597 | 70 | 72 | 106 | 0.041657 | 0.043931 | 0.091282 | 6.4 | 6 | 6.7 | 9 |  | 6917 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 325.0334 | 336.4381 | 493.6597 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602601015 | 80 | 15 | 3 | 60 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2737.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 221 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.001659 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 3042 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602601115 | 80 | 15 | 3 | 60 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2641.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 213 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0031278 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 3884 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3602601515 | 60 | 15 | 3 | 60 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3881.6 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 313 | 407 | 412 | 482 | 16 | 21 | 21 | 25 | 0.0023528 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 4852 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3602601615 | 60 | 15 | 3 | 60 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3684.24 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 297 | 729 | 736 | 836 | 15 | 38 | 38 | 43 | 0.005208 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 284 | 294 | 432 | 0.95 | 0.95 | 0.95 | 225.8383 | 233.7903 | 343.5286 | 49 | 50 | 74 | 0.04922 | 0.051154 | 0.10822 | 5.2 | 6 | 6.7 | 9 |  | 5418 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 233.7903 | 343.5286 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602602015 | 60 | 15 | 3 | 60 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5424.8 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 437 | 560 | 579 | 649 | 23 | 29 | 30 | 33 | 0.003311 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 6781 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3602602115 | 60 | 15 | 3 | 60 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5994.4 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 483 | 691 | 701 | 841 | 25 | 36 | 36 | 43 | 0.0062862 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 323 | 334 | 490 | 0.85 | 0.85 | 0.85 | 263.1223 | 272.0831 | 399.1638 | 57 | 58 | 86 | 0.029338 | 0.030312 | 0.063595 | 6.9 | 6 | 6.7 | 9 |  | 7493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 263.1223 | 272.0831 | 399.1638 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602801015 | 60 | 15 | 3 | 60 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 2948.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 238 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.002057 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3276 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3602801115 | 60 | 15 | 3 | 60 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 2844.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 229 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0038875 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 4183 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3602801515 | 80 | 15 | 3 | 60 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4180 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 337 | 476 | 481 | 588 | 17 | 25 | 25 | 30 | 0.0027417 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 5225 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3602801615 | 80 | 15 | 3 | 60 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3967.8 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 320 | 827 | 834 | 986 | 17 | 43 | 43 | 51 | 0.0068121 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 375 | 383 | 570 | 0.95 | 0.95 | 0.95 | 298.202 | 304.5636 | 453.267 | 64 | 65 | 97 | 0.084096 | 0.08662 | 0.18616 | 5.6 | 6 | 6.7 | 9 |  | 5835 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.202 | 304.5636 | 453.267 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3602802015 | 80 | 15 | 3 | 60 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5841.6 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 471 | 650 | 679 | 782 | 24 | 34 | 35 | 40 | 0.0037069 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 7302 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3602802115 | 80 | 15 | 3 | 60 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6456 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 521 | 829 | 838 | 1050 | 27 | 43 | 43 | 54 | 0.0075464 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 422 | 431 | 641 | 0.85 | 0.85 | 0.85 | 343.7697 | 351.1012 | 522.1714 | 74 | 75 | 112 | 0.049573 | 0.050838 | 0.10808 | 7.5 | 6 | 6.7 | 9 |  | 8070 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 343.7697 | 351.1012 | 522.1714 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3603001015 | 40 | 15 | 3 | 60 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3159 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 255 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0025092 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 3510 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3603001115 | 40 | 15 | 3 | 60 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 3047.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 246 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0047528 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 4482 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3603001515 | 60 | 15 | 3 | 60 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4478.4 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 361 | 459 | 462 | 535 | 19 | 24 | 24 | 28 | 0.0035014 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 5598 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3603001615 | 60 | 15 | 3 | 60 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4251.36 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 343 | 833 | 838 | 941 | 18 | 43 | 43 | 49 | 0.0078251 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 303 | 310 | 460 | 0.95 | 0.95 | 0.95 | 240.9472 | 246.5136 | 365.7944 | 52 | 53 | 79 | 0.058098 | 0.060238 | 0.12876 | 6 | 6 | 6.7 | 9 |  | 6252 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240.9472 | 246.5136 | 365.7944 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3603002015 | 60 | 15 | 3 | 60 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6259.2 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 505 | 634 | 654 | 723 | 26 | 33 | 34 | 37 | 0.0044462 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 7824 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3603002115 | 60 | 15 | 3 | 60 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6916.8 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 558 | 771 | 778 | 921 | 29 | 40 | 40 | 48 | 0.0089477 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 346 | 354 | 525 | 0.85 | 0.85 | 0.85 | 281.8585 | 288.3755 | 427.6755 | 61 | 62 | 92 | 0.035696 | 0.036797 | 0.077034 | 8 | 6 | 6.7 | 9 |  | 8646 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281.8585 | 288.3755 | 427.6755 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
370601015 | 80 | 15 | 3 | 70 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 674.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 54 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 749 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370601115 | 80 | 15 | 3 | 70 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 648.72 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 52 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 954 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370601515 | 80 | 15 | 3 | 70 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 946.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1183 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370601615 | 80 | 15 | 3 | 70 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 922.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1356 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370602015 | 80 | 15 | 3 | 70 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1321.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 107 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1652 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370602115 | 80 | 15 | 3 | 70 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1524.8 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 123 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.0002313 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1906 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370701015 | 80 | 15 | 3 | 70 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 786.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 63 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6.1482e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 874 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370701115 | 80 | 15 | 3 | 70 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 756.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0.00010882 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1113 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370701515 | 70 | 15 | 3 | 70 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1104 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 193 | 208 | 275 | 5 | 10 | 11 | 14 | 0.00014954 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1380 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
370701615 | 70 | 15 | 3 | 70 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1075.76 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 273 | 294 | 389 | 4 | 14 | 15 | 20 | 0.00026794 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 239 | 256 | 339 | 0.95 | 0.95 | 0.95 | 190.054 | 203.5725 | 269.5746 | 41 | 44 | 58 | 0.025683 | 0.029518 | 0.050896 | 1.4 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.054 | 203.5725 | 269.5746 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
370702015 | 70 | 15 | 3 | 70 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1541.6 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 124 | 269 | 288 | 345 | 6 | 14 | 15 | 18 | 0.00016328 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 1927 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
370702115 | 70 | 15 | 3 | 70 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1779.2 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 143 | 383 | 411 | 544 | 7 | 20 | 21 | 28 | 0.00032624 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 261 | 280 | 370 | 0.85 | 0.85 | 0.85 | 212.6158 | 228.0936 | 301.4094 | 46 | 49 | 65 | 0.012692 | 0.014361 | 0.024971 | 1.9 | 6 | 6.7 | 9 |  | 2224 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 212.6158 | 228.0936 | 301.4094 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
370801015 | 80 | 15 | 3 | 70 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 898.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 998 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370801115 | 80 | 15 | 3 | 70 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 864.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1272 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370801515 | 80 | 15 | 3 | 70 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1262.4 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 102 | 228 | 244 | 328 | 5 | 12 | 13 | 17 | 0.00015609 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1578 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370801615 | 80 | 15 | 3 | 70 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1229.44 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 99 | 322 | 345 | 463 | 5 | 17 | 18 | 24 | 0.00042712 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 281 | 302 | 405 | 0.95 | 0.95 | 0.95 | 223.4527 | 240.152 | 322.0581 | 48 | 52 | 69 | 0.035688 | 0.041775 | 0.072911 | 1.6 | 6 | 6.7 | 9 |  | 1808 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.4527 | 240.152 | 322.0581 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370802015 | 80 | 15 | 3 | 70 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1761.6 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 142 | 317 | 341 | 411 | 7 | 16 | 18 | 21 | 0.00022764 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370802115 | 80 | 15 | 3 | 70 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2033.6 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 164 | 451 | 484 | 649 | 8 | 23 | 25 | 33 | 0.00044029 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 307 | 329 | 441 | 0.85 | 0.85 | 0.85 | 250.0884 | 268.01 | 359.2474 | 54 | 58 | 77 | 0.01785 | 0.02052 | 0.03569 | 2.1 | 6 | 6.7 | 9 |  | 2542 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.0884 | 268.01 | 359.2474 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370901015 | 80 | 15 | 3 | 70 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 1010.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00012273 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1123 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
370901115 | 80 | 15 | 3 | 70 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 973.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 78 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1431 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
370901515 | 80 | 15 | 3 | 70 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1420 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 115 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1775 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
370901615 | 80 | 15 | 3 | 70 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1383.12 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 112 | 344 | 366 | 489 | 6 | 18 | 19 | 25 | 0.00062691 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 282 | 302 | 411 | 0.95 | 0.95 | 0.95 | 224.2479 | 240.152 | 326.8293 | 48 | 52 | 70 | 0.036334 | 0.042517 | 0.076246 | 1.8 | 6 | 6.7 | 9 |  | 2034 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.2479 | 240.152 | 326.8293 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
370902015 | 80 | 15 | 3 | 70 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1982.4 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 160 | 332 | 356 | 430 | 8 | 17 | 18 | 22 | 0.00030408 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2478 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
370902115 | 80 | 15 | 3 | 70 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2287.2 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 184 | 465 | 497 | 669 | 9 | 24 | 26 | 35 | 0.00057443 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 308 | 330 | 450 | 0.85 | 0.85 | 0.85 | 250.903 | 268.8246 | 366.579 | 54 | 58 | 79 | 0.018331 | 0.021064 | 0.038451 | 2.4 | 6 | 6.7 | 9 |  | 2859 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250.903 | 268.8246 | 366.579 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701001015 | 80 | 15 | 3 | 70 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1123.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 91 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1248 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701001115 | 80 | 15 | 3 | 70 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1081.2 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00023754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1590 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701001515 | 80 | 15 | 3 | 70 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1577.6 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 248 | 264 | 354 | 7 | 13 | 14 | 18 | 0.00032186 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 1972 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701001615 | 80 | 15 | 3 | 70 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1536.8 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 124 | 366 | 388 | 516 | 6 | 19 | 20 | 27 | 0.00064483 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 283 | 303 | 418 | 0.95 | 0.95 | 0.95 | 225.0431 | 240.9472 | 332.3958 | 48 | 52 | 71 | 0.036981 | 0.043259 | 0.079671 | 2 | 6 | 6.7 | 9 |  | 2260 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.0431 | 240.9472 | 332.3958 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701002015 | 80 | 15 | 3 | 70 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2202.4 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 178 | 348 | 372 | 448 | 9 | 18 | 19 | 23 | 0.00039308 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2753 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701002115 | 80 | 15 | 3 | 70 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2541.6 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 205 | 480 | 511 | 689 | 11 | 25 | 26 | 36 | 0.00087568 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 310 | 332 | 458 | 0.85 | 0.85 | 0.85 | 252.5322 | 270.4539 | 373.096 | 54 | 58 | 80 | 0.018812 | 0.021608 | 0.040352 | 2.7 | 6 | 6.7 | 9 |  | 3177 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.5322 | 270.4539 | 373.096 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701101015 | 80 | 15 | 3 | 70 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1235.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 100 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00021129 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1373 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701101115 | 80 | 15 | 3 | 70 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1189.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1749 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701101515 | 70 | 15 | 3 | 70 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1735.2 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 140 | 238 | 251 | 327 | 7 | 12 | 13 | 17 | 0.00033355 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2169 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3701101615 | 70 | 15 | 3 | 70 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1690.48 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 136 | 368 | 386 | 493 | 7 | 19 | 20 | 25 | 0.00089237 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 248 | 266 | 366 | 0.95 | 0.95 | 0.95 | 197.2109 | 211.5246 | 291.0451 | 42 | 45 | 63 | 0.028986 | 0.033168 | 0.064049 | 2.2 | 6 | 6.7 | 9 |  | 2486 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 197.2109 | 211.5246 | 291.0451 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3701102015 | 70 | 15 | 3 | 70 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2422.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 195 | 335 | 355 | 419 | 10 | 17 | 18 | 22 | 0.00049511 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 3028 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3701102115 | 70 | 15 | 3 | 70 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2796 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 225 | 449 | 475 | 625 | 12 | 23 | 25 | 32 | 0.0010707 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 273 | 293 | 403 | 0.85 | 0.85 | 0.85 | 222.3913 | 238.6837 | 328.2919 | 48 | 51 | 71 | 0.015365 | 0.017274 | 0.032769 | 2.9 | 6 | 6.7 | 9 |  | 3495 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 222.3913 | 238.6837 | 328.2919 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3701201015 | 80 | 15 | 3 | 70 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1348.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1498 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701201115 | 80 | 15 | 3 | 70 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1297.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00040866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 1908 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701201515 | 80 | 15 | 3 | 70 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1892.8 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 153 | 272 | 288 | 380 | 8 | 14 | 15 | 20 | 0.00044509 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701201615 | 80 | 15 | 3 | 70 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.16 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 149 | 415 | 437 | 568 | 8 | 21 | 23 | 29 | 0.0011844 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 290 | 310 | 432 | 0.95 | 0.95 | 0.95 | 230.6095 | 246.5136 | 343.5286 | 50 | 53 | 74 | 0.041446 | 0.046438 | 0.089139 | 2.4 | 6 | 6.7 | 9 |  | 2712 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 230.6095 | 246.5136 | 343.5286 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701202015 | 80 | 15 | 3 | 70 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2643.2 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 213 | 380 | 404 | 485 | 11 | 20 | 21 | 25 | 0.00061062 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3304 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701202115 | 80 | 15 | 3 | 70 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3049.6 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 246 | 516 | 547 | 729 | 13 | 27 | 28 | 38 | 0.001289 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 318 | 341 | 474 | 0.85 | 0.85 | 0.85 | 259.0492 | 277.7854 | 386.1299 | 56 | 60 | 83 | 0.02121 | 0.024231 | 0.045363 | 3.2 | 6 | 6.7 | 9 |  | 3812 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 259.0492 | 277.7854 | 386.1299 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701401015 | 80 | 15 | 3 | 70 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1572.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 127 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1747 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701401115 | 80 | 15 | 3 | 70 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1513.68 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 122 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00063987 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2226 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701401515 | 80 | 15 | 3 | 70 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2208.8 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 178 | 296 | 312 | 406 | 9 | 15 | 16 | 21 | 0.00059309 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2761 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701401615 | 80 | 15 | 3 | 70 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2151.52 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 465 | 487 | 620 | 9 | 24 | 25 | 32 | 0.0015586 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 296 | 317 | 445 | 0.95 | 0.95 | 0.95 | 235.3807 | 252.08 | 353.8663 | 51 | 54 | 76 | 0.044514 | 0.049747 | 0.096765 | 2.8 | 6 | 6.7 | 9 |  | 3164 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 235.3807 | 252.08 | 353.8663 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701402015 | 80 | 15 | 3 | 70 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3083.2 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 249 | 412 | 437 | 522 | 13 | 21 | 23 | 27 | 0.00088388 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 3854 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701402115 | 80 | 15 | 3 | 70 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3558.4 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 287 | 552 | 583 | 769 | 15 | 28 | 30 | 40 | 0.0017995 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 327 | 350 | 491 | 0.85 | 0.85 | 0.85 | 266.3808 | 285.117 | 399.9784 | 57 | 61 | 86 | 0.023003 | 0.026203 | 0.050733 | 3.7 | 6 | 6.7 | 9 |  | 4448 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 266.3808 | 285.117 | 399.9784 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701601015 | 80 | 15 | 3 | 70 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1797.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 145 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00050754 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1997 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701601115 | 80 | 15 | 3 | 70 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1729.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 140 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00093804 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2544 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701601515 | 80 | 15 | 3 | 70 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2524 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 204 | 319 | 334 | 432 | 11 | 16 | 17 | 22 | 0.00091872 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 3155 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3701601615 | 80 | 15 | 3 | 70 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2458.88 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 198 | 513 | 534 | 672 | 10 | 26 | 28 | 35 | 0.0019946 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 301 | 322 | 459 | 0.95 | 0.95 | 0.95 | 239.3568 | 256.0561 | 364.9992 | 51 | 55 | 78 | 0.045949 | 0.053189 | 0.10478 | 3.2 | 6 | 6.7 | 9 |  | 3616 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 239.3568 | 256.0561 | 364.9992 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701602015 | 80 | 15 | 3 | 70 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3524 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 284 | 445 | 471 | 559 | 15 | 23 | 24 | 29 | 0.0012162 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 4405 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3701602115 | 80 | 15 | 3 | 70 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4066.4 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 328 | 587 | 616 | 809 | 17 | 30 | 32 | 42 | 0.0024135 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 334 | 356 | 508 | 0.85 | 0.85 | 0.85 | 272.0831 | 290.0047 | 413.827 | 58 | 62 | 89 | 0.024872 | 0.028255 | 0.056471 | 4.3 | 6 | 6.7 | 9 |  | 5083 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 272.0831 | 290.0047 | 413.827 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701801015 | 80 | 15 | 3 | 70 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 2021.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 163 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00070519 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 2246 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3701801115 | 80 | 15 | 3 | 70 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1946.16 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0013098 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 2862 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3701801515 | 60 | 15 | 3 | 70 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2840 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 229 | 302 | 312 | 378 | 12 | 16 | 16 | 20 | 0.0011421 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3550 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3701801615 | 60 | 15 | 3 | 70 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2766.24 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 223 | 520 | 534 | 627 | 12 | 27 | 28 | 32 | 0.0029462 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 233 | 249 | 355 | 0.95 | 0.95 | 0.95 | 185.2828 | 198.0061 | 282.2978 | 40 | 43 | 61 | 0.029655 | 0.034092 | 0.066968 | 3.6 | 6 | 6.7 | 9 |  | 4068 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 185.2828 | 198.0061 | 282.2978 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3701802015 | 60 | 15 | 3 | 70 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3964 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 320 | 423 | 441 | 501 | 17 | 22 | 23 | 26 | 0.001611 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 4955 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3701802115 | 60 | 15 | 3 | 70 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4575.2 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 369 | 530 | 549 | 680 | 19 | 27 | 28 | 35 | 0.0031376 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 262 | 279 | 398 | 0.85 | 0.85 | 0.85 | 213.4304 | 227.279 | 324.2188 | 46 | 49 | 70 | 0.016707 | 0.018837 | 0.037145 | 4.8 | 6 | 6.7 | 9 |  | 5719 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 213.4304 | 227.279 | 324.2188 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702001015 | 80 | 15 | 3 | 70 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 2246.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 181 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00094435 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2496 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702001115 | 80 | 15 | 3 | 70 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 2162.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0017614 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 3180 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702001515 | 80 | 15 | 3 | 70 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3155.2 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 254 | 372 | 383 | 484 | 13 | 19 | 20 | 25 | 0.0013958 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 3944 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702001615 | 80 | 15 | 3 | 70 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3073.6 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 248 | 618 | 634 | 777 | 13 | 32 | 33 | 40 | 0.0035686 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 319 | 336 | 486 | 0.95 | 0.95 | 0.95 | 253.6705 | 267.1889 | 386.4697 | 55 | 57 | 83 | 0.056458 | 0.060479 | 0.12487 | 4 | 6 | 6.7 | 9 |  | 4520 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 253.6705 | 267.1889 | 386.4697 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702002015 | 80 | 15 | 3 | 70 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4404.8 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 355 | 512 | 538 | 633 | 18 | 26 | 28 | 33 | 0.001869 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 5506 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702002115 | 80 | 15 | 3 | 70 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 5083.2 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 410 | 668 | 691 | 890 | 21 | 34 | 36 | 46 | 0.0039779 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 356 | 375 | 541 | 0.85 | 0.85 | 0.85 | 290.0047 | 305.4825 | 440.7094 | 62 | 66 | 95 | 0.030695 | 0.034563 | 0.069092 | 5.3 | 6 | 6.7 | 9 |  | 6354 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 290.0047 | 305.4825 | 440.7094 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702201015 | 80 | 15 | 3 | 70 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2471.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 199 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0012281 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 2746 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702201115 | 80 | 15 | 3 | 70 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2378.64 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 192 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.002299 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3498 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702201515 | 80 | 15 | 3 | 70 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3470.4 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 280 | 398 | 407 | 510 | 14 | 21 | 21 | 26 | 0.0016812 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 4338 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702201615 | 80 | 15 | 3 | 70 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3380.96 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 273 | 670 | 683 | 829 | 14 | 35 | 35 | 43 | 0.0042635 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 328 | 342 | 499 | 0.95 | 0.95 | 0.95 | 260.8273 | 271.9602 | 396.8074 | 56 | 58 | 85 | 0.060138 | 0.064331 | 0.13421 | 4.4 | 6 | 6.7 | 9 |  | 4972 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 260.8273 | 271.9602 | 396.8074 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702202015 | 80 | 15 | 3 | 70 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4845.6 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 391 | 545 | 571 | 670 | 20 | 28 | 29 | 35 | 0.0023704 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 6057 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702202115 | 80 | 15 | 3 | 70 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5591.2 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 451 | 708 | 726 | 930 | 23 | 37 | 37 | 48 | 0.0049404 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 367 | 382 | 557 | 0.85 | 0.85 | 0.85 | 298.9656 | 311.1849 | 453.7434 | 64 | 67 | 98 | 0.033891 | 0.036958 | 0.075993 | 5.9 | 6 | 6.7 | 9 |  | 6989 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298.9656 | 311.1849 | 453.7434 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702401015 | 80 | 15 | 3 | 70 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2695.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 217 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0015594 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2995 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702401115 | 80 | 15 | 3 | 70 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2594.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 209 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0029285 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 3816 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702401515 | 80 | 15 | 3 | 70 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3786.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 305 | 424 | 432 | 536 | 16 | 22 | 22 | 28 | 0.0022556 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 4733 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702401615 | 80 | 15 | 3 | 70 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3688.32 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 297 | 723 | 734 | 881 | 15 | 37 | 38 | 45 | 0.005034 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 337 | 350 | 513 | 0.95 | 0.95 | 0.95 | 267.9842 | 278.3218 | 407.9403 | 58 | 60 | 88 | 0.066122 | 0.070559 | 0.14716 | 4.8 | 6 | 6.7 | 9 |  | 5424 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267.9842 | 278.3218 | 407.9403 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702402015 | 80 | 15 | 3 | 70 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5285.6 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 426 | 578 | 605 | 708 | 22 | 30 | 31 | 37 | 0.0029424 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 6607 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702402115 | 80 | 15 | 3 | 70 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6100 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 492 | 748 | 764 | 970 | 25 | 39 | 39 | 50 | 0.0060308 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 378 | 391 | 574 | 0.85 | 0.85 | 0.85 | 307.9264 | 318.5164 | 467.5919 | 66 | 68 | 101 | 0.037281 | 0.03944 | 0.083299 | 6.4 | 6 | 6.7 | 9 |  | 7625 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 307.9264 | 318.5164 | 467.5919 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702601015 | 80 | 15 | 3 | 70 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2920.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 236 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0019411 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 3245 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702601115 | 80 | 15 | 3 | 70 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2811.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 227 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0036558 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 4134 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3702601515 | 60 | 15 | 3 | 70 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4101.6 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 331 | 407 | 412 | 482 | 17 | 21 | 21 | 25 | 0.0026338 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 5127 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3702601615 | 60 | 15 | 3 | 70 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3995.68 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 322 | 729 | 736 | 836 | 17 | 38 | 38 | 43 | 0.0065962 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 269 | 279 | 409 | 0.95 | 0.95 | 0.95 | 213.9102 | 221.8623 | 325.2389 | 46 | 48 | 70 | 0.043632 | 0.047321 | 0.097302 | 5.2 | 6 | 6.7 | 9 |  | 5876 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 213.9102 | 221.8623 | 325.2389 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702602015 | 60 | 15 | 3 | 70 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5726.4 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 462 | 560 | 579 | 649 | 24 | 29 | 30 | 33 | 0.0035878 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 7158 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3702602115 | 60 | 15 | 3 | 70 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6608 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 533 | 691 | 701 | 841 | 28 | 36 | 36 | 43 | 0.0077634 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 306 | 317 | 465 | 0.85 | 0.85 | 0.85 | 249.2737 | 258.2346 | 378.7983 | 54 | 56 | 81 | 0.026508 | 0.02838 | 0.056808 | 6.9 | 6 | 6.7 | 9 |  | 8260 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 249.2737 | 258.2346 | 378.7983 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702801015 | 60 | 15 | 3 | 70 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3144.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 254 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0023761 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3494 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3702801115 | 60 | 15 | 3 | 70 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 3027.36 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 244 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0044866 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 4452 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3702801515 | 80 | 15 | 3 | 70 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4417.6 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 356 | 476 | 481 | 588 | 18 | 25 | 25 | 30 | 0.0030486 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 5522 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3702801615 | 80 | 15 | 3 | 70 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4303.04 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 347 | 827 | 834 | 986 | 18 | 43 | 43 | 51 | 0.0075868 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 355 | 363 | 540 | 0.95 | 0.95 | 0.95 | 282.2978 | 288.6595 | 429.4108 | 61 | 62 | 92 | 0.076738 | 0.079154 | 0.16822 | 5.6 | 6 | 6.7 | 9 |  | 6328 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 282.2978 | 288.6595 | 429.4108 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3702802015 | 80 | 15 | 3 | 70 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6166.4 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 497 | 650 | 679 | 782 | 26 | 34 | 35 | 40 | 0.0043096 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 7708 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3702802115 | 80 | 15 | 3 | 70 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 7116.8 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 574 | 829 | 838 | 1050 | 30 | 43 | 43 | 54 | 0.0091785 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 400 | 408 | 607 | 0.85 | 0.85 | 0.85 | 325.848 | 332.365 | 494.4744 | 70 | 71 | 106 | 0.044665 | 0.045869 | 0.097428 | 7.5 | 6 | 6.7 | 9 |  | 8896 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 325.848 | 332.365 | 494.4744 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3703001015 | 40 | 15 | 3 | 70 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3369.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 272 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0028672 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 3744 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3703001115 | 40 | 15 | 3 | 70 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 3243.6 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 262 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0054262 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 4770 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3703001515 | 60 | 15 | 3 | 70 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4732.8 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 382 | 459 | 462 | 535 | 20 | 24 | 24 | 28 | 0.0038506 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 5916 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3703001615 | 60 | 15 | 3 | 70 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4610.4 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 372 | 833 | 838 | 941 | 19 | 43 | 43 | 49 | 0.0086626 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 287 | 293 | 436 | 0.95 | 0.95 | 0.95 | 228.2239 | 232.9951 | 346.7095 | 49 | 50 | 75 | 0.051899 | 0.053928 | 0.11662 | 6 | 6 | 6.7 | 9 |  | 6780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 228.2239 | 232.9951 | 346.7095 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3703002015 | 60 | 15 | 3 | 70 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6607.2 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 533 | 634 | 654 | 723 | 28 | 33 | 34 | 37 | 0.0051104 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 8259 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3703002115 | 60 | 15 | 3 | 70 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 7624.8 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 615 | 771 | 778 | 921 | 32 | 40 | 40 | 48 | 0.01074 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 328 | 335 | 498 | 0.85 | 0.85 | 0.85 | 267.1954 | 272.8977 | 405.6808 | 57 | 59 | 87 | 0.03145 | 0.033542 | 0.06937 | 8 | 6 | 6.7 | 9 |  | 9531 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267.1954 | 272.8977 | 405.6808 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
390601015 | 80 | 15 | 3 | 90 | 60 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 738.9 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 60 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5.6252e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 821 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390601115 | 80 | 15 | 3 | 90 | 60 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 717.4 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 58 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 9.8355e-05 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1055 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390601515 | 80 | 15 | 3 | 90 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1017.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9.2732e-05 | 0 | 0 | 0 | 0.0002083 | 1.724 | 2 | 0.00046183 | 0 | 0 | 0 | 1.01 | 1.01 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1272 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390601615 | 80 | 15 | 3 | 90 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1059.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00025902 | 0 | 0 | 0 | 0.0002083 | 1.724 | 4 | 0.0013928 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1558 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390602015 | 80 | 15 | 3 | 90 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1419.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 114 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00015781 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1774 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390602115 | 80 | 15 | 3 | 90 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1809.6 | 0 | 0 | 0 | 1.5 | 1.05 | 1.05 | 1.05 | 146 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00040438 | 0 | 0 | 0 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 0 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 2262 |  | 80% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390701015 | 80 | 15 | 3 | 90 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41.1 | 862.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.0001055 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 958 |  | 90% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390701115 | 80 | 15 | 3 | 90 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41.1 | 837.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00018585 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1231 |  | 68% |  |  | 0 | DBH-unit is te lang! | DBH-unit is te lang! | DBH-unit is te lang! |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390701515 | 70 | 15 | 3 | 90 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 1187.2 | 1185 | 1272 | 1684 | 1.5 | 1.08 | 1.08 | 1.08 | 96 | 193 | 208 | 275 | 5 | 10 | 11 | 14 | 0.00014954 | 0.00057282 | 0.00068934 | 0.0011018 | 0.0002083 | 1.724 | 2 | 0.00046183 | 162 | 174 | 230 | 1.01 | 1.01 | 1.01 | 126.9722 | 136.3776 | 180.2692 | 27 | 29 | 39 | 0.0039657 | 0.00456 | 0.00814 | 0.7 | 6 | 6.7 | 9 |  | 1484 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 126.9722 | 136.3776 | 180.2692 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
390701615 | 70 | 15 | 3 | 90 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1235.56 | 1733 | 1860 | 2462 | 1.5 | 1.1 | 1.1 | 1.1 | 100 | 273 | 294 | 389 | 5 | 14 | 15 | 20 | 0.00041403 | 0.0031048 | 0.0035549 | 0.0062541 | 0.0002083 | 1.724 | 4 | 0.0013928 | 212 | 228 | 302 | 0.95 | 0.95 | 0.95 | 168.5835 | 181.3068 | 240.152 | 36 | 39 | 52 | 0.019878 | 0.023273 | 0.041033 | 1.4 | 6 | 6.7 | 9 |  | 1817 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 168.5835 | 181.3068 | 240.152 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
390702015 | 70 | 15 | 3 | 90 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1656 | 1647 | 1767 | 2112 | 1.5 | 1.08 | 1.08 | 1.08 | 134 | 269 | 288 | 345 | 7 | 14 | 15 | 18 | 0.00022051 | 0.00085422 | 0.00097776 | 0.0013975 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 204 | 218 | 261 | 0.95 | 0.95 | 0.95 | 162.2219 | 173.3547 | 207.5486 | 35 | 37 | 45 | 0.005155 | 0.0057501 | 0.0084507 | 0.9 | 6 | 6.7 | 9 |  | 2070 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 162.2219 | 173.3547 | 207.5486 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
390702115 | 70 | 15 | 3 | 90 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 2111.2 | 2232 | 2396 | 3171 | 1.5 | 1.05 | 1.05 | 1.05 | 170 | 383 | 411 | 544 | 9 | 20 | 21 | 28 | 0.00053044 | 0.0024992 | 0.0027482 | 0.0048138 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 232 | 249 | 329 | 0.85 | 0.85 | 0.85 | 188.9918 | 202.8404 | 268.01 | 41 | 44 | 58 | 0.010135 | 0.011635 | 0.019976 | 1.9 | 6 | 6.7 | 9 |  | 2639 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 188.9918 | 202.8404 | 268.01 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
390801015 | 80 | 15 | 3 | 90 | 80 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 985.5 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 79 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00011412 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 6 | 6.7 | 9 |  | 1095 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390801115 | 80 | 15 | 3 | 90 | 80 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 956.08 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 77 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00020308 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 1406 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390801515 | 80 | 15 | 3 | 90 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1356.8 | 1395 | 1496 | 2008 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 228 | 244 | 328 | 6 | 12 | 13 | 17 | 0.00022173 | 0.00084598 | 0.00098787 | 0.0016621 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190 | 204 | 274 | 1.01 | 1.01 | 1.01 | 148.918 | 159.8909 | 214.7555 | 32 | 34 | 46 | 0.0056883 | 0.0064018 | 0.011547 | 0.8 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 148.918 | 159.8909 | 214.7555 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390801615 | 80 | 15 | 3 | 90 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1412.36 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 114 | 322 | 345 | 463 | 6 | 17 | 18 | 24 | 0.00060898 | 0.0046529 | 0.005204 | 0.0091455 | 0.0002083 | 1.724 | 4 | 0.0013928 | 250 | 268 | 360 | 0.95 | 0.95 | 0.95 | 198.8013 | 213.115 | 286.2739 | 43 | 46 | 62 | 0.028745 | 0.032822 | 0.059059 | 1.6 | 6 | 6.7 | 9 |  | 2077 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.8013 | 213.115 | 286.2739 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.84525 | 0.7893 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390802015 | 80 | 15 | 3 | 90 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1892.8 | 1943 | 2086 | 2518 | 1.5 | 1.08 | 1.08 | 1.08 | 153 | 317 | 341 | 411 | 8 | 16 | 18 | 21 | 0.0002951 | 0.0011391 | 0.0014338 | 0.0019379 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240 | 258 | 311 | 0.95 | 0.95 | 0.95 | 190.8492 | 205.1629 | 247.3088 | 41 | 44 | 53 | 0.0071861 | 0.0082542 | 0.011895 | 1.1 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.8492 | 205.1629 | 247.3088 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390802115 | 80 | 15 | 3 | 90 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2412.8 | 2628 | 2818 | 3781 | 1.5 | 1.05 | 1.05 | 1.05 | 195 | 451 | 484 | 649 | 10 | 23 | 25 | 33 | 0.00067687 | 0.0033915 | 0.0039873 | 0.006839 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 273 | 292 | 392 | 0.85 | 0.85 | 0.85 | 222.3913 | 237.869 | 319.3311 | 48 | 51 | 69 | 0.014186 | 0.015966 | 0.028804 | 2.1 | 6 | 6.7 | 9 |  | 3016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 222.3913 | 237.869 | 319.3311 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390901015 | 80 | 15 | 3 | 90 | 90 | 10 | 11.5 | 0 | 26 | 30 | 43.3 | 1108.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 89 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00018592 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6 | 6.7 | 9 |  | 1232 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.84525 | 0.7893 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
390901115 | 80 | 15 | 3 | 90 | 90 | 11 | 11.5 | 0 | 26 | 30 | 43.3 | 1075.76 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 87 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.00022031 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 1582 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
390901515 | 80 | 15 | 3 | 90 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1526.4 | 1487 | 1593 | 2169 | 1.5 | 1.08 | 1.08 | 1.08 | 123 | 238 | 254 | 341 | 6 | 12 | 13 | 18 | 0.0002307 | 0.00087559 | 0.0010219 | 0.0019168 | 0.0002083 | 1.724 | 2 | 0.00046183 | 192 | 206 | 280 | 1.01 | 1.01 | 1.01 | 150.4856 | 161.4585 | 219.4582 | 32 | 35 | 47 | 0.0058489 | 0.0069615 | 0.012354 | 0.9 | 6 | 6.7 | 9 |  | 1908 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 150.4856 | 161.4585 | 219.4582 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
390901615 | 80 | 15 | 3 | 90 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1588.48 | 2234 | 2393 | 3260 | 1.5 | 1.1 | 1.1 | 1.1 | 128 | 344 | 366 | 489 | 7 | 18 | 19 | 25 | 0.00084561 | 0.0053231 | 0.0059161 | 0.010118 | 0.0002083 | 1.724 | 4 | 0.0013928 | 251 | 268 | 366 | 0.95 | 0.95 | 0.95 | 199.5965 | 213.115 | 291.0451 | 43 | 46 | 63 | 0.02928 | 0.033423 | 0.061983 | 1.8 | 6 | 6.7 | 9 |  | 2336 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 199.5965 | 213.115 | 291.0451 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.8364 | 0.77994 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
390902015 | 80 | 15 | 3 | 90 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2128.8 | 2098 | 2257 | 2748 | 1.5 | 1.08 | 1.08 | 1.08 | 172 | 332 | 356 | 430 | 9 | 17 | 18 | 22 | 0.00038208 | 0.0013151 | 0.00147 | 0.0021737 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 244 | 262 | 319 | 0.95 | 0.95 | 0.95 | 194.0301 | 208.3438 | 253.6705 | 42 | 45 | 55 | 0.0076901 | 0.0088021 | 0.013041 | 1.2 | 6 | 6.7 | 9 |  | 2661 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 194.0301 | 208.3438 | 253.6705 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.75556 | 0.70384 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
390902115 | 80 | 15 | 3 | 90 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2714.4 | 2762 | 2959 | 4030 | 1.5 | 1.05 | 1.05 | 1.05 | 219 | 465 | 497 | 669 | 11 | 24 | 26 | 35 | 0.00084461 | 0.0038026 | 0.0044395 | 0.0078964 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 274 | 293 | 400 | 0.85 | 0.85 | 0.85 | 223.2059 | 238.6837 | 325.848 | 48 | 51 | 70 | 0.014579 | 0.016402 | 0.030377 | 2.4 | 6 | 6.7 | 9 |  | 3393 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 223.2059 | 238.6837 | 325.848 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.75556 | 0.70384 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901001015 | 80 | 15 | 3 | 90 | 100 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1232.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.0001986 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1369 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.8364 | 0.77994 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901001115 | 80 | 15 | 3 | 90 | 100 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1195.44 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 96 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00035791 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 1758 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.75556 | 0.70384 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901001515 | 80 | 15 | 3 | 90 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1696 | 1579 | 1691 | 2331 | 1.5 | 1.08 | 1.08 | 1.08 | 137 | 248 | 264 | 354 | 7 | 13 | 14 | 18 | 0.00032186 | 0.0010559 | 0.0012177 | 0.0019763 | 0.0002083 | 1.724 | 2 | 0.00046183 | 194 | 208 | 287 | 1.01 | 1.01 | 1.01 | 152.0531 | 163.0261 | 224.9446 | 33 | 35 | 48 | 0.0063786 | 0.007149 | 0.013194 | 1 | 6 | 6.7 | 9 |  | 2120 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 152.0531 | 163.0261 | 224.9446 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901001615 | 80 | 15 | 3 | 90 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1765.28 | 2428 | 2599 | 3583 | 1.5 | 1.1 | 1.1 | 1.1 | 142 | 366 | 388 | 516 | 7 | 19 | 20 | 27 | 0.00086899 | 0.0060469 | 0.0066828 | 0.012002 | 0.0002083 | 1.724 | 4 | 0.0013928 | 252 | 270 | 372 | 0.95 | 0.95 | 0.95 | 200.3917 | 214.7054 | 295.8163 | 43 | 46 | 64 | 0.029814 | 0.034023 | 0.064992 | 2 | 6 | 6.7 | 9 |  | 2596 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 200.3917 | 214.7054 | 295.8163 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82846 | 0.77134 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901002015 | 80 | 15 | 3 | 90 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2365.6 | 2252 | 2426 | 2978 | 1.5 | 1.08 | 1.08 | 1.08 | 191 | 348 | 372 | 448 | 10 | 18 | 19 | 23 | 0.00048192 | 0.0015063 | 0.0016731 | 0.0024259 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 247 | 266 | 327 | 0.95 | 0.95 | 0.95 | 196.4157 | 211.5246 | 260.0321 | 42 | 45 | 56 | 0.0078461 | 0.0089778 | 0.013766 | 1.3 | 6 | 6.7 | 9 |  | 2957 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 196.4157 | 211.5246 | 260.0321 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.74531 | 0.69504 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901002115 | 80 | 15 | 3 | 90 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3016 | 2899 | 3104 | 4279 | 1.5 | 1.05 | 1.05 | 1.05 | 243 | 480 | 511 | 689 | 13 | 25 | 26 | 36 | 0.0012062 | 0.0042427 | 0.0045761 | 0.0085791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 276 | 295 | 407 | 0.85 | 0.85 | 0.85 | 224.8351 | 240.3129 | 331.5504 | 48 | 52 | 71 | 0.014972 | 0.017484 | 0.031999 | 2.7 | 6 | 6.7 | 9 |  | 3770 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 224.8351 | 240.3129 | 331.5504 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.74531 | 0.69504 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901101015 | 80 | 15 | 3 | 90 | 110 | 10 | 11.5 | 0 | 26 | 30 | 44.1 | 1355.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 109 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00029601 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 6 | 6.7 | 9 |  | 1506 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82846 | 0.77134 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901101115 | 80 | 15 | 3 | 90 | 110 | 11 | 11.5 | 0 | 26 | 30 | 44.1 | 1315.12 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 106 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0.00038328 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 1934 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.74531 | 0.69504 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901101515 | 70 | 15 | 3 | 90 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1865.6 | 1578 | 1690 | 2330 | 1.5 | 1.08 | 1.08 | 1.08 | 150 | 238 | 251 | 327 | 8 | 12 | 13 | 17 | 0.00043037 | 0.00093481 | 0.0010898 | 0.001824 | 0.0002083 | 1.724 | 2 | 0.00046183 | 173 | 185 | 255 | 1.01 | 1.01 | 1.01 | 135.5938 | 144.9991 | 199.8637 | 29 | 31 | 43 | 0.0051022 | 0.0058032 | 0.010924 | 1.1 | 6 | 6.7 | 9 |  | 2332 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 135.5938 | 144.9991 | 199.8637 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 10
3901101615 | 70 | 15 | 3 | 90 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1942.08 | 2546 | 2726 | 3757 | 1.5 | 1.1 | 1.1 | 1.1 | 157 | 368 | 386 | 493 | 8 | 19 | 20 | 25 | 0.001155 | 0.0061777 | 0.0068256 | 0.010538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 221 | 236 | 326 | 0.95 | 0.95 | 0.95 | 175.7404 | 187.6684 | 259.2369 | 38 | 40 | 56 | 0.02384 | 0.026351 | 0.050864 | 2.2 | 6 | 6.7 | 9 |  | 2856 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 187.6684 | 259.2369 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.82124 | 0.76344 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3901102015 | 70 | 15 | 3 | 90 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2602.4 | 2292 | 2470 | 3031 | 1.5 | 1.08 | 1.08 | 1.08 | 210 | 335 | 355 | 419 | 11 | 17 | 18 | 22 | 0.00059509 | 0.0013809 | 0.0015426 | 0.0022762 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 221 | 238 | 292 | 0.95 | 0.95 | 0.95 | 175.7404 | 189.2588 | 232.1999 | 38 | 41 | 50 | 0.0065849 | 0.0076351 | 0.011241 | 1.5 | 6 | 6.7 | 9 |  | 3253 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 175.7404 | 189.2588 | 232.1999 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.7343 | 0.6854 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 10
3901102115 | 70 | 15 | 3 | 90 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3317.6 | 2823 | 3022 | 4167 | 1.5 | 1.05 | 1.05 | 1.05 | 268 | 449 | 475 | 625 | 14 | 23 | 25 | 32 | 0.0014376 | 0.0037234 | 0.0043705 | 0.0070278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 243 | 260 | 358 | 0.85 | 0.85 | 0.85 | 197.9527 | 211.8012 | 291.634 | 43 | 46 | 63 | 0.012424 | 0.014152 | 0.025997 | 2.9 | 6 | 6.7 | 9 |  | 4147 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 197.9527 | 211.8012 | 291.634 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.7343 | 0.6854 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 10
3901201015 | 80 | 15 | 3 | 90 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1478.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 119 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00031342 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 6 | 6.7 | 9 |  | 1643 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.82124 | 0.76344 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901201115 | 80 | 15 | 3 | 90 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1434.8 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.00057024 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.7343 | 0.6854 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901201515 | 80 | 15 | 3 | 90 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 1781 | 1907 | 2654 | 1.5 | 1.08 | 1.08 | 1.08 | 164 | 272 | 288 | 380 | 8 | 14 | 15 | 20 | 0.00044509 | 0.001295 | 0.0014777 | 0.0025647 | 0.0002083 | 1.724 | 2 | 0.00046183 | 201 | 215 | 299 | 1.01 | 1.01 | 1.01 | 157.5396 | 168.5125 | 234.35 | 34 | 36 | 50 | 0.0071151 | 0.0079437 | 0.014976 | 1.2 | 6 | 6.7 | 9 |  | 2544 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 157.5396 | 168.5125 | 234.35 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901201615 | 80 | 15 | 3 | 90 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2118.2 | 2840 | 3041 | 4231 | 1.5 | 1.1 | 1.1 | 1.1 | 171 | 415 | 437 | 568 | 9 | 21 | 23 | 29 | 0.0014865 | 0.0076605 | 0.0091403 | 0.014342 | 0.0002083 | 1.724 | 4 | 0.0013928 | 257 | 276 | 384 | 0.95 | 0.95 | 0.95 | 204.3677 | 219.4766 | 305.3588 | 44 | 47 | 66 | 0.032299 | 0.036733 | 0.071274 | 2.4 | 6 | 6.7 | 9 |  | 3115 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 204.3677 | 219.4766 | 305.3588 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901202015 | 80 | 15 | 3 | 90 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2838.4 | 2555 | 2760 | 3438 | 1.5 | 1.08 | 1.08 | 1.08 | 229 | 380 | 404 | 485 | 12 | 20 | 21 | 25 | 0.00072203 | 0.0019355 | 0.0021271 | 0.0029811 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 255 | 275 | 342 | 0.95 | 0.95 | 0.95 | 202.7773 | 218.6814 | 271.9602 | 44 | 47 | 58 | 0.0089303 | 0.010153 | 0.015288 | 1.6 | 6 | 6.7 | 9 |  | 3548 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 218.6814 | 271.9602 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901202115 | 80 | 15 | 3 | 90 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3619.2 | 3206 | 3433 | 4776 | 1.5 | 1.05 | 1.05 | 1.05 | 292 | 516 | 547 | 729 | 15 | 27 | 28 | 38 | 0.0016935 | 0.0052134 | 0.00559 | 0.01005 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 283 | 303 | 422 | 0.85 | 0.85 | 0.85 | 230.5375 | 246.8299 | 343.7697 | 50 | 53 | 74 | 0.017047 | 0.019074 | 0.036333 | 3.2 | 6 | 6.7 | 9 |  | 4524 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 230.5375 | 246.8299 | 343.7697 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901401015 | 80 | 15 | 3 | 90 | 140 | 10 | 11.5 | 0 | 26 | 30 | 45.4 | 1725.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 139 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00046205 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 6 | 6.7 | 9 |  | 1917 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901401115 | 80 | 15 | 3 | 90 | 140 | 11 | 11.5 | 0 | 26 | 30 | 45.4 | 1673.48 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 135 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0.00084707 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 2461 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901401515 | 80 | 15 | 3 | 90 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 1981 | 2121 | 2977 | 1.5 | 1.08 | 1.08 | 1.08 | 191 | 296 | 312 | 406 | 10 | 15 | 16 | 21 | 0.0007242 | 0.0015647 | 0.0017694 | 0.0029719 | 0.0002083 | 1.724 | 2 | 0.00046183 | 208 | 222 | 312 | 1.01 | 1.01 | 1.01 | 163.0261 | 173.999 | 244.5391 | 35 | 37 | 53 | 0.0078988 | 0.0087873 | 0.017528 | 1.4 | 6 | 6.7 | 9 |  | 2968 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 163.0261 | 173.999 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901401615 | 80 | 15 | 3 | 90 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2471.12 | 3247 | 3477 | 4879 | 1.5 | 1.1 | 1.1 | 1.1 | 199 | 465 | 487 | 620 | 10 | 24 | 25 | 32 | 0.0019081 | 0.010319 | 0.011167 | 0.018012 | 0.0002083 | 1.724 | 4 | 0.0013928 | 263 | 282 | 396 | 0.95 | 0.95 | 0.95 | 209.139 | 224.2479 | 314.9013 | 45 | 48 | 68 | 0.034903 | 0.039566 | 0.077913 | 2.8 | 6 | 6.7 | 9 |  | 3634 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 209.139 | 224.2479 | 314.9013 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.81467 | 0.7562 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901402015 | 80 | 15 | 3 | 90 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3312 | 2853 | 3090 | 3897 | 1.5 | 1.08 | 1.08 | 1.08 | 267 | 412 | 437 | 522 | 14 | 21 | 23 | 27 | 0.0010189 | 0.0022217 | 0.0026472 | 0.0036063 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 262 | 284 | 358 | 0.95 | 0.95 | 0.95 | 208.3438 | 225.8383 | 284.6835 | 45 | 49 | 61 | 0.0096806 | 0.011417 | 0.01746 | 1.9 | 6 | 6.7 | 9 |  | 4140 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 208.3438 | 225.8383 | 284.6835 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.72541 | 0.67746 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901402115 | 80 | 15 | 3 | 90 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4222.4 | 3510 | 3759 | 5274 | 1.5 | 1.05 | 1.05 | 1.05 | 341 | 552 | 583 | 769 | 18 | 28 | 30 | 40 | 0.0025438 | 0.0059005 | 0.006731 | 0.011666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 290 | 311 | 436 | 0.85 | 0.85 | 0.85 | 236.2398 | 253.3468 | 355.1743 | 51 | 54 | 76 | 0.018582 | 0.020736 | 0.039988 | 3.7 | 6 | 6.7 | 9 |  | 5278 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 236.2398 | 253.3468 | 355.1743 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.72541 | 0.67746 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901601015 | 80 | 15 | 3 | 90 | 160 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 1971 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 159 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.00064784 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 6 | 6.7 | 9 |  | 2190 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.81467 | 0.7562 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901601115 | 80 | 15 | 3 | 90 | 160 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 1912.84 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 154 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0.0011951 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 6 | 6.7 | 9 |  | 2813 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.72541 | 0.67746 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901601515 | 80 | 15 | 3 | 90 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 2168 | 2315 | 3300 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 319 | 334 | 432 | 11 | 16 | 17 | 22 | 0.00091872 | 0.0018666 | 0.002094 | 0.0034164 | 0.0002083 | 1.724 | 2 | 0.00046183 | 213 | 228 | 324 | 1.01 | 1.01 | 1.01 | 166.945 | 178.7016 | 253.9444 | 36 | 38 | 55 | 0.0087309 | 0.0096807 | 0.019641 | 1.6 | 6 | 6.7 | 9 |  | 3392 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 166.945 | 178.7016 | 253.9444 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3901601615 | 80 | 15 | 3 | 90 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2824.72 | 3631 | 3877 | 5526 | 1.5 | 1.1 | 1.1 | 1.1 | 228 | 513 | 534 | 672 | 12 | 26 | 28 | 35 | 0.0028278 | 0.012497 | 0.014417 | 0.022179 | 0.0002083 | 1.724 | 4 | 0.0013928 | 268 | 286 | 408 | 0.95 | 0.95 | 0.95 | 213.115 | 227.4287 | 324.4437 | 46 | 49 | 70 | 0.037627 | 0.042523 | 0.084916 | 3.2 | 6 | 6.7 | 9 |  | 4154 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 213.115 | 227.4287 | 324.4437 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.80301 | 0.7433 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901602015 | 80 | 15 | 3 | 90 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3784.8 | 3147 | 3416 | 4357 | 1.5 | 1.08 | 1.08 | 1.08 | 305 | 445 | 471 | 559 | 16 | 23 | 24 | 29 | 0.001376 | 0.0027579 | 0.0029926 | 0.0043045 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 270 | 293 | 374 | 0.95 | 0.95 | 0.95 | 214.7054 | 232.9951 | 297.4067 | 46 | 50 | 64 | 0.010467 | 0.012294 | 0.019809 | 2.1 | 6 | 6.7 | 9 |  | 4731 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 214.7054 | 232.9951 | 297.4067 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71879 | 0.67123 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3901602115 | 80 | 15 | 3 | 90 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4825.6 | 3793 | 4049 | 5772 | 1.5 | 1.05 | 1.05 | 1.05 | 389 | 587 | 616 | 809 | 20 | 30 | 32 | 42 | 0.003282 | 0.0070806 | 0.0080047 | 0.013432 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 296 | 317 | 451 | 0.85 | 0.85 | 0.85 | 241.1275 | 258.2346 | 367.3936 | 52 | 56 | 79 | 0.020189 | 0.023259 | 0.044934 | 4.3 | 6 | 6.7 | 9 |  | 6032 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 241.1275 | 258.2346 | 367.3936 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71879 | 0.67123 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901801015 | 80 | 15 | 3 | 90 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46.4 | 2217.6 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 179 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.00087401 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 6 | 6.7 | 9 |  | 2464 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.80301 | 0.7433 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3901801115 | 80 | 15 | 3 | 90 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46.4 | 2151.52 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0.0016207 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 6.7 | 9 |  | 3164 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71879 | 0.67123 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3901801515 | 60 | 15 | 3 | 90 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 2167 | 2314 | 3298 | 1.5 | 1.08 | 1.08 | 1.08 | 246 | 302 | 312 | 378 | 13 | 16 | 16 | 20 | 0.0013278 | 0.0019638 | 0.0019638 | 0.0029934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 172 | 183 | 261 | 1.01 | 1.01 | 1.01 | 134.81 | 143.4316 | 204.5664 | 29 | 31 | 44 | 0.0060511 | 0.0068677 | 0.013368 | 1.8 | 6 | 6.7 | 9 |  | 3816 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 134.81 | 143.4316 | 204.5664 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3901801615 | 60 | 15 | 3 | 90 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 3177.64 | 3860 | 4121 | 5874 | 1.5 | 1.1 | 1.1 | 1.1 | 256 | 520 | 534 | 627 | 13 | 27 | 28 | 32 | 0.0034326 | 0.01392 | 0.014927 | 0.019297 | 0.0002083 | 1.724 | 4 | 0.0013928 | 207 | 221 | 316 | 0.95 | 0.95 | 0.95 | 164.6075 | 175.7404 | 251.2848 | 35 | 38 | 54 | 0.022929 | 0.026864 | 0.052914 | 3.6 | 6 | 6.7 | 9 |  | 4673 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 164.6075 | 175.7404 | 251.2848 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.79292 | 0.73212 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3901802015 | 60 | 15 | 3 | 90 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 4258.4 | 3224 | 3500 | 4464 | 1.5 | 1.08 | 1.08 | 1.08 | 343 | 423 | 441 | 501 | 18 | 22 | 23 | 26 | 0.0017965 | 0.0026349 | 0.0028685 | 0.0036264 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 220 | 239 | 304 | 0.95 | 0.95 | 0.95 | 174.9451 | 190.054 | 241.7424 | 38 | 41 | 52 | 0.0075042 | 0.0086829 | 0.013712 | 2.4 | 6 | 6.7 | 9 |  | 5323 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 174.9451 | 190.054 | 241.7424 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.71271 | 0.66551 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3901802115 | 60 | 15 | 3 | 90 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 5428.8 | 3645 | 3892 | 5548 | 1.5 | 1.05 | 1.05 | 1.05 | 438 | 530 | 549 | 680 | 23 | 27 | 28 | 35 | 0.0044979 | 0.0060883 | 0.0065215 | 0.0099481 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233 | 248 | 354 | 0.85 | 0.85 | 0.85 | 189.8065 | 202.0258 | 288.3755 | 41 | 43 | 62 | 0.013428 | 0.014698 | 0.029475 | 4.8 | 6 | 6.7 | 9 |  | 6786 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 189.8065 | 202.0258 | 288.3755 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.71271 | 0.66551 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902001015 | 80 | 15 | 3 | 90 | 200 | 10 | 11.5 | 0 | 26 | 30 | 47.1 | 2464.2 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 199 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0011436 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 6 | 6.7 | 9 |  | 2738 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.79292 | 0.73212 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902001115 | 80 | 15 | 3 | 90 | 200 | 11 | 11.5 | 0 | 26 | 30 | 47.1 | 2390.88 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 193 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.0021301 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 6 | 6.7 | 9 |  | 3516 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.71271 | 0.66551 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902001515 | 80 | 15 | 3 | 90 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3392 | 2595 | 2734 | 3946 | 1.5 | 1.08 | 1.08 | 1.08 | 274 | 372 | 383 | 484 | 14 | 19 | 20 | 25 | 0.001604 | 0.0028475 | 0.0031362 | 0.0047766 | 0.0002083 | 1.724 | 2 | 0.00046183 | 230 | 242 | 350 | 1.01 | 1.01 | 1.01 | 180.2692 | 189.6745 | 274.3227 | 39 | 41 | 59 | 0.011077 | 0.012179 | 0.024315 | 2 | 6 | 6.7 | 9 |  | 4240 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 180.2692 | 189.6745 | 274.3227 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902001615 | 80 | 15 | 3 | 90 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3530.56 | 4486 | 4727 | 6821 | 1.5 | 1.1 | 1.1 | 1.1 | 285 | 618 | 634 | 777 | 15 | 32 | 33 | 40 | 0.004686 | 0.01994 | 0.021152 | 0.030599 | 0.0002083 | 1.724 | 4 | 0.0013928 | 284 | 299 | 432 | 0.95 | 0.95 | 0.95 | 225.8383 | 237.7664 | 343.5286 | 49 | 51 | 74 | 0.045202 | 0.048819 | 0.10004 | 4 | 6 | 6.7 | 9 |  | 5192 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 225.8383 | 237.7664 | 343.5286 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902002015 | 80 | 15 | 3 | 90 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4731.2 | 3722 | 4057 | 5276 | 1.5 | 1.08 | 1.08 | 1.08 | 382 | 512 | 538 | 633 | 20 | 26 | 28 | 33 | 0.0022834 | 0.003763 | 0.0043342 | 0.0059309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 286 | 311 | 405 | 0.95 | 0.95 | 0.95 | 227.4287 | 247.3088 | 322.0581 | 49 | 53 | 69 | 0.012638 | 0.01469 | 0.02438 | 2.7 | 6 | 6.7 | 9 |  | 5914 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 227.4287 | 247.3088 | 322.0581 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902002115 | 80 | 15 | 3 | 90 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 6032 | 4450 | 4689 | 6768 | 1.5 | 1.05 | 1.05 | 1.05 | 486 | 668 | 691 | 890 | 25 | 34 | 36 | 46 | 0.0055199 | 0.0098503 | 0.010972 | 0.017436 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 316 | 333 | 481 | 0.85 | 0.85 | 0.85 | 257.4199 | 271.2685 | 391.8322 | 55 | 58 | 84 | 0.024457 | 0.027048 | 0.054661 | 5.3 | 6 | 6.7 | 9 |  | 7540 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 257.4199 | 271.2685 | 391.8322 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902201015 | 80 | 15 | 3 | 90 | 220 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2710.8 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 219 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0014597 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 6 | 6.7 | 9 |  | 3012 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902201115 | 80 | 15 | 3 | 90 | 220 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2630.24 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 212 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.0027293 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 6 | 6.7 | 9 |  | 3868 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902201515 | 80 | 15 | 3 | 90 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 2808 | 2925 | 4269 | 1.5 | 1.08 | 1.08 | 1.08 | 301 | 398 | 407 | 510 | 16 | 21 | 21 | 26 | 0.0021583 | 0.0035936 | 0.0035936 | 0.0053683 | 0.0002083 | 1.724 | 2 | 0.00046183 | 238 | 248 | 362 | 1.01 | 1.01 | 1.01 | 186.5394 | 194.3772 | 283.728 | 40 | 42 | 61 | 0.012093 | 0.013261 | 0.026884 | 2.2 | 6 | 6.7 | 9 |  | 4664 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 186.5394 | 194.3772 | 283.728 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902201615 | 80 | 15 | 3 | 90 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3883.48 | 4913 | 5118 | 7469 | 1.5 | 1.1 | 1.1 | 1.1 | 313 | 670 | 683 | 829 | 16 | 35 | 35 | 43 | 0.0054937 | 0.024429 | 0.024429 | 0.03623 | 0.0002083 | 1.724 | 4 | 0.0013928 | 292 | 304 | 444 | 0.95 | 0.95 | 0.95 | 232.1999 | 241.7424 | 353.0711 | 50 | 52 | 76 | 0.04838 | 0.052162 | 0.10818 | 4.4 | 6 | 6.7 | 9 |  | 5711 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 241.7424 | 353.0711 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.78402 | 0.72224 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902202015 | 80 | 15 | 3 | 90 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5204 | 3982 | 4351 | 5736 | 1.5 | 1.08 | 1.08 | 1.08 | 420 | 545 | 571 | 670 | 22 | 28 | 29 | 35 | 0.0028399 | 0.0044894 | 0.0047992 | 0.0068647 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292 | 319 | 420 | 0.95 | 0.95 | 0.95 | 232.1999 | 253.6705 | 333.9862 | 50 | 55 | 72 | 0.013558 | 0.016268 | 0.027248 | 2.9 | 6 | 6.7 | 9 |  | 6505 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 232.1999 | 253.6705 | 333.9862 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.70153 | 0.65707 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902202115 | 80 | 15 | 3 | 90 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6635.2 | 4779 | 4978 | 7265 | 1.5 | 1.05 | 1.05 | 1.05 | 535 | 708 | 726 | 930 | 28 | 37 | 37 | 48 | 0.0071424 | 0.012056 | 0.012056 | 0.019684 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 326 | 339 | 495 | 0.85 | 0.85 | 0.85 | 265.5661 | 276.1562 | 403.2369 | 57 | 59 | 87 | 0.027227 | 0.02906 | 0.060623 | 5.9 | 6 | 6.7 | 9 |  | 8294 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 265.5661 | 276.1562 | 403.2369 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.70153 | 0.65707 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902401015 | 80 | 15 | 3 | 90 | 240 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 2957.4 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 239 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0018252 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6 | 6.7 | 9 |  | 3286 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.78402 | 0.72224 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902401115 | 80 | 15 | 3 | 90 | 240 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 2868.92 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 231 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.0034241 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 6 | 6.7 | 9 |  | 4219 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.70153 | 0.65707 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902401515 | 80 | 15 | 3 | 90 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 3021 | 3131 | 4592 | 1.5 | 1.08 | 1.08 | 1.08 | 328 | 424 | 432 | 536 | 17 | 22 | 22 | 28 | 0.0025258 | 0.00409 | 0.00409 | 0.0064269 | 0.0002083 | 1.724 | 2 | 0.00046183 | 247 | 256 | 375 | 1.01 | 1.01 | 1.01 | 193.5934 | 200.6475 | 293.9172 | 42 | 43 | 63 | 0.013775 | 0.014399 | 0.029614 | 2.4 | 6 | 6.7 | 9 |  | 5088 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 193.5934 | 200.6475 | 293.9172 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902401615 | 80 | 15 | 3 | 90 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4236.4 | 5340 | 5535 | 8117 | 1.5 | 1.1 | 1.1 | 1.1 | 342 | 723 | 734 | 881 | 18 | 37 | 38 | 45 | 0.0071103 | 0.027995 | 0.029457 | 0.040685 | 0.0002083 | 1.724 | 4 | 0.0013928 | 300 | 311 | 456 | 0.95 | 0.95 | 0.95 | 238.5616 | 247.3088 | 362.6136 | 51 | 53 | 78 | 0.051689 | 0.055638 | 0.11672 | 4.8 | 6 | 6.7 | 9 |  | 6230 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 238.5616 | 247.3088 | 362.6136 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.76886 | 0.70539 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902402015 | 80 | 15 | 3 | 90 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5677.6 | 4243 | 4648 | 6195 | 1.5 | 1.08 | 1.08 | 1.08 | 458 | 578 | 605 | 708 | 24 | 30 | 31 | 37 | 0.0034688 | 0.0052937 | 0.0056334 | 0.0078823 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 299 | 327 | 436 | 0.95 | 0.95 | 0.95 | 237.7664 | 260.0321 | 346.7095 | 51 | 56 | 75 | 0.014517 | 0.017351 | 0.030313 | 3.2 | 6 | 6.7 | 9 |  | 7097 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.7664 | 260.0321 | 346.7095 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.69292 | 0.65762 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902402115 | 80 | 15 | 3 | 90 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7238.4 | 5108 | 5294 | 7763 | 1.5 | 1.05 | 1.05 | 1.05 | 584 | 748 | 764 | 970 | 30 | 39 | 39 | 50 | 0.0084792 | 0.013861 | 0.013861 | 0.022102 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 336 | 348 | 510 | 0.85 | 0.85 | 0.85 | 273.7123 | 283.4878 | 415.4562 | 59 | 61 | 89 | 0.03018 | 0.032136 | 0.065568 | 6.4 | 6 | 6.7 | 9 |  | 9048 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 273.7123 | 283.4878 | 415.4562 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.69292 | 0.65762 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902601015 | 80 | 15 | 3 | 90 | 260 | 10 | 11.5 | 0 | 26 | 30 | 48.1 | 3203.1 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 258 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.002243 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 6 | 6.7 | 9 |  | 3559 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.76886 | 0.70539 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902601115 | 80 | 15 | 3 | 90 | 260 | 11 | 11.5 | 0 | 26 | 30 | 48.1 | 3108.28 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 251 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0.0042203 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 6 | 6.7 | 9 |  | 4571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.69292 | 0.65762 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 0
3902601515 | 60 | 15 | 3 | 90 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 3020 | 3130 | 4590 | 1.5 | 1.08 | 1.08 | 1.08 | 356 | 407 | 412 | 482 | 18 | 21 | 21 | 25 | 0.0029295 | 0.0039044 | 0.0039044 | 0.0054063 | 0.0002083 | 1.724 | 2 | 0.00046183 | 205 | 213 | 312 | 1.01 | 1.01 | 1.01 | 160.6747 | 166.945 | 244.5391 | 35 | 36 | 53 | 0.010148 | 0.010699 | 0.022128 | 2.6 | 6 | 6.7 | 9 |  | 5512 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 160.6747 | 166.945 | 244.5391 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3902601615 | 60 | 15 | 3 | 90 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4590 | 5570 | 5772 | 8465 | 1.5 | 1.1 | 1.1 | 1.1 | 370 | 729 | 736 | 836 | 19 | 38 | 38 | 43 | 0.0081394 | 0.030321 | 0.030321 | 0.038369 | 0.0002083 | 1.724 | 4 | 0.0013928 | 239 | 248 | 364 | 0.95 | 0.95 | 0.95 | 190.054 | 197.2109 | 289.4547 | 41 | 42 | 62 | 0.035041 | 0.036687 | 0.077145 | 5.2 | 6 | 6.7 | 9 |  | 6750 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190.054 | 197.2109 | 289.4547 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75856 | 0.69426 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902602015 | 60 | 15 | 3 | 90 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 6150.4 | 4285 | 4727 | 6302 | 1.5 | 1.08 | 1.08 | 1.08 | 496 | 560 | 579 | 649 | 26 | 29 | 30 | 33 | 0.0041729 | 0.005129 | 0.0054685 | 0.0065489 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 249 | 275 | 367 | 0.95 | 0.95 | 0.95 | 198.0061 | 218.6814 | 291.8403 | 43 | 47 | 63 | 0.010815 | 0.012804 | 0.022351 | 3.5 | 6 | 6.7 | 9 |  | 7688 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 198.0061 | 218.6814 | 291.8403 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.68521 | 0.65781 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3902602115 | 60 | 15 | 3 | 90 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7841.6 | 4961 | 5141 | 7539 | 1.5 | 1.05 | 1.05 | 1.05 | 632 | 691 | 701 | 841 | 33 | 36 | 36 | 43 | 0.010547 | 0.012408 | 0.012408 | 0.017298 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 272 | 282 | 413 | 0.85 | 0.85 | 0.85 | 221.5766 | 229.7228 | 336.4381 | 48 | 49 | 72 | 0.021255 | 0.022092 | 0.04551 | 6.9 | 6 | 6.7 | 9 |  | 9802 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 221.5766 | 229.7228 | 336.4381 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.68521 | 0.65781 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902801015 | 60 | 15 | 3 | 90 | 280 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3449.7 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 278 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0027158 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 6 | 6.7 | 9 |  | 3833 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75856 | 0.69426 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 20
3902801115 | 60 | 15 | 3 | 90 | 280 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 3346.96 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 270 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.0051235 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 6 | 6.7 | 9 |  | 4922 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.68521 | 0.65781 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 20
3902801515 | 80 | 15 | 3 | 90 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 3447 | 3525 | 5238 | 1.5 | 1.08 | 1.08 | 1.08 | 383 | 476 | 481 | 588 | 20 | 25 | 25 | 30 | 0.0037077 | 0.0056162 | 0.0056162 | 0.0078904 | 0.0002083 | 1.724 | 2 | 0.00046183 | 263 | 269 | 400 | 1.01 | 1.01 | 1.01 | 206.1339 | 210.8366 | 313.5116 | 44 | 45 | 67 | 0.016149 | 0.016844 | 0.035569 | 2.8 | 6 | 6.7 | 9 |  | 5936 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 206.1339 | 210.8366 | 313.5116 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 0
3902801615 | 80 | 15 | 3 | 90 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4942.92 | 6195 | 6334 | 9412 | 1.5 | 1.1 | 1.1 | 1.1 | 399 | 827 | 834 | 986 | 21 | 43 | 43 | 51 | 0.010147 | 0.039438 | 0.039438 | 0.054559 | 0.0002083 | 1.724 | 4 | 0.0013928 | 316 | 323 | 480 | 0.95 | 0.95 | 0.95 | 251.2848 | 256.8513 | 381.6985 | 54 | 55 | 82 | 0.060832 | 0.062996 | 0.13499 | 5.6 | 6 | 6.7 | 9 |  | 7269 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 251.2848 | 256.8513 | 381.6985 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75028 | 0.68489 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3902802015 | 80 | 15 | 3 | 90 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6624 | 4838 | 5341 | 7114 | 1.5 | 1.08 | 1.08 | 1.08 | 534 | 650 | 679 | 782 | 28 | 34 | 35 | 40 | 0.0049551 | 0.0071465 | 0.0075486 | 0.0097152 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 318 | 351 | 467 | 0.95 | 0.95 | 0.95 | 252.8753 | 279.117 | 371.3608 | 54 | 60 | 80 | 0.01715 | 0.020945 | 0.036189 | 3.7 | 6 | 6.7 | 9 |  | 8280 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 252.8753 | 279.117 | 371.3608 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 0
3902802115 | 80 | 15 | 3 | 90 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 8444.8 | 5765 | 5894 | 8759 | 1.5 | 1.05 | 1.05 | 1.05 | 681 | 829 | 838 | 1050 | 35 | 43 | 43 | 54 | 0.012228 | 0.017948 | 0.017948 | 0.02747 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 355 | 363 | 540 | 0.85 | 0.85 | 0.85 | 289.1901 | 295.7071 | 439.8948 | 62 | 64 | 95 | 0.035577 | 0.037757 | 0.07927 | 7.5 | 6 | 6.7 | 9 |  | 10556 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 289.1901 | 295.7071 | 439.8948 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 0
3903001015 | 40 | 15 | 3 | 90 | 300 | 10 | 11.5 | 0 | 26 | 30 | 48.9 | 3696.3 | 0 | 0 | 0 | 1.5 | 1.08 | 1.08 | 1.08 | 298 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.0032464 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 6.7 | 9 |  | 4107 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2298 | 4062 | 502 | 78 | 0.75028 | 0.68489 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521 |  | 40
3903001115 | 40 | 15 | 3 | 90 | 300 | 11 | 11.5 | 0 | 26 | 30 | 48.9 | 3586.32 | 0 | 0 | 0 | 1.5 | 1.1 | 1.1 | 1.1 | 289 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0.006139 | 0 | 0 | 0 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 6.7 | 9 |  | 5274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462 |  | 40
3903001515 | 60 | 15 | 3 | 90 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 5088 | 3446 | 3523 | 5236 | 1.5 | 1.08 | 1.08 | 1.08 | 410 | 459 | 462 | 535 | 21 | 24 | 24 | 28 | 0.0042152 | 0.0054007 | 0.0054007 | 0.0071925 | 0.0002083 | 1.724 | 2 | 0.00046183 | 222 | 227 | 337 | 1.01 | 1.01 | 1.01 | 173.999 | 177.9179 | 264.1336 | 37 | 38 | 57 | 0.012088 | 0.012705 | 0.027116 | 3 | 6 | 6.7 | 9 |  | 6360 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 173.999 | 177.9179 | 264.1336 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947 |  | 20
3903001615 | 60 | 15 | 3 | 90 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 5295.84 | 6424 | 6568 | 9760 | 1.5 | 1.1 | 1.1 | 1.1 | 427 | 833 | 838 | 941 | 22 | 43 | 43 | 49 | 0.011415 | 0.040508 | 0.040508 | 0.051899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 255 | 261 | 388 | 0.95 | 0.95 | 0.95 | 202.7773 | 207.5486 | 308.5396 | 44 | 45 | 66 | 0.042312 | 0.044155 | 0.091418 | 6 | 6 | 6.7 | 9 |  | 7788 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 202.7773 | 207.5486 | 308.5396 |  | 0 | 0 | 0 | 1 | #VALUE! | 0 | 0 | #VALUE! | 0.75 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
3903002015 | 60 | 15 | 3 | 90 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 7096.8 | 4910 | 5422 | 7221 | 1.5 | 1.08 | 1.08 | 1.08 | 572 | 634 | 654 | 723 | 30 | 33 | 34 | 37 | 0.0058181 | 0.0069609 | 0.0073634 | 0.0086349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 271 | 299 | 398 | 0.95 | 0.95 | 0.95 | 215.5006 | 237.7664 | 316.4917 | 46 | 51 | 68 | 0.013021 | 0.015825 | 0.027282 | 4 | 6 | 6.7 | 9 |  | 8871 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215.5006 | 237.7664 | 316.4917 |  | 0 | 0 | 0 | 1 | 1615 | 3238 | 442 | 63 | 0.6819 | 0.65797 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378 |  | 20
3903002115 | 60 | 15 | 3 | 90 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 9048 | 5618 | 5743 | 8535 | 1.5 | 1.05 | 1.05 | 1.05 | 730 | 771 | 778 | 921 | 38 | 40 | 40 | 48 | 0.014778 | 0.016256 | 0.016256 | 0.022826 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 291 | 298 | 442 | 0.85 | 0.85 | 0.85 | 237.0544 | 242.7568 | 360.0621 | 51 | 52 | 77 | 0.025557 | 0.026499 | 0.055184 | 8 | 6 | 6.7 | 9 |  | 11310 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 237.0544 | 242.7568 | 360.0621 |  | 0 | 0 | 0 | 1 | 3238 | 4735 | 725 | 75 | 0.6819 | 0.65797 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521 |  | 20
[77 empty] | 2298 | 4062 | 502 | 78 | 0.75 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 2489 | 6098 | 791 | 92 | 0.6819 | 0.65797 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462
[77 empty] | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947
[77 empty] | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378
[77 empty] | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462
[77 empty] | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.78947 | 0.78947
[77 empty] | #VALUE! | 0 | 0 | #VALUE! | 0.75078 | 0.68 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 1615 | 3238 | 442 | 63 | 0.67294 | 0.65821 |  | 0.16321 | 0.080645 | 0.78378 | 0.78378
[77 empty] | 3238 | 4735 | 725 | 75 | 0.67294 | 0.65821 |  | 0.15782 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 2298 | 4062 | 502 | 78 | 0.75078 | 0.68 |  | 0.16321 | 0.080645 | 0.79521 | 0.79521
[77 empty] | 2489 | 6098 | 791 | 92 | 0.67294 | 0.65821 |  | 0.17163 | 0.080645 | 0.81462 | 0.81462
Note on D4: Thomas Henson: Strada = 1 Linea = 2 Tempo = 3 Built_in = 4
∆[𝑘𝑃𝑎]= 𝑘_1∗𝑞^𝑛∗((𝐿−144)∗𝑡)/1000+𝑘_2∗𝑞^2∗*0,0098

## NL (hidden)
Selectiontool Strada Hybrid
| Lengte |  | mm | Invulformulier | Statisch toestel | rel. vocht. | Unit | Kopieer alle data
| Hoogte |  | mm | Uitvoering | Hybrid toestel | Eenheidsstelsel | DBH set | SI-eenheden
| Type |  |  | Temperaturen | DBH rail type | Toestel |  | Imperiale-eenheden
| Diepte |  | mm | Indien de ventilatoren uitgeschakeld zijn, is de afgifte een indicatieve waarde. | Waterzijdig drukverlies
| Verwarmen: |  |  |  |  | Koelen:
| Water aanvoer |  |  | Water aanvoer |  |  |  | 0
| Water retour |  | 0 | Water retour |  |  |  | 0
| Ruimte (droge bol) |  | 0 | Ruimte (droge bol) |  |  |  | 0
|  | Verwarmen: // |  | Koelen: // |  | Watervolume | Elektrisch verbruik [W] | Geluidsdrukniveau [dB(A)]**** | Geluidsvermogen [dB(A)]****
|  | Verwarmvermogen | Waterdebiet | Koelvermogen | Waterdebiet
Statisch (indicatieve waarde)
EN16430 | Ventilatorsnelheid
Ventilatorsnelheid 2
Ventilatorsnelheid 3
| Stuurspanning [v] | [6 empty] | #REF!
* | Koelvermogen is berekend volgens EN16430 met de ventilatoren naar boven blazend voor alle types.
** | Wanneer het watervolume in gallons wordt gegeven, zijn dit imperial gallons.
*** | Geluidsvermogen volgens ISO 3741:2010, Voor het geluidsdrukniveau is er een aangenomen kamerdemping van 8 dB(A).

## EN (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## FR (hidden)
Selectiontool Strada Hybrid
| Longeur |  | mm | Formulaire | Appareil statique | hum. rel. | Unité | Copier toutes des données
| Hauteur |  | mm | Version | Appareil Hybrid | Système unitaire | DBH set | Unités-SI
| Type |  |  | Températures | DBH rail type | Appareil |  | Unités-Impériales
| Profondeur |  | mm | Si les ventilateurs sont éteints, la sortie est une valeur indicative. | Perte de charge
| Chauffer: |  |  |  |  | Refroidir:
| Entrée de l'eau |  |  | Entrée de l'eau |  |  |  | 0
| Retour de l'eau |  | 0 | Retour de l'eau |  |  |  | 0
| Ambiante (bulbe sec) |  | 0 | Ambiante (bulbe sec) |  |  |  | 0
|  | Chauffer: // |  | Refroidir: // |  | Volume d'eau | Puissance absorbée elec. [W] | Pression sonore [dB(A)]**** | Puissance sonore [dB(A)]****
|  | Puissance de chauffer | Débit d'eau | Puissance de refroidir | Débit d'eau
Ventilateur éteint (indicative)
EN16430 | Vitesse ventilateur
Vitesse du ventilateur 2
Vitesse du ventilateur 3
Tension ventilateur [V]
* | La puissance de refroidissement est calculée selon EN 16430 avec des ventilateurs qui soufflent pour toutes les hauteurs.
** | Lorsque le volume d'eau est donné en gallons, ce sont des gallons impérial.
*** | Puissance acoustique selon ISO 3741: 2010, niveau de pression acoustique avec un amortissement de la pièce supposé de 8 dB(A).

## DE (hidden)
Selectiontool Strada Hybrid
| Länge |  | mm | Eingabefelder | Statisches Gerät | rel. Luftf. | Unit | Kopieren Sie alle daten
| Höhe |  | mm | Ausführung | Hybrid Gerät | Einheiten | DBH set | SI-einheiten
| Typ |  |  | Temperaturen | DBH rail typ | Gerät |  | Imperiale-einheiten
| Tiefe |  | mm | Wenn die Lüfter ausgeschaltet sind, ist der Ausgang ein Richtwert. | zug. wassers. Druckverlust
| Heizen: |  |  |  |  | Kühlen:
| Vorlauf wasser |  |  | Vorlauf wasser |  |  |  | 0
| Rücklauf wasser |  | 0 | Rücklauf wasser |  |  |  | 0
| Raum (trocken) |  | 0 | Raum (trocken) |  |  |  | 0
|  | Heizen: // |  | Kühlen: // |  | Wasservolumen | Elektr. Leistung [W] | Schalldruckpegel [dB(A)]**** | Schallleistungspegel [dB(A)]****
|  | Heizleistung | Heizmittelstrom | Kühlleistung | Kühlmittelstrom
Lüfter aus (richtwert)
EN16430 | Auslegungsstufe
Auslegungsstufe 2
Auslegungsstufe 3
Lufterspannung [V]
* | Die Kühlleistung wird nach EN 16430 berechnet, wobei die Lüfter für alle Höhen hochgehen.
** | Wenn das Wasservolumen in Gallonen angegeben ist, sind dies imperiale Gallonen.
*** | Schallleistung nach ISO 3741: 2010, Schalldruckpegel bei angenommener Raumdämpfung von 8 dB(A).

## NR (hidden)
Selectiontool Strada Hybrid
| Lengde |  | mm | Inngangsskjema | Statisk modell | rel. fuktighet | Unit | Kopier alle data
| Høyde |  | mm | Versjon | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Type |  |  | Temperaturer | DBH rail type | Modell |  | Imperiale-enheter
| Bredde |  | mm | Hvis viftene er slått av, er utgangen en indikativ verdi. | Trykktap
| Varme: |  |  |  |  | Kjøling:
| Tur vann |  |  | Tur vann |  |  |  | 0
| Retur vann |  | 0 | Retur vann |  |  |  | 0
| Rom (tørr pære) |  | 0 | Rom (tørr pære) |  |  |  | 0
|  | Varme: // |  | Kjøling: // |  | Vannvolum | Elektrisk effekt [W] | Lydtrykk [dB(A)]**** | Lydeffekt [dB(A)]****
|  | Varme effekt | Vannmengde | Kjøle effekt | Vannmengde
Lüfter aus (richtwert)
EN16430 | Styresignal
Auslegungsstufe 2
Auslegungsstufe 3
Viftespenning [V]
* | Kjølekapasitet beregnes i henhold til EN16430 med viftene som blåser oppover for alle typer.
** | Når vannvolumet er gitt i gallon, er dette imperial gallons.
*** | Lydeffekt i henhold til ISO 3741: 2010. For lydtrykknivået er det en antatt romdemping på 8 dB (A).

## SP (hidden)
Selectiontool Strada Hybrid
| Longitud |  | mm | Formulary | Dispositivo estático | Hum. Relativa | Unit | Copiar todos los datos
| Altura |  | mm | Versión | Dispositivo Hybrid | Convers. de unidades | DBH set | Unidades-SI
| Tipo |  |  | Temperaturas | tipo de riel DBH | Despositivo |  | Unidades-Imperial
| Profund. |  | mm | La velocidad del ventilador en "0" tiene una emisión indicativa. | Pérdida de carga del agua
| Calefacción: |  |  |  |  | Enfriamiento:
| Agua impulsión |  |  | Agua impulsión |  |  |  | 0
| Agua retorno |  | 0 | Agua retorno |  |  |  | 0
| Ambiente (bulbo seco) |  | 0 | Ambiente (bulbo seco) |  |  |  | 0
|  | Calefacción: // |  | Enfriamiento: // |  | Volumen de agua | Potencia eléctrica absorbida [W] | Presión sonora [dB(A)]**** | Potencia sonora [dB(A)]****
|  | Emisión calefacción | Caudal de agua, calefacción | Emisión sensible Frío | Caudal de agua, calefacción
Fans off (indicative value)
EN16430 | Velocidad del ventilador
Fan speed selection 2
Fan speed selection 3
Voltaje control [V]
* | La potencia de enfriamiento se calcula según la norma EN 16430 con ventiladores de todas las alturas.
** | Cuando el volumen de agua se da en galones, las unidades son específicamente galones imperiales.
*** | Potencia sonora según ISO 3741: 2010, nivel de presión acústica con una amortiguación ambiental supuesta de 8 dB (A).

## SW (hidden)
Selectiontool Strada Hybrid
| Längd |  | mm | Inngangsskjema | Statisk modell | rel. Fuktighet | Unit | Kopiera all data
| Höjd |  | mm | Storlek | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Typ |  |  | Temperaturer | DBH rail typ | Modell |  | Imperiella-enheter
| Djup |  | mm | Om fläktarna är avstängda är utgången ett indikationsvärde. | Tryckfall, vatten
| Värme: |  |  |  |  | Kyla:
| Tillopp |  |  | Tillopp |  |  |  | 0
| Retur |  | 0 | Retur |  |  |  | 0
| Rum (torr) |  | 0 | Rum (torr) |  |  |  | 0
|  | Värme: // |  | Kyla: // |  | Vattenvolym | Effektförbrukning [W] | Ljudtryck [dB(A)]**** | Ljudeffekt [dB(A)]****
|  | Effekt | Vattenflöde | Kyleffekt | Vattenflöde
Fans off (indicative value)
EN16430 | Fläkthastighet
Fan speed selection 2
Fan speed selection 3
Spänning, Fläkt [V]
* | Kyleffekt är beräknad enligt EN16430 med fläktar blåsandes i riktning uppåt för alla höjder
** | När vattenvolymen är given i gallon avser det Imperiella gallon.
*** | Ljudeffekt enligt ISO 3741:2010 ljudtryck med antagen ljudreduktion från rummet på 8 dB(A)

## TS (hidden)
Selectiontool Strada Hybrid
| Délka |  | mm | Formulary | Statická jednotka | Relativní vlhkost | Jednotka | Kopírovat všechna data
| Výška |  | mm | Verze | Hybridní jednotka | Převod jednotek | DBH sada | Mezinárodní (Sl)
| Typ |  |  | Teploty | DBH rail type | Device |  | Imperiální
| Hloubka |  | mm | Pokud jsou ventilátory vypnuté, je výkon pouze orientační. | Tlaková ztráta
| Topení: |  |  |  |  | Chlazení:
| Voda na přívodu |  |  | Voda na přívodu |  |  |  | 0
| Voda na zpátečce |  | 0 | Voda na zpátečce |  |  |  | 0
| "Suchá" teplota vzduchu |  | 0 | "Suchá" teplota vzduchu |  |  |  | 0
|  | Topení: // |  | Chlazení: // |  | Objem vody | Elektrický výkon [W] | Akustický tlak [dB(A)]**** | Akustický výkon [dB(A)]****
|  | Výkon Topení | Průtok vody | Výkon Chlazení | Průtok vody
Fans off (indicative value)
EN16430 | Rychlost otáček ventilátoru
Fan speed selection 2
Fan speed selection 3
Napětí ventilárotu [V]
* | Chladicí výkon vypočítán podle EN 16430 s ventilátory, které u všech typů - výšek foukají nahoru.
**
*** | Akustický výkon podle ISO 3741: 2010, hladina akustického tlaku s předpokládaným útlumem místnosti o 8 dB (A).

## ExtraTaal1 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal2 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal3 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).