## Vertilina
Selectiontool Vertilina Hybrid
|  |  |  | Taal/Language/Sprache/Språk/Jazyk |  |  |  | English
|  |  |  | Hybrid device |  |  |  | Vertilina Hybrid
|  |  |  | Version [centimeter] |  |  |  | 30dB(A) | 41 | 11 | 11.5
[5 empty] | Length | Fan speed |  |  | Length [cm] | Type | Depth
Temperatures
Heating: |  |  |  |  | Cooling:
Supply water | 0 | 0 | 35 | °C | Supply water | 0 | 0 | 16 | °C | Unit conversion
Return water | 0 | 0 | 30 | °C | Return water | 0 | 0 | 18 | °C
Entering air (dry bulb) | 0 | 0 | 20 | °C | Entering air (dry bulb) | 0 | 0 | 27 | °C
[5 empty] | rel. humid. |  |  | 50%
Heigth [cm] |  | Heating capacity [W] | Water flow [kg/h] | Water side pressure loss [kPa] | Cooling capacity [W] | Water flow [kg/h] | Water side pressure loss [kPa] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]**** | Electrical consumption [W] | Water volume [l]
Vertilina Hybrid, Length [cm] 41cm, Type 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 |  | 438 | 75 | 0.052694 | 273 | 117 | 0.12254 | 30 | 38 | 11.4721 | 1.2
100 |  | 502 | 86 | 0.071826 | 315 | 135 | 0.1686 | 30 | 38 | 12.7407 | 1.3
120 |  | 629 | 108 | 0.12096 | 397 | 171 | 0.28731 | 30 | 38 | 15.1953 | 1.6
150 |  | 814 | 140 | 0.22171 | 517 | 222 | 0.52523 | 30 | 38 | 18.744 | 2
170 |  | 936 | 161 | 0.30879 | 596 | 256 | 0.73301 | 30 | 38 | 21.0288 | 2.3
190 |  | 1056 | 182 | 0.41383 | 675 | 290 | 0.98355 | 30 | 38 | 23.2418 | 2.5
210 |  | 1172 | 202 | 0.53317 | 751 | 323 | 1.2723 | 30 | 38 | 25.3154 | 2.8
230 |  | 1291 | 222 | 0.67147 | 828 | 356 | 1.6073 | 30 | 38 | 27.4714 | 3.1
250 |  | 1413 | 243 | 0.83608 | 907 | 390 | 2.0005 | 30 | 38 | 28.4891 | 3.3
270 |  | 1521 | 262 | 1.0091 | 978 | 421 | 2.4153 | 30 | 38 | 31.4391 | 3.6
290 |  | 1647 | 283 | 1.2183 | 1060 | 456 | 2.9261 | 30 | 38 | 31.44 | 3.9
300 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
v2025-03-07
* | Output without fans is negligible | [9 empty] | v2026-04-13
** | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
*** | When the water volume is given in gallons, the units are specifically imperial gallons.
**** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## data (hidden)
Vertilina_L | [11 empty] | heating | Ti | 35 | 35 | [20 empty] | cooling | Ti | 16 | 16 |  | RH | 50% |  |  |  | RH | [24 empty] | DBH rail | NONE | 10 | 15 |  |  | Imperial/SI |  | toestel | taal | lengte | hoogte | type | Vertilina Hybrid
Vertilina | [12 empty] | Tr | 30 | 30 | [21 empty] | Tr | 18 | 18 | [31 empty] | 1 | [5 empty] | 1 |  | Geselecteerd |  |  |  |  | hoogte | lengte | type | Type van letter tot cijfer voor zoek functie | [12 empty] | Selectiontool LowH2O Hybrids
Vertilina_T | [12 empty] | Ta | 20 | 20 | [21 empty] | Ta | 27 | 27 | [37 empty] | 1 | Vertilina | Vertilina Hybrid | Nederlands | 90 | 41 | 8 | 90 | 41 | 8 | 11
kolomindex | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 |  | Linea | 0 | English | 100 | 41 | 11 | 100 |  | 11 | [17 empty] | Taal/Language/Sprache/Langue/Språk/Lengua |  |  |  | English | 0
19011 |  |  | 1 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 34.8451 | 565.76 | 720.3428 | 796.4007 | 891.4998 | N/A | 1 | 1 | 1 | #VALUE! | 396 | 438 | 491 | #VALUE! | 68 | 75 | 84 | #VALUE! | 0.043772 | 0.052694 | 0.065317 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 224.8432 | 242.8013 | 260.5002 | 1 | 1 | 1 | 253 | 273 | 293 | 109 | 117 | 126 | 0.1071 | 0.12254 | 0.14109 | 1.2 | 9.8888 | 11.4721 | 12.35 | 0 | 832 | 0 | 0.68 | 0 | 0 | 0 | 13.6 | 15.6 | 21.85 | 0 | 1 | 1 | 1 | 253 | 273 | 293 | 0 | 0 | 0 | 0 | 1 |  | Tempo | 0 | Français | 120 | 41 | 16 | 120 |  | 16 | [17 empty] | 0 |  |  |  | Vertilina Hybrid | 0
110011 |  |  | 1 | 100 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 35.5123 | 629.68 | 827.7406 | 912.9332 | 1040.0833 | N/A | 1 | 1 | 1 | #VALUE! | 456 | 502 | 572 | #VALUE! | 78 | 86 | 98 | #VALUE! | 0.059737 | 0.071826 | 0.091933 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 259.0562 | 279.7075 | 303.9166 | 1 | 1 | 1 | 292 | 315 | 342 | 126 | 135 | 147 | 0.14793 | 0.1686 | 0.19815 | 1.3 | 11.0942 | 12.7407 | 14.4083 | 0 | 926 | 0 | 0.68 | 0 | 0 | 0 | 13.6 | 15.6 | 21.85 | 0 | 1 | 1 | 1 | 292 | 315 | 342 | 0 | 0 | 0 | 0 | 1 |  | Built_in | 0 | Deutsch | 150 | 41 |  | 150 | [19 empty] | [centimeter] |  |  |  | 30dB(A) | 41 | 11 | 0
112011 |  |  | 1 | 120 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 36.6 | 733.04 | 1038.2507 | 1142.0803 | 1337.25 | N/A | 1 | 1 | 1 | #VALUE! | 571 | 629 | 736 | #VALUE! | 98 | 108 | 127 | #VALUE! | 0.10078 | 0.12096 | 0.16404 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 326.2129 | 352.3573 | 390.75 | 1 | 1 | 1 | 367 | 397 | 440 | 158 | 171 | 189 | 0.24751 | 0.28731 | 0.34705 | 1.6 | 13.3958 | 15.1953 | 18.525 | 0 | 1078 | 0 | 0.68 | 0 | 0 | 0 | 13.6 | 15.6 | 21.85 | 0 | 1 | 1 | 1 | 367 | 397 | 440 | 0 | 0 | 0 | 0 | 1 |  | MiniHybrid | Mini Hybrid | Norsk | 170 | 41 |  | 170 | [20 empty] | 0 |  | 0 |  | 0 | 0 | 0
115011 |  |  | 1 | 150 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 37.8451 | 599.76 | 1342.8565 | 1479.2042 | 1783.0001 | N/A | 1 | 1 | 1 | #VALUE! | 739 | 814 | 981 | #VALUE! | 127 | 140 | 169 | #VALUE! | 0.18485 | 0.22171 | 0.31517 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 423.6582 | 459.3348 | 520.9999 | 1 | 1 | 1 | 477 | 517 | 587 | 205 | 222 | 252 | 0.45239 | 0.52523 | 0.66622 | 2 | 16.5581 | 18.744 | 24.7 | 0 | 882 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 477 | 517 | 587 | 0 | 0 | 0 | 0 | 1 |  | StradaMM | Strada Hybrid MM | Español | 190 | 41 |  | 190 | [15 empty] | 0
117011 |  |  | 1 | 170 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.5123 | 707.2 | 1538.8654 | 1700.2751 | 2080.1667 | N/A | 1 | 1 | 1 | #VALUE! | 847 | 936 | 1145 | #VALUE! | 146 | 161 | 197 | #VALUE! | 0.25745 | 0.30879 | 0.4496 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 486.5089 | 529.5631 | 607.8333 | 1 | 1 | 1 | 548 | 596 | 685 | 236 | 256 | 295 | 0.62971 | 0.73301 | 0.9555 | 2.3 | 18.4892 | 21.0288 | 28.8167 | 0 | 1040 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 548 | 596 | 685 | 0 | 0 | 0 | 0 | 1 |  | #REF! | 1 | Svenska | 210 | 41 |  | 210 | [15 empty] | 0 |  |  |  |  | 0
119011 |  |  | 1 | 190 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 39.0902 | 784.04 | 1729.738 | 1918.3503 | 2377.3333 | N/A | 1 | 1 | 1 | #VALUE! | 952 | 1056 | 1308 | #VALUE! | 164 | 182 | 225 | #VALUE! | 0.3412 | 0.41383 | 0.61346 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.7922 | 598.9271 | 694.6667 | 1 | 1 | 1 | 617 | 675 | 782 | 265 | 290 | 336 | 0.8316 | 0.98355 | 1.2941 | 2.5 | 20.298 | 23.2418 | 32.9333 | 0 | 1153 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 617 | 675 | 782 | 0 | 0 | 0 | 0 | 1 |  | W/m,beript dyn heat | W/m,beript dyn cool | Čeština | 230 | 41 |  | 230 | [15 empty] | 0 | 0 | 0 | 35 | °C | 0 | 0 | 0 | 16 | °C | 0
121011 |  |  | 1 | 210 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 39.6 | 875.84 | 1918.3844 | 2129.7362 | 2674.4999 | N/A | 1 | 1 | 1 | #VALUE! | 1056 | 1172 | 1472 | #VALUE! | 182 | 202 | 253 | #VALUE! | 0.43973 | 0.53317 | 0.80877 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 608.3343 | 666.4723 | 781.5 | 1 | 1 | 1 | 685 | 751 | 880 | 295 | 323 | 378 | 1.0752 | 1.2723 | 1.7042 | 2.8 | 21.9149 | 25.3154 | 37.05 | 0 | 1288 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 685 | 751 | 880 | 0 | 0 | 0 | 0 | 1 |  |  | 1 | ExtraTaal1 | 250 | 41 |  | 250 | [15 empty] | 0 | 0 | 0 | 30 | °C | 0 | 0 | 0 | 18 | °C
123011 |  |  | 1 | 230 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.056 | 650.08 | 2098.7535 | 2346.2836 | 2971.6665 | N/A | 1 | 1 | 1 | #VALUE! | 1155 | 1291 | 1635 | #VALUE! | 199 | 222 | 281 | #VALUE! | 0.54887 | 0.67147 | 1.0375 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 666.3741 | 735.2764 | 868.3334 | 1 | 1 | 1 | 750 | 828 | 978 | 323 | 356 | 421 | 1.3424 | 1.6073 | 2.1934 | 3.1 | 23.6342 | 27.4714 | 41.1667 | 0 | 956 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 750 | 828 | 978 | 0 | 0 | 0 | 0 | 1 |  | OFF |  | ExtraTaal2 | 270 | 41 |  | 270 | [15 empty] | 0 | 0 | 0 | 20 | °C | 0 | 0 | 0 | 27 | °C
125011 |  |  | 1 | 250 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.2672 | 774.52 | 2292.9964 | 2568.345 | 3268.8335 | N/A | 1 | 1 | 1 | #VALUE! | 1262 | 1413 | 1799 | #VALUE! | 217 | 243 | 309 | #VALUE! | 0.67898 | 0.83608 | 1.3016 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 728.4144 | 805.4943 | 955.1668 | 1 | 1 | 1 | 820 | 907 | 1076 | 353 | 390 | 463 | 1.664 | 2.0005 | 2.7477 | 3.3 | 24.4218 | 28.4891 | 43.225 | 0 | 1139 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 820 | 907 | 1076 | 0 | 0 | 0 | 0 | 1 |  | 26dB(A) |  | ExtraTaal3 | 290 | 41 | Copy all data | 290 | [20 empty] | 0 |  |  | 50%
127011 |  |  | 1 | 270 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.8451 | 886.72 | 2454.2122 | 2763.2823 | 3566.0001 | N/A | 1 | 1 | 1 | #VALUE! | 1351 | 1521 | 1963 | #VALUE! | 232 | 262 | 338 | #VALUE! | 0.80724 | 1.0091 | 1.6117 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 780.6001 | 868.457 | 1042.0002 | 1 | 1 | 1 | 879 | 978 | 1173 | 378 | 421 | 504 | 1.9803 | 2.4153 | 3.3668 | 3.6 | 26.6941 | 31.4391 | 49.4 | 0 | 1304 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 879 | 978 | 1173 | 0 | 0 | 0 | 0 | 1 |  | 30dB(A) |  |  |  |  | SI-units
129011 |  |  | 1 | 290 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.8451 | 1092.08 | 2658.7299 | 2993.5557 | 3863.1668 | N/A | 1 | 1 | 1 | #VALUE! | 1463 | 1647 | 2126 | #VALUE! | 252 | 283 | 366 | #VALUE! | 0.98505 | 1.2183 | 1.953 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 845.65 | 940.8282 | 1128.8332 | 1 | 1 | 1 | 952 | 1060 | 1271 | 409 | 456 | 547 | 2.3954 | 2.9261 | 4.0914 | 3.9 | 26.69 | 31.44 | 49.4 | 0 | 1606 | 0 | 0.68 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 952 | 1060 | 1271 | 0 | 0 | 0 | 0 | 1 |  | MAX |  |  |  |  | Imperial-units
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [23 empty] | [cm] | 0 |  |  | [ONWAAR] |  |  | [ONWAAR] | 0 | 0 | 0
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 2 | [19 empty] | 26, 30 30cm, 36,6 35,5122897619372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [23 empty] | 50 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 1.2
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [23 empty] | 50 | 13.6 | 396 | 68 | 0.043772 | 253 | 109 | 0.1071 | 26 | 34 | 9.8888 | 1.2
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |  |  |  | 50 | 15.6 | 438 | 75 | 0.052694 | 273 | 117 | 0.12254 | 30 | 38 | 11.4721 | 1.2
111 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [13 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | 50 | 21.85 | 491 | 84 | 0.065317 | 293 | 126 | 0.14109 | 34.8451 | 42.8451 | 12.35 | 1.2
[88 empty] | Raillengte | Railtype | BMS-stuurspanningen |  |  | Opgenomen elektrisch vermogen | [6 empty] | 60 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 1.3
[87 empty] | 5010 | 50 | 10 | 14.2 | 16.2 | 21.85 | 3.6 | 4.1 | 5.1 |  |  |  |  | 60 | 13.6 | 456 | 78 | 0.059737 | 292 | 126 | 0.14793 | 26 | 34 | 11.0942 | 1.3
[87 empty] | 5015 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 60 | 15.6 | 502 | 86 | 0.071826 | 315 | 135 | 0.1686 | 30 | 38 | 12.7407 | 1.3
[87 empty] | 6010 | 60 | 10 | 13.6 | 15.6 | 21.85 | 4.8 | 5.4 | 6.8 |  |  |  |  | 60 | 21.85 | 572 | 98 | 0.091933 | 342 | 147 | 0.19815 | 35.5123 | 43.5123 | 14.4083 | 1.3
[8 empty] | soundpressure level |  |  |  | power | 45/40/20 |  |  | n |  |  |  | result | power |  |  | result | flow |  |  | static pressure loss | [7 empty] | power | 16/20/27 |  | n |  |  | result | power |  | result | flow |  | static pressure loss |  |  |  | electrical power nominal |  |  |  | oude cataloog |  | Statisch met rail / statisch cataloog |  |  |  |  | BMS-stuurspanning |  |  | Sensible heat factor |  |  | Total cooling capacity |  |  |  | Diff. Total and sensible |  |  | Show or not | [10 empty] | 6015 | 60 | 15 | 12.3 | 14.4 | 21.85 | 4.8 | 5.5 | 7.2 |  |  |  |  | 70 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 1.6
lookup code | L,rail | T,rail | toestel | height | length | type | depth | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | k1 | n | t | k2 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | watervolume | 1 | 2 | 3 |  | Static,H | Static,C |  |  |  | 0 | 1 | 2 | 3 |  | SHF 1 | SHF 2 | SHF 3 | Q,t 1 | Q,t 2 | Q,t 3 |  | ΔQ,t,s 1 | ΔQ,t,s 2 | ΔQ,t,s 3 | OK/NOTOK | [10 empty] | 7010 | 70 | 10 | 13.2 | 15.1 | 21.85 | 5.5 | 5.9 | 7.9 |  |  |  |  | 70 | 13.6 | 571 | 98 | 0.10078 | 367 | 158 | 0.24751 | 26 | 34 | 13.3958 | 1.6
11008 |  |  | 1 | 100 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 30.9 | 0 | 531.0839 | 593.5851 | 603.7501 | N/A | 1 | 1 | 1 | #VALUE! | 292 | 327 | 332 | #VALUE! | 50 | 56 | 57 | #VALUE! | 0.068487 | 0.084889 | 0.087785 | 0.000937 | 1.789 | 4 | 0.00139 | 165.2042 | 176.5749 | 177.9165 | 1 | 1 | 1 | 186 | 199 | 200 | 80 | 86 | 86 | 0.167 | 0.1916 | 0.1916 | 0.65 | 3.968 | 4.5178 | 4.5714 |  | 449 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 186 | 199 | 200 |  | 0 | 0 | 0 | 1 | [10 empty] | 7015 | 70 | 15 | 12.3 | 14.4 | 21.85 | 5.1 | 5.6 | 7.2 |  |  |  |  | 70 | 15.6 | 629 | 108 | 0.12096 | 397 | 171 | 0.28731 | 30 | 38 | 15.1953 | 1.6
11208 |  |  | 1 | 120 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 31.5 | 0 | 660.9183 | 754.0763 | 776.2499 | N/A | 1 | 1 | 1 | #VALUE! | 364 | 415 | 427 | #VALUE! | 63 | 71 | 73 | #VALUE! | 0.11829 | 0.14821 | 0.15619 | 0.000937 | 1.789 | 4 | 0.00139 | 207.5532 | 225.6902 | 228.7499 | 1 | 1 | 1 | 234 | 254 | 258 | 101 | 109 | 111 | 0.28838 | 0.3331 | 0.34475 | 0.8 | 4.5889 | 5.3127 | 5.7143 |  | 538 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 234 | 254 | 258 |  | 0 | 0 | 0 | 1 | [10 empty] | 8010 | 80 | 10 | 12.8 | 14.7 | 21.85 | 6.3 | 6.8 | 9.1 |  |  |  |  | 70 | 21.85 | 736 | 127 | 0.16404 | 440 | 189 | 0.34705 | 36.6 | 44.6 | 18.525 | 1.6
11508 |  |  | 1 | 150 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 32.5 | 0 | 827.5813 | 984.8027 | 1034.9999 | N/A | 1 | 1 | 1 | #VALUE! | 455 | 542 | 570 | #VALUE! | 78 | 93 | 98 | #VALUE! | 0.20373 | 0.28336 | 0.31262 | 0.000937 | 1.789 | 4 | 0.00139 | 263.9328 | 297.6019 | 305.0001 | 1 | 1 | 1 | 297 | 335 | 343 | 128 | 144 | 147 | 0.51633 | 0.64437 | 0.66986 | 1 | 5.5884 | 6.7631 | 8 |  | 606 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 297 | 335 | 343 |  | 0 | 0 | 0 | 1 | [10 empty] | 8015 | 80 | 15 | 11.8 | 13.7 | 21.85 | 6 | 6.7 | 9 |  |  |  |  | 80 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 2
11708 |  |  | 1 | 170 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 34.1 | 0 | 935.3255 | 1110.0611 | 1207.5001 | N/A | 1 | 1 | 1 | #VALUE! | 515 | 611 | 665 | #VALUE! | 89 | 105 | 114 | #VALUE! | 0.28349 | 0.3862 | 0.45046 | 0.000937 | 1.789 | 4 | 0.00139 | 300.2905 | 340.1672 | 355.8334 | 1 | 1 | 1 | 338 | 383 | 401 | 145 | 165 | 172 | 0.70686 | 0.90066 | 0.97368 | 1.15 | 5.978 | 7.4234 | 9.1429 |  | 598 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 338 | 383 | 401 |  | 0 | 0 | 0 | 1 | [10 empty] | 9010 | 90 | 10 | 12.5 | 14.7 | 21.85 | 6.7 | 7.4 | 10.3 |  |  |  |  | 80 | 12.3 | 739 | 127 | 0.18485 | 477 | 205 | 0.45239 | 26 | 34 | 16.5581 | 2
11908 |  |  | 1 | 190 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 34.7 | 0 | 1034.6409 | 1249.2455 | 1380 | N/A | 1 | 1 | 1 | #VALUE! | 569 | 688 | 759 | #VALUE! | 98 | 118 | 131 | #VALUE! | 0.36625 | 0.51788 | 0.62945 | 0.000937 | 1.789 | 4 | 0.00139 | 334.2445 | 384.9538 | 406.6668 | 1 | 1 | 1 | 376 | 434 | 458 | 162 | 187 | 197 | 0.93609 | 1.2243 | 1.3497 | 1.25 | 6.3001 | 8.0425 | 10.2857 |  | 693 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 376 | 434 | 458 |  | 0 | 0 | 0 | 1 | [10 empty] | 9015 | 90 | 15 | 11.3 | 13.2 | 21.85 | 7 | 7.7 | 10.7 |  |  |  |  | 80 | 14.4 | 814 | 140 | 0.22171 | 517 | 222 | 0.52523 | 30 | 38 | 18.744 | 2
12108 |  |  | 1 | 210 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 35.2 | 0 | 1125.2963 | 1384.7628 | 1552.4998 | N/A | 1 | 1 | 1 | #VALUE! | 619 | 762 | 854 | #VALUE! | 106 | 131 | 147 | #VALUE! | 0.45482 | 0.67452 | 0.83602 | 0.000937 | 1.789 | 4 | 0.00139 | 365.6603 | 428.8538 | 457.5001 | 1 | 1 | 1 | 412 | 483 | 515 | 177 | 208 | 221 | 1.1819 | 1.5972 | 1.7887 | 1.4 | 6.5586 | 8.6219 | 11.4286 |  | 772 |  | FALSE |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 412 | 483 | 515 |  | 0 | 0 | 0 | 1 | [10 empty] | 10010 | 100 | 10 | 12.3 | 14.1 | 21.85 | 7.8 | 8.7 | 12.2 |  |  |  |  | 80 | 21.85 | 981 | 169 | 0.31517 | 587 | 252 | 0.66622 | 37.8451 | 45.8451 | 24.7 | 2
12308 |  |  | 1 | 230 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 35.7 | 0 | 1207.0335 | 1516.5744 | 1725.0001 | N/A | 1 | 1 | 1 | #VALUE! | 664 | 835 | 949 | #VALUE! | 114 | 144 | 163 | #VALUE! | 0.55589 | 0.85789 | 1.0802 | 0.000937 | 1.789 | 4 | 0.00139 | 394.3977 | 471.8389 | 508.3335 | 1 | 1 | 1 | 444 | 531 | 572 | 191 | 228 | 246 | 1.4507 | 2.0174 | 2.3242 | 1.55 | 6.7572 | 9.1627 | 12.5714 |  | 539 |  | FALSE |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 444 | 531 | 572 |  | 0 | 0 | 0 | 1 | [10 empty] | 10015 | 100 | 15 | 10.9 | 12.8 | 21.85 | 7 | 7.7 | 10.7 |  |  |  |  | 90 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 2.3
12508 |  |  | 1 | 250 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 36.2 | 0 | 1279.5762 | 1644.6199 | 1897.4999 | N/A | 1 | 1 | 1 | #VALUE! | 704 | 905 | 1044 | #VALUE! | 121 | 156 | 180 | #VALUE! | 0.66002 | 1.0571 | 1.3787 | 0.000937 | 1.789 | 4 | 0.00139 | 420.3119 | 513.8754 | 559.1668 | 1 | 1 | 1 | 473 | 579 | 630 | 203 | 249 | 271 | 1.7236 | 2.5195 | 2.9493 | 1.65 | 6.8992 | 9.6657 | 13.7143 |  | 646 |  | FALSE |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 473 | 579 | 630 |  | 0 | 0 | 0 | 1 | [10 empty] | 11010 | 110 | 10 | 12 | 13.9 | 21.85 | 8.4 | 9.3 | 14 |  |  |  |  | 90 | 12.3 | 847 | 146 | 0.25745 | 548 | 236 | 0.62971 | 26 | 34 | 18.4892 | 2.3
12708 |  |  | 1 | 270 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 36.6 | 0 | 1315.6992 | 1768.8253 | 2070.0002 | N/A | 1 | 1 | 1 | #VALUE! | 724 | 973 | 1139 | #VALUE! | 125 | 167 | 196 | #VALUE! | 0.74246 | 1.2692 | 1.7075 | 0.000937 | 1.789 | 4 | 0.00139 | 435.4235 | 554.9254 | 610.0002 | 1 | 1 | 1 | 490 | 625 | 687 | 211 | 269 | 295 | 1.9577 | 3.0722 | 3.6464 | 1.8 | 7.0137 | 10.3513 | 15.4286 |  | 727 |  | FALSE |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 490 | 625 | 687 |  | 0 | 0 | 0 | 1 | [10 empty] | 11015 | 110 | 15 | 10.9 | 12.8 | 21.85 | 7.9 | 8.8 | 12.5 |  |  |  |  | 90 | 14.4 | 936 | 161 | 0.30879 | 596 | 256 | 0.73301 | 30 | 38 | 21.0288 | 2.3
12908 |  |  | 1 | 290 | 40.5 | 8 | 9.5 | 0 | 26 | 30 | 37.1 | 0 | 1336.331 | 1875.6071 | 2242.5 | N/A | 1 | 1 | 1 | #VALUE! | 735 | 1032 | 1234 | #VALUE! | 126 | 178 | 212 | #VALUE! | 0.79552 | 1.5063 | 2.0816 | 0.000937 | 1.789 | 4 | 0.00139 | 445.369 | 591.7994 | 660.8335 | 1 | 1 | 1 | 502 | 666 | 744 | 216 | 286 | 320 | 2.1548 | 3.6246 | 4.464 | 1.95 | 7.0193 | 10.9569 | 17.1429 |  | 836 |  | FALSE |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 502 | 666 | 744 |  | 0 | 0 | 0 | 1 | [10 empty] | 12010 | 120 | 10 | 11.8 | 13.7 | 21.85 | 8.9 | 9.9 | 14.8 |  |  |  |  | 90 | 21.85 | 1145 | 197 | 0.4496 | 685 | 295 | 0.9555 | 38.5123 | 46.5123 | 28.8167 | 2.3
17011 |  |  | 1 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 33.0902 | 406.6873 | 501.6873 | 555.7763 | 594.3332 | N/A | 1 | 1 | 1 | #VALUE! | 276 | 306 | 327 | #VALUE! | 47 | 53 | 56 | #VALUE! | 0.01931 | 0.024281 | 0.02697 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 155.2032 | 166.9571 | 173.6668 | 1 | 1 | 1 | 175 | 188 | 196 | 75 | 81 | 84 | 0.047129 | 0.054606 | 0.058543 | 0.9 | 7.3986 | 8.7271 | 8.2333 |  | 718 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 175 | 188 | 196 |  | 0 | 0 | 0 | 1 | [10 empty] | 12015 | 120 | 15 | 10.6 | 12.5 | 21.85 | 8.7 | 9.8 | 14.3 |  |  |  |  | 100 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 2.5
19011 |  |  | 1 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 34.8451 | 565.76 | 720.3428 | 796.4007 | 891.4998 | N/A | 1 | 1 | 1 | #VALUE! | 396 | 438 | 491 | #VALUE! | 68 | 75 | 84 | #VALUE! | 0.043772 | 0.052694 | 0.065317 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 224.8432 | 242.8013 | 260.5002 | 1 | 1 | 1 | 253 | 273 | 293 | 109 | 117 | 126 | 0.1071 | 0.12254 | 0.14109 | 1.2 | 9.8888 | 11.4721 | 12.35 |  | 832 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 253 | 273 | 293 |  | 0 | 0 | 0 | 1 | [10 empty] | 14010 | 140 | 10 | 11.5 | 13.3 | 21.85 | 10.1 | 11.2 | 17.5 |  |  |  |  | 100 | 12.3 | 952 | 164 | 0.3412 | 617 | 265 | 0.8316 | 26 | 34 | 20.298 | 2.5
110011 |  |  | 1 | 100 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 35.5123 | 629.68 | 827.7406 | 912.9332 | 1040.0833 | N/A | 1 | 1 | 1 | #VALUE! | 456 | 502 | 572 | #VALUE! | 78 | 86 | 98 | #VALUE! | 0.059737 | 0.071826 | 0.091933 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 259.0562 | 279.7075 | 303.9166 | 1 | 1 | 1 | 292 | 315 | 342 | 126 | 135 | 147 | 0.14793 | 0.1686 | 0.19815 | 1.3 | 11.0942 | 12.7407 | 14.4083 |  | 926 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 292 | 315 | 342 |  | 0 | 0 | 0 | 1 | [10 empty] | 14015 | 140 | 15 | 10.4 | 12.2 | 21.85 | 9.6 | 10.5 | 16.1 |  |  |  |  | 100 | 14.4 | 1056 | 182 | 0.41383 | 675 | 290 | 0.98355 | 30 | 38 | 23.2418 | 2.5
112011 |  |  | 1 | 120 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 36.6 | 733.04 | 1038.2507 | 1142.0803 | 1337.25 | N/A | 1 | 1 | 1 | #VALUE! | 571 | 629 | 736 | #VALUE! | 98 | 108 | 127 | #VALUE! | 0.10078 | 0.12096 | 0.16404 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 326.2129 | 352.3573 | 390.75 | 1 | 1 | 1 | 367 | 397 | 440 | 158 | 171 | 189 | 0.24751 | 0.28731 | 0.34705 | 1.6 | 13.3958 | 15.1953 | 18.525 |  | 1078 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 367 | 397 | 440 |  | 0 | 0 | 0 | 1 | [10 empty] | 16010 | 160 | 10 | 11.2 | 13 | 21.85 | 11 | 12.4 | 19.2 |  |  |  |  | 100 | 21.85 | 1308 | 225 | 0.61346 | 782 | 336 | 1.2941 | 39.0902 | 47.0902 | 32.9333 | 2.5
115011 |  |  | 1 | 150 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 37.8451 | 599.76 | 1342.8565 | 1479.2042 | 1783.0001 | N/A | 1 | 1 | 1 | #VALUE! | 739 | 814 | 981 | #VALUE! | 127 | 140 | 169 | #VALUE! | 0.18485 | 0.22171 | 0.31517 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 423.6582 | 459.3348 | 520.9999 | 1 | 1 | 1 | 477 | 517 | 587 | 205 | 222 | 252 | 0.45239 | 0.52523 | 0.66622 | 2 | 16.5581 | 18.744 | 24.7 |  | 882 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 517 | 587 |  | 0 | 0 | 0 | 1 | [10 empty] | 16015 | 160 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6 |  |  |  |  | 110 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 2.8
117011 |  |  | 1 | 170 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.5123 | 707.2 | 1538.8654 | 1700.2751 | 2080.1667 | N/A | 1 | 1 | 1 | #VALUE! | 847 | 936 | 1145 | #VALUE! | 146 | 161 | 197 | #VALUE! | 0.25745 | 0.30879 | 0.4496 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 486.5089 | 529.5631 | 607.8333 | 1 | 1 | 1 | 548 | 596 | 685 | 236 | 256 | 295 | 0.62971 | 0.73301 | 0.9555 | 2.3 | 18.4892 | 21.0288 | 28.8167 |  | 1040 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 548 | 596 | 685 |  | 0 | 0 | 0 | 1 | [10 empty] | 18010 | 180 | 10 | 10.9 | 12.7 | 21.85 | 12.2 | 13.7 | 22 |  |  |  |  | 110 | 12.3 | 1056 | 182 | 0.43973 | 685 | 295 | 1.0752 | 26 | 34 | 21.9149 | 2.8
119011 |  |  | 1 | 190 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 39.0902 | 784.04 | 1729.738 | 1918.3503 | 2377.3333 | N/A | 1 | 1 | 1 | #VALUE! | 952 | 1056 | 1308 | #VALUE! | 164 | 182 | 225 | #VALUE! | 0.3412 | 0.41383 | 0.61346 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.7922 | 598.9271 | 694.6667 | 1 | 1 | 1 | 617 | 675 | 782 | 265 | 290 | 336 | 0.8316 | 0.98355 | 1.2941 | 2.5 | 20.298 | 23.2418 | 32.9333 |  | 1153 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 617 | 675 | 782 |  | 0 | 0 | 0 | 1 | [10 empty] | 18015 | 180 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6 |  |  |  |  | 110 | 14.4 | 1172 | 202 | 0.53317 | 751 | 323 | 1.2723 | 30 | 38 | 25.3154 | 2.8
121011 |  |  | 1 | 210 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 39.6 | 875.84 | 1918.3844 | 2129.7362 | 2674.4999 | N/A | 1 | 1 | 1 | #VALUE! | 1056 | 1172 | 1472 | #VALUE! | 182 | 202 | 253 | #VALUE! | 0.43973 | 0.53317 | 0.80877 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 608.3343 | 666.4723 | 781.5 | 1 | 1 | 1 | 685 | 751 | 880 | 295 | 323 | 378 | 1.0752 | 1.2723 | 1.7042 | 2.8 | 21.9149 | 25.3154 | 37.05 |  | 1288 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 685 | 751 | 880 |  | 0 | 0 | 0 | 1 | [10 empty] | 20010 | 200 | 10 | 10.7 | 12.5 | 21.85 | 13.4 | 14.8 | 24 |  |  |  |  | 110 | 21.85 | 1472 | 253 | 0.80877 | 880 | 378 | 1.7042 | 39.6 | 47.6 | 37.05 | 2.8
123011 |  |  | 1 | 230 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.056 | 650.08 | 2098.7535 | 2346.2836 | 2971.6665 | N/A | 1 | 1 | 1 | #VALUE! | 1155 | 1291 | 1635 | #VALUE! | 199 | 222 | 281 | #VALUE! | 0.54887 | 0.67147 | 1.0375 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 666.3741 | 735.2764 | 868.3334 | 1 | 1 | 1 | 750 | 828 | 978 | 323 | 356 | 421 | 1.3424 | 1.6073 | 2.1934 | 3.1 | 23.6342 | 27.4714 | 41.1667 |  | 956 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 750 | 828 | 978 |  | 0 | 0 | 0 | 1 | [10 empty] | 20015 | 200 | 15 | 10 | 11.4 | 21.85 | 13.2 | 14.7 | 23.5 |  |  |  |  | 120 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 3.1
125011 |  |  | 1 | 250 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.2672 | 774.52 | 2292.9964 | 2568.345 | 3268.8335 | N/A | 1 | 1 | 1 | #VALUE! | 1262 | 1413 | 1799 | #VALUE! | 217 | 243 | 309 | #VALUE! | 0.67898 | 0.83608 | 1.3016 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 728.4144 | 805.4943 | 955.1668 | 1 | 1 | 1 | 820 | 907 | 1076 | 353 | 390 | 463 | 1.664 | 2.0005 | 2.7477 | 3.3 | 24.4218 | 28.4891 | 43.225 |  | 1139 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 820 | 907 | 1076 |  | 0 | 0 | 0 | 1 | [10 empty] | 22010 | 220 | 10 | 10.5 | 12.3 | 21.85 | 13.4 | 14.8 | 24 |  |  |  |  | 120 | 12.3 | 1155 | 199 | 0.54887 | 750 | 323 | 1.3424 | 26 | 34 | 23.6342 | 3.1
127011 |  |  | 1 | 270 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.8451 | 886.72 | 2454.2122 | 2763.2823 | 3566.0001 | N/A | 1 | 1 | 1 | #VALUE! | 1351 | 1521 | 1963 | #VALUE! | 232 | 262 | 338 | #VALUE! | 0.80724 | 1.0091 | 1.6117 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 780.6001 | 868.457 | 1042.0002 | 1 | 1 | 1 | 879 | 978 | 1173 | 378 | 421 | 504 | 1.9803 | 2.4153 | 3.3668 | 3.6 | 26.6941 | 31.4391 | 49.4 |  | 1304 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 879 | 978 | 1173 |  | 0 | 0 | 0 | 1 | [10 empty] | 22015 | 220 | 15 | 10 | 11.1 | 21.85 | 15.5 | 16.8 | 27.5 |  |  |  |  | 120 | 14.4 | 1291 | 222 | 0.67147 | 828 | 356 | 1.6073 | 30 | 38 | 27.4714 | 3.1
129011 |  |  | 1 | 290 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40.8451 | 1092.08 | 2658.7299 | 2993.5557 | 3863.1668 | N/A | 1 | 1 | 1 | #VALUE! | 1463 | 1647 | 2126 | #VALUE! | 252 | 283 | 366 | #VALUE! | 0.98505 | 1.2183 | 1.953 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 845.65 | 940.8282 | 1128.8332 | 1 | 1 | 1 | 952 | 1060 | 1271 | 409 | 456 | 547 | 2.3954 | 2.9261 | 4.0914 | 3.9 | 26.69 | 31.44 | 49.4 |  | 1606 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 952 | 1060 | 1271 |  | 0 | 0 | 0 | 1 | [10 empty] | 24010 | 240 | 10 | 10.4 | 12.2 | 21.85 | 14.8 | 16.6 | 28 |  |  |  |  | 120 | 21.85 | 1635 | 281 | 1.0375 | 978 | 421 | 2.1934 | 40.056 | 48.056 | 41.1667 | 3.1
19016 |  |  | 1 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 32.3733 | 1000.4309 | 1000.4309 | 1061.1878 | 1097.4999 | N/A | 1 | 1 | 1 | #VALUE! | 551 | 584 | 604 | #VALUE! | 95 | 100 | 104 | #VALUE! | 0.13904 | 0.15381 | 0.16616 | 0.0002083 | 1.724 | 4 | 0.0013928 | 292.1672 | 314.0225 | 330.5 | 1 | 1 | 1 | 329 | 354 | 372 | 141 | 152 | 160 | 0.30268 | 0.351 | 0.38837 | 1.8 | 9 | 9.8 | 12 |  | 1236 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 329 | 354 | 372 |  | 0 | 0 | 0 | 1 | [10 empty] | 24015 | 240 | 15 | 10 | 10.9 | 21.85 | 16.4 | 17.7 | 29.7 |  |  |  |  | 140 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 3.3
110016 |  |  | 1 | 100 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 33.5 | 1144.2946 | 1144.2946 | 1219.8568 | 1280.4166 | N/A | 1 | 1 | 1 | #VALUE! | 630 | 671 | 705 | #VALUE! | 108 | 115 | 121 | #VALUE! | 0.1816 | 0.20546 | 0.22708 | 0.0002083 | 1.724 | 4 | 0.0013928 | 333.7102 | 359.2078 | 385.5833 | 1 | 1 | 1 | 376 | 405 | 434 | 162 | 174 | 187 | 0.40326 | 0.4642 | 0.535 | 2 | 10.6 | 11.5 | 15 |  | 1455 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 376 | 405 | 434 |  | 0 | 0 | 0 | 1 | [10 empty] | 26010 | 260 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 |  |  |  |  | 140 | 12.3 | 1262 | 217 | 0.67898 | 820 | 353 | 1.664 | 26 | 34 | 24.4218 | 3.3
112016 |  |  | 1 | 120 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 34.4206 | 1444.1514 | 1444.1514 | 1549.13 | 1646.2501 | N/A | 1 | 1 | 1 | #VALUE! | 795 | 853 | 906 | #VALUE! | 137 | 147 | 156 | #VALUE! | 0.29781 | 0.34195 | 0.38424 | 0.0002083 | 1.724 | 4 | 0.0013928 | 421.0185 | 454.7257 | 495.7501 | 1 | 1 | 1 | 474 | 512 | 558 | 204 | 220 | 240 | 0.65072 | 0.75481 | 0.89563 | 2.4 | 12 | 13.2 | 18 |  | 1611 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 474 | 512 | 558 |  | 0 | 0 | 0 | 1 | [10 empty] | 26015 | 260 | 15 | 10 | 10.9 | 21.85 | 16.2 | 18.6 | 31.4 |  |  |  |  | 140 | 14.4 | 1413 | 243 | 0.83608 | 907 | 390 | 2.0005 | 30 | 38 | 28.4891 | 3.3
115016 |  |  | 1 | 150 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 35.8733 | 1863.8708 | 1863.8708 | 2019.296 | 2195.0001 | N/A | 1 | 1 | 1 | #VALUE! | 1026 | 1111 | 1208 | #VALUE! | 176 | 191 | 208 | #VALUE! | 0.50512 | 0.59273 | 0.70032 | 0.0002083 | 1.724 | 4 | 0.0013928 | 544.1215 | 590.3545 | 660.9999 | 1 | 1 | 1 | 613 | 665 | 744 | 264 | 286 | 320 | 1.1169 | 1.3066 | 1.6284 | 3 | 14.6 | 16.2 | 24 |  | 1795 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 613 | 665 | 744 |  | 0 | 0 | 0 | 1 | [10 empty] | 28010 | 280 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 |  |  |  |  | 140 | 21.85 | 1799 | 309 | 1.3016 | 1076 | 463 | 2.7477 | 40.2672 | 48.2672 | 43.225 | 3.3
117016 |  |  | 1 | 170 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 37 | 2118.8633 | 2118.8633 | 2307.013 | 2560.8334 | N/A | 1 | 1 | 1 | #VALUE! | 1166 | 1270 | 1409 | #VALUE! | 201 | 218 | 242 | #VALUE! | 0.67022 | 0.78528 | 0.96293 | 0.0002083 | 1.724 | 4 | 0.0013928 | 620.1576 | 673.0826 | 771.1667 | 1 | 1 | 1 | 698 | 758 | 868 | 300 | 326 | 373 | 1.4653 | 1.724 | 2.2439 | 3.4 | 16.9 | 18.9 | 30 |  | 1268 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 698 | 758 | 868 |  | 0 | 0 | 0 | 1 | [10 empty] | 28015 | 280 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5 |  |  |  |  | 160 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 3.6
119016 |  |  | 1 | 190 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 37 | 2421.5581 | 2421.5581 | 2636.5863 | 2926.6667 | N/A | 1 | 1 | 1 | #VALUE! | 1333 | 1451 | 1611 | #VALUE! | 229 | 250 | 277 | #VALUE! | 0.88361 | 1.0483 | 1.2803 | 0.0002083 | 1.724 | 4 | 0.0013928 | 708.7516 | 769.2373 | 881.3334 | 1 | 1 | 1 | 798 | 866 | 993 | 343 | 372 | 427 | 1.9426 | 2.2762 | 2.98 | 3.8 | 16.9 | 18.9 | 30 |  | 1549 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 798 | 866 | 993 |  | 0 | 0 | 0 | 1 | [10 empty] | 30010 | 300 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 |  |  |  |  | 160 | 12.3 | 1351 | 232 | 0.80724 | 879 | 378 | 1.9803 | 26 | 34 | 26.6941 | 3.6
121016 |  |  | 1 | 210 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 37 | 2669.5314 | 2669.5314 | 2909.964 | 3292.5 | N/A | 1 | 1 | 1 | #VALUE! | 1469 | 1601 | 1812 | #VALUE! | 253 | 275 | 312 | #VALUE! | 1.0957 | 1.2885 | 1.6473 | 0.0002083 | 1.724 | 4 | 0.0013928 | 783.5261 | 848.374 | 991.4999 | 1 | 1 | 1 | 882 | 955 | 1117 | 379 | 411 | 480 | 2.4062 | 2.8181 | 3.8144 | 4.2 | 19.3 | 21.3 | 36 |  | 1818 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 882 | 955 | 1117 |  | 0 | 0 | 0 | 1 | [10 empty] | 30015 | 300 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5 |  |  |  |  | 160 | 14.4 | 1521 | 262 | 1.0091 | 978 | 421 | 2.4153 | 30 | 38 | 31.4391 | 3.6
123016 |  |  | 1 | 230 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 37.9206 | 2918.8231 | 2918.8231 | 3177.4564 | 3658.3333 | N/A | 1 | 1 | 1 | #VALUE! | 1606 | 1749 | 2013 | #VALUE! | 276 | 301 | 346 | #VALUE! | 1.324 | 1.5668 | 2.0538 | 0.0002083 | 1.724 | 4 | 0.0013928 | 858.9837 | 926.4939 | 1101.6666 | 1 | 1 | 1 | 967 | 1043 | 1241 | 416 | 448 | 534 | 2.9388 | 3.3948 | 4.7792 | 4.6 | 21.6 | 23.6 | 42 |  | 2352 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 967 | 1043 | 1241 |  | 0 | 0 | 0 | 1 | [23 empty] | 160 | 21.85 | 1963 | 338 | 1.6117 | 1173 | 504 | 3.3668 | 40.8451 | 48.8451 | 49.4 | 3.6
125016 |  |  | 1 | 250 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 38.699 | 3189.1985 | 3189.1985 | 3467.538 | 4024.1666 | N/A | 1 | 1 | 1 | #VALUE! | 1755 | 1908 | 2215 | #VALUE! | 302 | 328 | 381 | #VALUE! | 1.6077 | 1.8868 | 2.5229 | 0.0002083 | 1.724 | 4 | 0.0013928 | 939.7017 | 1011.3774 | 1211.8334 | 1 | 1 | 1 | 1058 | 1139 | 1365 | 455 | 490 | 587 | 3.5612 | 4.1129 | 5.8442 | 5 | 22.7 | 24.7 | 45 |  | 629 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 1058 | 1139 | 1365 |  | 0 | 0 | 0 | 1 | [23 empty] | 180 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 3.9
127016 |  |  | 1 | 270 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 38.699 | 3479.1256 | 3479.1256 | 3782.7687 | 4389.9999 | N/A | 1 | 1 | 1 | #VALUE! | 1915 | 2082 | 2416 | #VALUE! | 329 | 358 | 416 | #VALUE! | 1.9337 | 2.2771 | 3.0458 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1025.129 | 1103.3206 | 1321.9999 | 1 | 1 | 1 | 1154 | 1243 | 1489 | 496 | 534 | 640 | 4.2838 | 4.9437 | 7.0276 | 5.4 | 22.7 | 24.7 | 45 |  | 753 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 1154 | 1243 | 1489 |  | 0 | 0 | 0 | 1 | [23 empty] | 180 | 12.3 | 1463 | 252 | 0.98505 | 952 | 409 | 2.3954 | 26 | 34 | 26.69 | 3.9
129016 |  |  | 1 | 290 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 39.0474 | 3707.9681 | 3707.9681 | 4011.8787 | 4755.8335 | N/A | 1 | 1 | 1 | #VALUE! | 2041 | 2208 | 2617 | #VALUE! | 351 | 380 | 450 | #VALUE! | 2.2316 | 2.6016 | 3.6081 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1096.0869 | 1171.823 | 1432.1666 | 1 | 1 | 1 | 1234 | 1320 | 1613 | 531 | 568 | 694 | 4.9714 | 5.6647 | 8.3554 | 5.8 | 26.2 | 27.9 | 54 |  | 848 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 1234 | 1320 | 1613 |  | 0 | 0 | 0 | 1 | [10 empty] | L,rail/L,tot | T10 | T11 | T15 | T16 | T20 | T21 | ALS | [5 empty] | 180 | 14.4 | 1647 | 283 | 1.2183 | 1060 | 456 | 2.9261 | 30 | 38 | 31.44 | 3.9
19510 |  |  | 1 | 95 | 40.5 | 10 | 16.5 | 0 | 26 | 30 | 41 | 877.5 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.052409 | 0.059791 | 0.08345 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.026843 | 0.030669 | 0.043605 | 0.6 | 5.5 | 5.9 | 7.9 |  | 975 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 90% | 68% | 80% | 68% | 80% | 80% | #REF! | T10 |  |  |  |  | 180 | 21.85 | 2126 | 366 | 1.953 | 1271 | 547 | 4.0914 | 40.8451 | 48.8451 | 49.4 | 3.9
13511 |  |  | 1 | 35 | 40.5 | 11 | 16.5 | 0 | 26 | 30 | 41 | 569.16 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.11334 | 0.13083 | 0.18635 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.084992 | 0.097098 | 0.13632 | 0.5 | 5.5 | 5.9 | 7.9 |  | 837 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1 | [10 empty] | 0.8 | 92% | 74.4% | 84% | 74.4% | 84% | 84% | #REF! | T11 |  |  |  |  | 200 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15011 |  |  | 1 | 50 | 40.5 | 11 | 16.5 | 0 | 26 | 30 | 41 | 659.6 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.12447 | 0.14346 | 0.20361 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.093622 | 0.1068 | 0.14941 | 0.7 | 5.5 | 5.9 | 7.9 |  | 970 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1 | [10 empty] | 0.6 | 94% | 80.8% | 88% | 80.8% | 88% | 88% | #REF! | T15 |  |  |  |  | 200 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16511 |  |  | 1 | 65 | 40.5 | 11 | 16.5 | 0 | 26 | 30 | 41 | 734.4 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.1356 | 0.15609 | 0.22087 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216.4625 | 232.1327 | 277.537 | 1 | 1 | 1 | 244 | 261 | 313 | 105 | 112 | 135 | 0.087288 | 0.098827 | 0.1416 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1080 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 244 | 261 | 313 |  | 0 | 0 | 0 | 1 | [10 empty] | 0.4 | 96% | 87.2% | 92% | 87.2% | 92% | 92% | #REF! | T16 |  |  |  |  | 200 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19511 |  |  | 1 | 95 | 40.5 | 11 | 16.5 | 0 | 26 | 30 | 41 | 854.76 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.15786 | 0.18135 | 0.25538 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.3604 | 194.4896 | 232.531 | 1 | 1 | 1 | 204 | 219 | 262 | 88 | 94 | 113 | 0.073177 | 0.08291 | 0.11753 | 1.3 | 5.5 | 5.9 | 7.9 |  | 1257 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 204 | 219 | 262 |  | 0 | 0 | 0 | 1 | [10 empty] | 0.2 | 98% | 93.6% | 96% | 93.6% | 96% | 96% | #REF! | T20 |  |  |  |  | 200 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.048569 | 0.05651 | 0.098274 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.020245 | 0.023453 | 0.041227 | 0.4 | 5.1 | 5.6 | 7.2 |  | 1029 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1 | [10 empty] | 0 | 100% | 100% | 100% | 100% | 100% | 100% | #REF! | T21 |  |  |  |  | 220 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.050317 | 0.058503 | 0.1015 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.021062 | 0.024382 | 0.042743 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1214 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1 | [23 empty] | 220 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.052065 | 0.060496 | 0.10472 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.02188 | 0.025311 | 0.044259 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1345 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1 | [23 empty] | 220 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.05556 | 0.064483 | 0.11116 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.023515 | 0.027169 | 0.047291 | 1 | 5.1 | 5.6 | 7.2 |  | 1502 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1 | [23 empty] | 220 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 758.2 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.33364 | 0.38279 | 0.67287 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.15858 | 0.1833 | 0.32082 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1115 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1 | [10 empty] | Lengths | Calculation factors for lower fan settings | [11 empty] | 240 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.34088 | 0.39094 | 0.68614 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.16238 | 0.18761 | 0.32782 | 1 | 5.1 | 5.6 | 7.2 |  | 1329 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1 | [11 empty] | T10 |  | T11 |  | T15 |  | T16 |  | T20 |  | T21 |  | 240 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1034.28 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.34811 | 0.39909 | 0.69942 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.1279 | 218.0533 | 288.6 | 1 | 1 | 1 | 229 | 246 | 325 | 98 | 106 | 140 | 0.14228 | 0.16618 | 0.28823 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1521 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 229 | 246 | 325 |  | 0 | 0 | 0 | 1 | [11 empty] | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | 240 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1274.32 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.36258 | 0.41538 | 0.72596 | 0.0002083 | 1.724 | 4 | 0.0013928 | 170.1882 | 182.6933 | 241.8 | 1 | 1 | 1 | 192 | 206 | 272 | 83 | 89 | 117 | 0.10742 | 0.12322 | 0.21105 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1874 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 272 |  | 0 | 0 | 0 | 1 | [10 empty] | 50 | 0.85519 | 0.79918 | 0.85519 | 0.79918 | [8 empty] | 240 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1153.6 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.078123 | 0.089375 | 0.12765 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.026464 | 0.030406 | 0.043052 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1442 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 60 | 0.84525 | 0.7893 | 0.84525 | 0.7893 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.84525 | 0.7893 | 0.75556 | 0.70384 | 260 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.080053 | 0.091543 | 0.1306 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027221 | 0.031259 | 0.044205 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1698 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 70 | 0.8364 | 0.77994 | 0.8364 | 0.77994 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.8364 | 0.77994 | 0.75556 | 0.70384 | 260 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.081982 | 0.09371 | 0.13355 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027977 | 0.032112 | 0.045357 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1880 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 80 | 0.82846 | 0.77134 | 0.82846 | 0.77134 | 0.74531 | 0.69504 | 0.74531 | 0.69504 | 0.82846 | 0.77134 | 0.74531 | 0.69504 | 260 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.085841 | 0.098046 | 0.13946 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.029489 | 0.033817 | 0.047661 | 1.3 | 5.1 | 5.6 | 7.2 |  | 2094 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 90 | 0.82124 | 0.76344 | 0.82124 | 0.76344 | 0.7343 | 0.6854 | 0.7343 | 0.6854 | 0.82124 | 0.76344 | 0.7343 | 0.6854 | 260 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1184 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.18463 | 0.21311 | 0.37198 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.072733 | 0.082941 | 0.14571 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1480 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1 | [10 empty] | 100 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 280 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19075 | 0.22005 | 0.38322 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.075464 | 0.086002 | 0.1507 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1807 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1 | [10 empty] | 110 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1696.8 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19688 | 0.22698 | 0.39446 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.2818 | 238.6146 | 315.8135 | 1 | 1 | 1 | 250 | 269 | 356 | 108 | 116 | 153 | 0.066805 | 0.076887 | 0.13259 | 1.7 | 5.1 | 5.6 | 7.2 |  | 2121 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 250 | 269 | 356 |  | 0 | 0 | 0 | 1 | [10 empty] | 120 | 0.80301 | 0.7433 | 0.80301 | 0.7433 | 0.71879 | 0.67123 | 0.71879 | 0.67123 | 0.80301 | 0.7433 | 0.71879 | 0.67123 | 280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.20913 | 0.24086 | 0.41693 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 186.2361 | 199.9203 | 264.6005 | 1 | 1 | 1 | 210 | 225 | 298 | 90 | 97 | 128 | 0.05016 | 0.058043 | 0.099696 | 2.5 | 5.1 | 5.6 | 7.2 |  | 2744 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 210 | 225 | 298 |  | 0 | 0 | 0 | 1 | [10 empty] | 140 | 0.79292 | 0.73212 | 0.79292 | 0.73212 | 0.71271 | 0.66551 | 0.71271 | 0.66551 | 0.79292 | 0.73212 | 0.71271 | 0.66551 | 280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 646.2 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.053626 | 0.061225 | 0.089351 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.027552 | 0.03166 | 0.045672 | 0.2 | 6.3 | 6.8 | 9.1 |  | 718 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 160 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 300 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.058006 | 0.066147 | 0.096216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.029989 | 0.034414 | 0.049475 | 0.3 | 6.3 | 6.8 | 9.1 |  | 861 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 180 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 872.1 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.062387 | 0.071069 | 0.10308 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.032425 | 0.037168 | 0.053278 | 0.4 | 6.3 | 6.8 | 9.1 |  | 969 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 200 | 0.76886 | 0.70539 | 0.76886 | 0.70539 | 0.69292 | 0.65762 | 0.69292 | 0.65762 | 0.76886 | 0.70539 | 0.69292 | 0.65762 | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1002.6 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.071147 | 0.080914 | 0.11681 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.037297 | 0.042675 | 0.060884 | 0.6 | 6.3 | 6.8 | 9.1 |  | 1114 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1 | [10 empty] | 220 | 0.75856 | 0.69426 | 0.75856 | 0.69426 | 0.68521 | 0.65781 | 0.68521 | 0.65781 | 0.75856 | 0.69426 | 0.68521 | 0.65781 | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 650.76 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.15738 | 0.18206 | 0.26161 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.11674 | 0.13265 | 0.19287 | 0.5 | 6.3 | 6.8 | 9.1 |  | 957 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1 | [10 empty] | 240 | 0.75028 | 0.68489 | 0.75028 | 0.68489 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75028 | 0.68489 | 0.6819 | 0.65797 | [11 empty] | v2020-09-17
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.17225 | 0.19897 | 0.28489 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.12816 | 0.14543 | 0.21066 | 0.7 | 6.3 | 6.8 | 9.1 |  | 1109 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1 | [10 empty] | 260 | 0.75 | 0.68 | 0.75 | 0.68 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75 | 0.68 | 0.6819 | 0.65797 | * | 0
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 839.12 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.18712 | 0.21588 | 0.30817 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255.3 | 273.8 | 331.15 | 1 | 1 | 1 | 288 | 308 | 373 | 124 | 132 | 160 | 0.12022 | 0.1356 | 0.19648 | 0.9 | 6.3 | 6.8 | 9.1 |  | 1234 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 288 | 308 | 373 |  | 0 | 0 | 0 | 1 | [10 empty] | 280 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821 | ** | 0
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 977.16 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.21685 | 0.2497 | 0.35472 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 213.9 | 229.4 | 277.45 | 1 | 1 | 1 | 241 | 258 | 312 | 104 | 111 | 134 | 0.10041 | 0.11361 | 0.16243 | 1.3 | 6.3 | 6.8 | 9.1 |  | 1437 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 241 | 258 | 312 |  | 0 | 0 | 0 | 1 | [10 empty] | 300 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821 | *** | 0
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 940.8 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.082668 | 0.095579 | 0.17052 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.040351 | 0.046678 | 0.083917 | 0.4 | 6 | 6.7 | 9 |  | 1176 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1 | [23 empty] | **** | 0
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.08544 | 0.098724 | 0.17572 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.041839 | 0.048366 | 0.086726 | 0.5 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1 | [10 empty] | Type,ww | L/cm
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1230.4 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.088213 | 0.10187 | 0.18091 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.043327 | 0.050055 | 0.089535 | 0.7 | 6 | 6.7 | 9 |  | 1538 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1 | [10 empty] | 10 | 0.0066667
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1300.3374 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.093758 | 0.10816 | 0.1913 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.046303 | 0.053432 | 0.095153 | 1 | 6 | 6.7 | 9 |  | 1717 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1 | [10 empty] | 11 | 0.013333
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 866.32 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.52309 | 0.6014 | 1.0824 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32082 | 0.36906 | 0.66676 | 0.7 | 6 | 6.7 | 9 |  | 1274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1 | [10 empty] | 15 | 0.01
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.53376 | 0.61345 | 1.1024 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32782 | 0.37695 | 0.67993 | 1 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1 | [10 empty] | 16 | 0.02
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1181.84 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.54444 | 0.62549 | 1.1224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 288.6 | 309.875 | 416.25 | 1 | 1 | 1 | 325 | 349 | 469 | 140 | 150 | 202 | 0.28823 | 0.33043 | 0.5959 | 1.3 | 6 | 6.7 | 9 |  | 1738 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 325 | 349 | 469 |  | 0 | 0 | 0 | 1 | [10 empty] | 20 | 0.013333
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1456.56 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.56579 | 0.64958 | 1.1625 | 0.0002083 | 1.724 | 4 | 0.0013928 | 241.8 | 259.625 | 348.75 | 1 | 1 | 1 | 272 | 292 | 393 | 117 | 126 | 169 | 0.21105 | 0.2442 | 0.43546 | 1.9 | 6 | 6.7 | 9 |  | 2142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 272 | 292 | 393 |  | 0 | 0 | 0 | 1 | [10 empty] | 21 | 0.026667
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1318.4 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.12905 | 0.14784 | 0.21543 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.051512 | 0.059771 | 0.087064 | 0.5 | 6 | 6.7 | 9 |  | 1648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13202 | 0.15119 | 0.22007 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.052857 | 0.061301 | 0.089183 | 0.7 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1718.4 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.135 | 0.15454 | 0.22471 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.054203 | 0.062832 | 0.091303 | 0.9 | 6 | 6.7 | 9 |  | 2148 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1 | [10 empty] | Niveaus | Type | k1 | n | t | k2
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1847.5719 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.14096 | 0.16124 | 0.23399 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.056895 | 0.065893 | 0.095541 | 1.3 | 6 | 6.7 | 9 |  | 2394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1352.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.32621 | 0.37477 | 0.67158 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14397 | 0.16552 | 0.29569 | 0.9 | 6 | 6.7 | 9 |  | 1691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 row
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.33623 | 0.38608 | 0.69032 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14891 | 0.1711 | 0.30491 | 1.3 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 4 | 0.0013823 | 1.7232 | 1 | 0.00033291
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1939.2 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.34626 | 0.39739 | 0.70905 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315.2976 | 338.1017 | 453.6385 | 1 | 1 | 1 | 355 | 381 | 511 | 153 | 164 | 220 | 0.13259 | 0.15202 | 0.27123 | 1.7 | 6 | 6.7 | 9 |  | 2424 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 355 | 381 | 511 |  | 0 | 0 | 0 | 1 | [10 empty] | 2 | 5 | 0.000937 | 1.789 | 2 | 0.000446
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2508.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.36632 | 0.42001 | 0.74653 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264.1682 | 283.2744 | 380.0755 | 1 | 1 | 1 | 298 | 319 | 428 | 128 | 137 | 184 | 0.099696 | 0.11384 | 0.20261 | 2.5 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298 | 319 | 428 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 | 6 | 0.000937 | 1.789 | 4 | 0.00139
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 727.2 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.070367 | 0.081263 | 0.11996 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.03605 | 0.041526 | 0.061225 | 0.2 | 6.7 | 7.4 | 10.3 |  | 808 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1 | [10 empty] | 2 rows
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.075931 | 0.087579 | 0.12886 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.039137 | 0.045024 | 0.066147 | 0.3 | 6.7 | 7.4 | 10.3 |  | 968 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 9 | 0.00080534 | 1.8139 | 2 | 0.00039795
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 981 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.081495 | 0.093894 | 0.13775 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.042225 | 0.048521 | 0.071069 | 0.4 | 6.7 | 7.4 | 10.3 |  | 1090 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1 | [10 empty] | 2 | 10 | 0.0003969 | 1.7346 | 2 | 0.00036735
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1128.6 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.092623 | 0.10652 | 0.15554 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.0484 | 0.055515 | 0.080914 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1254 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 | 11 | 0.0003969 | 1.7346 | 4 | 0.00057429
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 731.68 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.20625 | 0.23917 | 0.35237 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.15344 | 0.17573 | 0.25907 | 0.5 | 6.7 | 7.4 | 10.3 |  | 1076 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1 | [10 empty] | 3 rows
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.22512 | 0.26068 | 0.38263 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.16798 | 0.19212 | 0.28215 | 0.7 | 6.7 | 7.4 | 10.3 |  | 1247 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 14 | 0.0025582 | 1.4943 | 3 | 0.00056162
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 944.52 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.24399 | 0.28219 | 0.41289 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 293.3758 | 315.5893 | 384.282 | 1 | 1 | 1 | 330 | 355 | 433 | 142 | 153 | 186 | 0.15609 | 0.18024 | 0.26275 | 0.9 | 6.7 | 7.4 | 10.3 |  | 1389 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 330 | 355 | 433 |  | 0 | 0 | 0 | 1 | [10 empty] | 2 | 15 | 0.0002083 | 1.724 | 2 | 0.00046183
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1098.88 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.28174 | 0.3252 | 0.47342 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 245.8013 | 264.4127 | 321.966 | 1 | 1 | 1 | 277 | 298 | 363 | 119 | 128 | 156 | 0.12965 | 0.14889 | 0.21685 | 1.3 | 6.7 | 7.4 | 10.3 |  | 1616 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 277 | 298 | 363 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 | 16 | 0.0002083 | 1.724 | 4 | 0.0013928
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1058.4 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.108 | 0.1242 | 0.23031 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.053462 | 0.060704 | 0.1123 | 0.4 | 7 | 7.7 | 10.7 |  | 1323 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 rows
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11149 | 0.12815 | 0.23705 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.055362 | 0.062825 | 0.11592 | 0.5 | 7 | 7.7 | 10.7 |  | 1561 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 19 | 0.011616 | 1.5869 | 1 | 0.0016553
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1384 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11499 | 0.13209 | 0.24379 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.057261 | 0.064946 | 0.11954 | 0.7 | 7 | 7.7 | 10.7 |  | 1730 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1 | [10 empty] | 2 | 20 | 0.0001276 | 1.7219 | 2 | 0.00037661
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1502.9168 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.12198 | 0.13999 | 0.25728 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.061061 | 0.069188 | 0.12677 | 1 | 7 | 7.7 | 10.7 |  | 1931 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 | 21 | 0.0001276 | 1.7219 | 4 | 0.0005142
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 975.12 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.68517 | 0.78756 | 1.4596 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.42065 | 0.48597 | 0.89706 | 0.7 | 7 | 7.7 | 10.7 |  | 1434 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.69865 | 0.80277 | 1.4856 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.42949 | 0.49599 | 0.91409 | 1 | 7 | 7.7 | 10.7 |  | 1708 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1 | [10 empty] | 1 | 7 | 0.0025582 | 1.4943 | 3 | 0.00056162
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1330.08 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.71213 | 0.81798 | 1.5115 | 0.0002083 | 1.724 | 4 | 0.0013928 | 330.9459 | 354.5558 | 482.85 | 1 | 1 | 1 | 373 | 399 | 544 | 160 | 172 | 234 | 0.37549 | 0.43333 | 0.79758 | 1.3 | 7 | 7.7 | 10.7 |  | 1956 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 373 | 399 | 544 |  | 0 | 0 | 0 | 1 | [10 empty] | 4 | 8 | 0.000937 | 1.789 | 4 | 0.00139
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1638.12 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.7391 | 0.8484 | 1.5634 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277.279 | 297.0603 | 404.55 | 1 | 1 | 1 | 312 | 335 | 456 | 134 | 144 | 196 | 0.27567 | 0.31765 | 0.58326 | 1.9 | 7 | 7.7 | 10.7 |  | 2409 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 456 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1483.2 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.1695 | 0.19605 | 0.29146 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.068641 | 0.079214 | 0.11678 | 0.5 | 7 | 7.7 | 10.7 |  | 1854 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17327 | 0.20033 | 0.29749 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.070366 | 0.081167 | 0.11951 | 0.7 | 7 | 7.7 | 10.7 |  | 2183 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1933.6 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17704 | 0.20461 | 0.30351 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.072092 | 0.08312 | 0.12225 | 0.9 | 7 | 7.7 | 10.7 |  | 2417 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2137.7837 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.18458 | 0.21316 | 0.31556 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.075542 | 0.087026 | 0.12771 | 1.3 | 7 | 7.7 | 10.7 |  | 2693 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1522.4 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.42668 | 0.4883 | 0.90539 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.18857 | 0.21735 | 0.40031 | 0.9 | 7 | 7.7 | 10.7 |  | 1903 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.43934 | 0.50252 | 0.92966 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.19481 | 0.2244 | 0.41228 | 1.3 | 7 | 7.7 | 10.7 |  | 2324 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2181.6 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.45199 | 0.51674 | 0.95392 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 361.0734 | 386.8326 | 526.806 | 1 | 1 | 1 | 407 | 436 | 593 | 175 | 187 | 255 | 0.17276 | 0.19688 | 0.36292 | 1.7 | 7 | 7.7 | 10.7 |  | 2727 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 407 | 436 | 593 |  | 0 | 0 | 0 | 1
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2822.4 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.4773 | 0.54519 | 1.0025 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 302.521 | 324.103 | 441.378 | 1 | 1 | 1 | 341 | 365 | 497 | 147 | 157 | 214 | 0.13064 | 0.14857 | 0.27229 | 2.5 | 7 | 7.7 | 10.7 |  | 3528 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 497 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 808.2 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.089351 | 0.10283 | 0.15502 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.045672 | 0.052711 | 0.079022 | 0.2 | 7.8 | 8.7 | 12.2 |  | 898 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.096216 | 0.1106 | 0.16616 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.049475 | 0.057025 | 0.085184 | 0.3 | 7.8 | 8.7 | 12.2 |  | 1076 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1089.9 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.10308 | 0.11836 | 0.1773 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.053278 | 0.06134 | 0.091346 | 0.4 | 7.8 | 8.7 | 12.2 |  | 1211 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1253.7 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.11681 | 0.1339 | 0.19959 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.060884 | 0.069969 | 0.10367 | 0.6 | 7.8 | 8.7 | 12.2 |  | 1393 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 813.28 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.26161 | 0.30395 | 0.45308 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.19287 | 0.22477 | 0.33488 | 0.5 | 7.8 | 8.7 | 12.2 |  | 1196 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.28489 | 0.33052 | 0.49084 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.21066 | 0.24513 | 0.36381 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1386 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1049.24 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.30817 | 0.35709 | 0.52861 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 331.15 | 356.125 | 437.525 | 1 | 1 | 1 | 373 | 401 | 493 | 160 | 172 | 212 | 0.19648 | 0.22591 | 0.33833 | 0.9 | 7.8 | 8.7 | 12.2 |  | 1543 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 373 | 401 | 493 |  | 0 | 0 | 0 | 1
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1221.28 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.35472 | 0.41022 | 0.60414 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277.45 | 298.375 | 366.575 | 1 | 1 | 1 | 312 | 336 | 413 | 134 | 144 | 178 | 0.16243 | 0.18624 | 0.27875 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1796 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 312 | 336 | 413 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1176 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.13669 | 0.15654 | 0.29667 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.067276 | 0.076561 | 0.1448 | 0.4 | 7 | 7.7 | 10.7 |  | 1470 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14098 | 0.16137 | 0.30506 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.069595 | 0.079155 | 0.14931 | 0.5 | 7 | 7.7 | 10.7 |  | 1734 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1537.6 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14527 | 0.16619 | 0.31346 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.071914 | 0.08175 | 0.15382 | 0.7 | 7 | 7.7 | 10.7 |  | 1922 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1703.7737 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.15384 | 0.17584 | 0.33025 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.076552 | 0.086938 | 0.16283 | 1 | 7 | 7.7 | 10.7 |  | 2146 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1083.24 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.86902 | 0.99871 | 1.8931 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.53394 | 0.61304 | 1.1614 | 0.7 | 7 | 7.7 | 10.7 |  | 1593 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.88558 | 1.0174 | 1.9255 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.54481 | 0.62528 | 1.1827 | 1 | 7 | 7.7 | 10.7 |  | 1898 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1477.64 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.90215 | 1.0361 | 1.958 | 0.0002083 | 1.724 | 4 | 0.0013928 | 372.775 | 398.675 | 550.375 | 1 | 1 | 1 | 420 | 449 | 620 | 181 | 193 | 267 | 0.47941 | 0.54444 | 1.0361 | 1.3 | 7 | 7.7 | 10.7 |  | 2173 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 420 | 449 | 620 |  | 0 | 0 | 0 | 1
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1820.36 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.93527 | 1.0734 | 2.023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312.325 | 334.025 | 461.125 | 1 | 1 | 1 | 352 | 376 | 519 | 151 | 162 | 223 | 0.34879 | 0.40063 | 0.75236 | 1.9 | 7 | 7.7 | 10.7 |  | 2677 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 352 | 376 | 519 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1648 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21543 | 0.25104 | 0.37654 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.087064 | 0.10138 | 0.15235 | 0.5 | 7 | 7.7 | 10.7 |  | 2060 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22007 | 0.25634 | 0.38406 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.089183 | 0.1038 | 0.15579 | 0.7 | 7 | 7.7 | 10.7 |  | 2425 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2148 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22471 | 0.26163 | 0.39158 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.091303 | 0.10622 | 0.15923 | 0.9 | 7 | 7.7 | 10.7 |  | 2685 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2393.6 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.23399 | 0.27222 | 0.40661 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.095541 | 0.11105 | 0.16611 | 1.3 | 7 | 7.7 | 10.7 |  | 2992 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.54057 | 0.61676 | 1.169 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.23915 | 0.27379 | 0.51738 | 0.9 | 7 | 7.7 | 10.7 |  | 2114 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.5561 | 0.63417 | 1.1993 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.24681 | 0.28241 | 0.53233 | 1.3 | 7 | 7.7 | 10.7 |  | 2582 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2424 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.57163 | 0.65158 | 1.2295 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 406.4601 | 435.2289 | 599.9735 | 1 | 1 | 1 | 458 | 490 | 676 | 197 | 211 | 291 | 0.21817 | 0.24979 | 0.47097 | 1.7 | 7 | 7.7 | 10.7 |  | 3030 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 458 | 490 | 676 |  | 0 | 0 | 0 | 1
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3136 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.60269 | 0.68639 | 1.2901 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.5476 | 364.6513 | 502.6805 | 1 | 1 | 1 | 384 | 411 | 566 | 165 | 177 | 243 | 0.16372 | 0.18781 | 0.34923 | 2.5 | 7 | 7.7 | 10.7 |  | 3920 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 384 | 411 | 566 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 889.2 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.11189 | 0.12973 | 0.19451 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.057363 | 0.066226 | 0.09906 | 0.2 | 8.4 | 9.3 | 14 |  | 988 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12026 | 0.13925 | 0.20811 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.062011 | 0.071501 | 0.10658 | 0.3 | 8.4 | 9.3 | 14 |  | 1184 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1198.8 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12862 | 0.14878 | 0.22171 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.066659 | 0.076776 | 0.11409 | 0.4 | 8.4 | 9.3 | 14 |  | 1332 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1378.8 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.14536 | 0.16784 | 0.24892 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.075955 | 0.087325 | 0.12913 | 0.6 | 8.4 | 9.3 | 14 |  | 1532 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 894.88 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.32914 | 0.37943 | 0.57 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.24162 | 0.27975 | 0.42027 | 0.5 | 8.4 | 9.3 | 14 |  | 1316 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.35764 | 0.41173 | 0.61623 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.26332 | 0.30444 | 0.45561 | 0.7 | 8.4 | 9.3 | 14 |  | 1525 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1153.96 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.38614 | 0.44403 | 0.66245 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 371.314 | 400.0249 | 491.027 | 1 | 1 | 1 | 418 | 451 | 553 | 180 | 194 | 238 | 0.24663 | 0.28502 | 0.42315 | 0.9 | 8.4 | 9.3 | 14 |  | 1697 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 418 | 451 | 553 |  | 0 | 0 | 0 | 1
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1343.68 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.44314 | 0.50864 | 0.7549 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 311.1009 | 335.156 | 411.401 | 1 | 1 | 1 | 350 | 377 | 463 | 151 | 162 | 199 | 0.20383 | 0.233 | 0.34474 | 1.3 | 8.4 | 9.3 | 14 |  | 1976 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 350 | 377 | 463 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1293.6 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15484 | 0.17592 | 0.33548 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.069541 | 0.078976 | 0.14978 | 0.4 | 7.9 | 8.8 | 12.5 |  | 1617 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15961 | 0.18125 | 0.34482 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.071928 | 0.081641 | 0.15442 | 0.5 | 7.9 | 8.8 | 12.5 |  | 1907 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.16439 | 0.18659 | 0.35416 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.074314 | 0.084306 | 0.15906 | 0.7 | 7.9 | 8.8 | 12.5 |  | 2114 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1813.1502 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.17395 | 0.19727 | 0.37283 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.079087 | 0.089636 | 0.16835 | 1 | 7.9 | 8.8 | 12.5 |  | 2361 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1191.36 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0212 | 1.1694 | 2.2132 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.54491 | 0.6307 | 1.1937 | 0.7 | 7.9 | 8.8 | 12.5 |  | 1752 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0402 | 1.1908 | 2.2504 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.55597 | 0.64325 | 1.2155 | 1 | 7.9 | 8.8 | 12.5 |  | 2088 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1625.2 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0593 | 1.2122 | 2.2875 | 0.0002083 | 1.724 | 4 | 0.0013928 | 377.2455 | 403.9466 | 556.85 | 1 | 1 | 1 | 425 | 455 | 627 | 183 | 196 | 270 | 0.48996 | 0.56134 | 1.0593 | 1.3 | 7.9 | 8.8 | 12.5 |  | 2390 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 425 | 455 | 627 |  | 0 | 0 | 0 | 1
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2002.6 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0974 | 1.2551 | 2.3619 | 0.0002083 | 1.724 | 4 | 0.0013928 | 316.0705 | 338.4417 | 466.55 | 1 | 1 | 1 | 356 | 381 | 525 | 153 | 164 | 226 | 0.35795 | 0.41044 | 0.77246 | 1.9 | 7.9 | 8.8 | 12.5 |  | 2945 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 356 | 381 | 525 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1812.8 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24717 | 0.28729 | 0.43075 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.090541 | 0.10513 | 0.15694 | 0.5 | 7.9 | 8.8 | 12.5 |  | 2266 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25239 | 0.29324 | 0.4392 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.092734 | 0.10762 | 0.16047 | 0.7 | 7.9 | 8.8 | 12.5 |  | 2668 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2363.2 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25762 | 0.29919 | 0.44764 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.094926 | 0.11012 | 0.16399 | 0.9 | 7.9 | 8.8 | 12.5 |  | 2954 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2597.5513 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.26806 | 0.31108 | 0.46453 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.09931 | 0.11511 | 0.17105 | 1.3 | 7.9 | 8.8 | 12.5 |  | 3291 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1860 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.59549 | 0.68282 | 1.29 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.24589 | 0.281 | 0.53389 | 0.9 | 7.9 | 8.8 | 12.5 |  | 2325 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.61237 | 0.70183 | 1.323 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.25374 | 0.28981 | 0.54925 | 1.3 | 7.9 | 8.8 | 12.5 |  | 2840 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2666.4 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.62926 | 0.72084 | 1.3559 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 412.2253 | 441.4022 | 608.4835 | 1 | 1 | 1 | 464 | 497 | 685 | 200 | 214 | 295 | 0.22476 | 0.25684 | 0.48383 | 1.7 | 7.9 | 8.8 | 12.5 |  | 3333 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 464 | 497 | 685 |  | 0 | 0 | 0 | 1
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3449.6 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.66303 | 0.75886 | 1.4219 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345.378 | 369.8235 | 509.8105 | 1 | 1 | 1 | 389 | 416 | 574 | 167 | 179 | 247 | 0.16762 | 0.19199 | 0.36058 | 2.5 | 7.9 | 8.8 | 12.5 |  | 4312 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 389 | 416 | 574 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 970.2 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.13259 | 0.15502 | 0.23843 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.06725 | 0.079022 | 0.12133 | 0.2 | 8.9 | 9.9 | 14.8 |  | 1078 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.1423 | 0.16616 | 0.25469 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.072596 | 0.085184 | 0.13032 | 0.3 | 8.9 | 9.9 | 14.8 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1307.7 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.15201 | 0.1773 | 0.27096 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.077943 | 0.091346 | 0.1393 | 0.4 | 8.9 | 9.9 | 14.8 |  | 1453 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1504.8 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.17144 | 0.19959 | 0.30349 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.088635 | 0.10367 | 0.15727 | 0.6 | 8.9 | 9.9 | 14.8 |  | 1672 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 975.8 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.38867 | 0.45308 | 0.70017 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.28771 | 0.33488 | 0.51521 | 0.5 | 8.9 | 9.9 | 14.8 |  | 1435 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.42166 | 0.49084 | 0.75556 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.31302 | 0.36381 | 0.5575 | 0.7 | 8.9 | 9.9 | 14.8 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1259.36 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.45466 | 0.52861 | 0.81096 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 404.225 | 437.525 | 544.825 | 1 | 1 | 1 | 455 | 493 | 614 | 196 | 212 | 264 | 0.29072 | 0.33833 | 0.51717 | 0.9 | 8.9 | 9.9 | 14.8 |  | 1852 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 455 | 493 | 614 |  | 0 | 0 | 0 | 1
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1465.4 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.52065 | 0.60414 | 0.92176 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 338.675 | 366.575 | 456.475 | 1 | 1 | 1 | 381 | 413 | 514 | 164 | 178 | 221 | 0.2385 | 0.27875 | 0.42106 | 1.3 | 8.9 | 9.9 | 14.8 |  | 2155 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 381 | 413 | 514 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1411.2 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.20807 | 0.23867 | 0.46027 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10238 | 0.11669 | 0.22413 | 0.4 | 8.7 | 9.8 | 14.3 |  | 1764 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.21425 | 0.24563 | 0.47256 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10572 | 0.12043 | 0.23072 | 0.5 | 8.7 | 9.8 | 14.3 |  | 2081 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.22042 | 0.25258 | 0.48484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10906 | 0.12417 | 0.2373 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2306 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2060 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.23277 | 0.26649 | 0.50941 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.11574 | 0.13165 | 0.25047 | 1 | 8.7 | 9.8 | 14.3 |  | 2575 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1300.16 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3191 | 1.5142 | 2.9155 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.80755 | 0.93274 | 1.7919 | 0.7 | 8.7 | 9.8 | 14.3 |  | 1912 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3428 | 1.541 | 2.9626 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.8231 | 0.95035 | 1.8229 | 1 | 8.7 | 9.8 | 14.3 |  | 2278 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1773.44 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3666 | 1.5677 | 3.0098 | 0.0002083 | 1.724 | 4 | 0.0013928 | 458.8 | 492.1 | 684.5 | 1 | 1 | 1 | 517 | 554 | 771 | 222 | 238 | 332 | 0.71854 | 0.82484 | 1.5962 | 1.3 | 8.7 | 9.8 | 14.3 |  | 2608 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 517 | 554 | 771 |  | 0 | 0 | 0 | 1
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2184.16 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.4141 | 1.6213 | 3.1042 | 0.0002083 | 1.724 | 4 | 0.0013928 | 384.4 | 412.3 | 573.5 | 1 | 1 | 1 | 433 | 464 | 646 | 186 | 200 | 278 | 0.52604 | 0.60697 | 1.1625 | 1.9 | 8.7 | 9.8 | 14.3 |  | 3212 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 433 | 464 | 646 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1977.6 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.32375 | 0.37654 | 0.58218 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.12905 | 0.15084 | 0.23384 | 0.5 | 8.7 | 9.8 | 14.3 |  | 2472 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33035 | 0.38406 | 0.59314 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13202 | 0.15425 | 0.23882 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2910 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2577.6 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33694 | 0.39158 | 0.60409 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.135 | 0.15766 | 0.2438 | 0.9 | 8.7 | 9.8 | 14.3 |  | 3222 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2872 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.35014 | 0.40661 | 0.626 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.14096 | 0.16448 | 0.25376 | 1.3 | 8.7 | 9.8 | 14.3 |  | 3590 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2029.6 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.81672 | 0.93595 | 1.8088 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.36094 | 0.41486 | 0.80035 | 0.9 | 8.7 | 9.8 | 14.3 |  | 2537 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.83892 | 0.96093 | 1.853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.37189 | 0.42721 | 0.82216 | 1.3 | 8.7 | 9.8 | 14.3 |  | 3098 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2908.8 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.86112 | 0.98591 | 1.8972 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 500.9437 | 536.44 | 746.3085 | 1 | 1 | 1 | 564 | 604 | 840 | 243 | 260 | 361 | 0.33 | 0.37709 | 0.72084 | 1.7 | 8.7 | 9.8 | 14.3 |  | 3636 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 564 | 604 | 840 |  | 0 | 0 | 0 | 1
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3763.2 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.90551 | 1.0359 | 1.9855 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 419.7096 | 449.4497 | 625.2855 | 1 | 1 | 1 | 473 | 506 | 704 | 203 | 218 | 303 | 0.24557 | 0.28234 | 0.5382 | 2.5 | 8.7 | 9.8 | 14.3 |  | 4704 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 473 | 506 | 704 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1131.3 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.18422 | 0.21592 | 0.33952 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.092934 | 0.10926 | 0.17257 | 0.2 | 10.1 | 11.2 | 17.5 |  | 1257 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.19719 | 0.23082 | 0.36171 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10004 | 0.11746 | 0.18481 | 0.3 | 10.1 | 11.2 | 17.5 |  | 1506 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1525.5 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.21016 | 0.24573 | 0.38389 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10715 | 0.12565 | 0.19706 | 0.4 | 10.1 | 11.2 | 17.5 |  | 1695 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
19510 |  |  | 1 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1755 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.23609 | 0.27555 | 0.42826 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.12136 | 0.14204 | 0.22154 | 0.6 | 10.1 | 11.2 | 17.5 |  | 1950 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1138.32 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.5368 | 0.62753 | 0.99516 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.39489 | 0.46316 | 0.73371 | 0.5 | 10.1 | 11.2 | 17.5 |  | 1674 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.58065 | 0.67784 | 1.0706 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.42835 | 0.50166 | 0.79144 | 0.7 | 10.1 | 11.2 | 17.5 |  | 1940 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1468.8 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.62449 | 0.72814 | 1.1461 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 476.375 | 516.15 | 651.2 | 1 | 1 | 1 | 536 | 581 | 733 | 230 | 250 | 315 | 0.39607 | 0.46541 | 0.72814 | 0.9 | 10.1 | 11.2 | 17.5 |  | 2160 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 536 | 581 | 733 |  | 0 | 0 | 0 | 1
19511 |  |  | 1 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1709.52 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.71218 | 0.82876 | 1.2971 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 399.125 | 432.45 | 545.6 | 1 | 1 | 1 | 449 | 487 | 614 | 193 | 209 | 264 | 0.3252 | 0.37852 | 0.59123 | 1.3 | 10.1 | 11.2 | 17.5 |  | 2514 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 449 | 487 | 614 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1646.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.29198 | 0.33298 | 0.656 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14316 | 0.16346 | 0.32064 | 0.4 | 9.6 | 10.5 | 16.1 |  | 2058 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30027 | 0.34226 | 0.6727 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14762 | 0.16846 | 0.32963 | 0.5 | 9.6 | 10.5 | 16.1 |  | 2428 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2152.8 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30855 | 0.35154 | 0.6894 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.15209 | 0.17347 | 0.33861 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2691 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
19515 |  |  | 1 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2403.2 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.32511 | 0.3701 | 0.72279 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.16101 | 0.18349 | 0.35657 | 1 | 9.6 | 10.5 | 16.1 |  | 3004 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1516.4 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8523 | 2.1254 | 4.1724 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1374 | 1.302 | 2.5702 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2230 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8841 | 2.1613 | 4.2367 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1583 | 1.3255 | 2.6125 | 1 | 9.6 | 10.5 | 16.1 |  | 2657 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2068.56 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.916 | 2.1972 | 4.301 | 0.0002083 | 1.724 | 4 | 0.0013928 | 544.825 | 582.75 | 818.625 | 1 | 1 | 1 | 614 | 656 | 922 | 264 | 282 | 396 | 1.0131 | 1.1547 | 2.2648 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3042 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 614 | 656 | 922 |  | 0 | 0 | 0 | 1
19516 |  |  | 1 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2548.64 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.9797 | 2.269 | 4.4296 | 0.0002083 | 1.724 | 4 | 0.0013928 | 456.475 | 488.25 | 685.875 | 1 | 1 | 1 | 514 | 550 | 772 | 221 | 237 | 332 | 0.7391 | 0.8484 | 1.6506 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3748 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 514 | 550 | 772 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2307.2 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.44617 | 0.52449 | 0.83232 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.17923 | 0.21006 | 0.33489 | 0.5 | 9.6 | 10.5 | 16.1 |  | 2884 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.45488 | 0.5345 | 0.84723 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18319 | 0.2146 | 0.34168 | 0.7 | 9.6 | 10.5 | 16.1 |  | 3395 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3007.2 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.46358 | 0.54451 | 0.86215 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18714 | 0.21913 | 0.34847 | 0.9 | 9.6 | 10.5 | 16.1 |  | 3759 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
19520 |  |  | 1 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3351.2 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.48099 | 0.56453 | 0.89199 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.19506 | 0.22821 | 0.36206 | 1.3 | 9.6 | 10.5 | 16.1 |  | 4189 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2368 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1494 | 1.316 | 2.58 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.50759 | 0.58151 | 1.1397 | 0.9 | 9.6 | 10.5 | 16.1 |  | 2960 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1792 | 1.3495 | 2.64 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.5223 | 0.59805 | 1.1693 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3615 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3393.6 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.2091 | 1.383 | 2.7 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 594.0588 | 636.1954 | 892.6435 | 1 | 1 | 1 | 669 | 716 | 1005 | 288 | 308 | 432 | 0.46143 | 0.52682 | 1.0278 | 1.7 | 9.6 | 10.5 | 16.1 |  | 4242 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 669 | 716 | 1005 |  | 0 | 0 | 0 | 1
19521 |  |  | 1 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4390.4 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.2687 | 1.4501 | 2.8201 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 497.7249 | 533.0285 | 747.8905 | 1 | 1 | 1 | 561 | 600 | 842 | 241 | 258 | 362 | 0.34362 | 0.39271 | 0.76299 | 2.5 | 9.6 | 10.5 | 16.1 |  | 5488 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 561 | 600 | 842 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1293.3 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.24035 | 0.28467 | 0.45825 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.12271 | 0.14433 | 0.2327 | 0.2 | 11 | 12.4 | 19.2 |  | 1437 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.25674 | 0.30367 | 0.48711 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.13179 | 0.1548 | 0.24862 | 0.3 | 11 | 12.4 | 19.2 |  | 1722 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1744.2 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.27312 | 0.32268 | 0.51598 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.14086 | 0.16526 | 0.26454 | 0.4 | 11 | 12.4 | 19.2 |  | 1938 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1301.52 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.70432 | 0.82996 | 1.3412 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.52236 | 0.61192 | 0.98532 | 0.5 | 11 | 12.4 | 19.2 |  | 1914 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.76 | 0.8943 | 1.4394 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.56517 | 0.66113 | 1.0601 | 0.7 | 11 | 12.4 | 19.2 |  | 2218 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1678.92 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.81569 | 0.95863 | 1.5375 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.6 | 593.85 | 757.575 | 1 | 1 | 1 | 617 | 669 | 853 | 265 | 288 | 367 | 0.52097 | 0.61208 | 0.97923 | 0.9 | 11 | 12.4 | 19.2 |  | 2469 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 617 | 669 | 853 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1881.6 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.38464 | 0.43716 | 0.88617 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.18883 | 0.21403 | 0.43431 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2352 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.39516 | 0.44891 | 0.90784 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.19451 | 0.22035 | 0.44599 | 0.5 | 11.5 | 12.8 | 19.6 |  | 2774 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2460 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.40567 | 0.46065 | 0.92951 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.20018 | 0.22668 | 0.45767 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3075 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1733.32 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4404 | 2.7896 | 5.6357 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.4959 | 1.713 | 3.4741 | 0.7 | 11.5 | 12.8 | 19.6 |  | 2549 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4809 | 2.8351 | 5.7191 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.5224 | 1.7427 | 3.529 | 1 | 11.5 | 12.8 | 19.6 |  | 3037 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2364.36 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.5213 | 2.8805 | 5.8025 | 0.0002083 | 1.724 | 4 | 0.0013928 | 625.3 | 667.85 | 952.75 | 1 | 1 | 1 | 704 | 752 | 1073 | 303 | 323 | 461 | 1.3315 | 1.5115 | 3.0623 | 1.3 | 11.5 | 12.8 | 19.6 |  | 3477 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 704 | 752 | 1073 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2636.8 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.58812 | 0.69359 | 1.1269 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.23572 | 0.27698 | 0.45137 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3296 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.59917 | 0.70634 | 1.1463 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24073 | 0.28274 | 0.46016 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3880 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3436.8 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.61022 | 0.71908 | 1.1657 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24575 | 0.2885 | 0.46895 | 0.9 | 11.5 | 12.8 | 19.6 |  | 4296 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2705.6 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.516 | 1.7243 | 3.4956 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.66785 | 0.76014 | 1.5442 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3382 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.554 | 1.7666 | 3.5736 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.6865 | 0.781 | 1.5827 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4131 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3878.4 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.5919 | 1.809 | 3.6517 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 682.6809 | 728.8758 | 1038.9785 | 1 | 1 | 1 | 769 | 821 | 1170 | 331 | 353 | 503 | 0.60733 | 0.68963 | 1.3885 | 1.7 | 11.5 | 12.8 | 19.6 |  | 4848 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 769 | 821 | 1170 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1454.4 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.3126 | 0.36755 | 0.59457 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.15971 | 0.18592 | 0.3017 | 0.2 | 12.2 | 13.7 | 22 |  | 1616 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.33323 | 0.39134 | 0.63084 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.17115 | 0.19899 | 0.3217 | 0.3 | 12.2 | 13.7 | 22 |  | 1937 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1962 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.35386 | 0.41512 | 0.66711 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.18259 | 0.21206 | 0.3417 | 0.4 | 12.2 | 13.7 | 22 |  | 2180 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1464.04 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.9178 | 1.0756 | 1.7382 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.67552 | 0.79428 | 1.2847 | 0.5 | 12.2 | 13.7 | 22 |  | 2153 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.98809 | 1.1564 | 1.8615 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.72919 | 0.85618 | 1.3791 | 0.7 | 12.2 | 13.7 | 22 |  | 2495 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1888.36 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 1.0584 | 1.2372 | 1.9847 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 624.4704 | 677.8928 | 864.6345 | 1 | 1 | 1 | 703 | 763 | 974 | 302 | 328 | 419 | 0.67104 | 0.78752 | 1.2664 | 0.9 | 12.2 | 13.7 | 22 |  | 2777 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 703 | 763 | 974 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2116.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.44001 | 0.50215 | 1.0163 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19642 | 0.22413 | 0.45153 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2646 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.45183 | 0.51539 | 1.0407 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.20229 | 0.23072 | 0.46362 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3121 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2768 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.46364 | 0.52864 | 1.0651 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.20816 | 0.2373 | 0.4757 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3460 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1949.56 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.941 | 3.3503 | 6.7845 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.5418 | 1.7621 | 3.572 | 0.7 | 11.5 | 12.8 | 19.6 |  | 2867 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.9885 | 3.4035 | 6.8824 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.569 | 1.7926 | 3.6282 | 1 | 11.5 | 12.8 | 19.6 |  | 3416 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2659.48 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 3.036 | 3.4567 | 6.9804 | 0.0002083 | 1.724 | 4 | 0.0013928 | 634.8357 | 677.7931 | 966.1625 | 1 | 1 | 1 | 715 | 763 | 1088 | 307 | 328 | 468 | 1.3666 | 1.5583 | 3.1554 | 1.3 | 11.5 | 12.8 | 19.6 |  | 3911 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 715 | 763 | 1088 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2966.4 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.68715 | 0.80774 | 1.3107 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24717 | 0.28937 | 0.47247 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3708 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.69979 | 0.82228 | 1.3328 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25239 | 0.29536 | 0.48161 | 0.7 | 11.5 | 12.8 | 19.6 |  | 4365 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3866.4 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.71243 | 0.83681 | 1.3549 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25762 | 0.30135 | 0.49076 | 0.9 | 11.5 | 12.8 | 19.6 |  | 4833 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3044 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.6886 | 1.9269 | 3.9059 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.69036 | 0.78818 | 1.5954 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3805 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7303 | 1.9735 | 3.9919 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.70956 | 0.8097 | 1.6351 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4648 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4363.2 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7719 | 2.0202 | 4.0778 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 693.8642 | 740.8158 | 1055.9985 | 1 | 1 | 1 | 781 | 834 | 1189 | 336 | 359 | 511 | 0.62558 | 0.71297 | 1.4325 | 1.7 | 11.5 | 12.8 | 19.6 |  | 5454 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 781 | 834 | 1189 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1616.4 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.37714 | 0.44506 | 0.74844 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.19105 | 0.22703 | 0.37956 | 0.2 | 13.4 | 14.8 | 24 |  | 1796 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.40147 | 0.47319 | 0.79282 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.20444 | 0.24261 | 0.40402 | 0.3 | 13.4 | 14.8 | 24 |  | 2152 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2179.8 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.4258 | 0.50133 | 0.8372 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.21783 | 0.2582 | 0.42849 | 0.4 | 13.4 | 14.8 | 24 |  | 2422 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1626.56 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1014 | 1.3015 | 2.1934 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.81202 | 0.96093 | 1.6107 | 0.5 | 13.4 | 14.8 | 24 |  | 2392 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1839 | 1.3971 | 2.3445 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.87514 | 1.0341 | 1.7259 | 0.7 | 13.4 | 14.8 | 24 |  | 2772 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2098.48 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.2664 | 1.4926 | 2.4957 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 685.425 | 746.475 | 971.25 | 1 | 1 | 1 | 772 | 841 | 1094 | 332 | 362 | 470 | 0.80625 | 0.95352 | 1.583 | 0.9 | 13.4 | 14.8 | 24 |  | 3086 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 772 | 841 | 1094 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2352 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.63179 | 0.69856 | 1.4549 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.30854 | 0.34302 | 0.71304 | 0.4 | 13.2 | 14.7 | 23.5 |  | 2940 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.64795 | 0.71619 | 1.4882 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.31723 | 0.35254 | 0.73099 | 0.5 | 13.2 | 14.7 | 23.5 |  | 3468 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3075.2 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.66412 | 0.73382 | 1.5215 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.32591 | 0.36206 | 0.74894 | 0.7 | 13.2 | 14.7 | 23.5 |  | 3844 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2166.48 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0067 | 4.4506 | 9.2646 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.4755 | 2.7278 | 5.6888 | 0.7 | 13.2 | 14.7 | 23.5 |  | 3186 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0688 | 4.5186 | 9.3927 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.5164 | 2.7723 | 5.7729 | 1 | 13.2 | 14.7 | 23.5 |  | 3796 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2955.28 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.1309 | 4.5867 | 9.5209 | 0.0002083 | 1.724 | 4 | 0.0013928 | 802.9 | 845.45 | 1221 | 1 | 1 | 1 | 904 | 952 | 1375 | 389 | 409 | 591 | 2.186 | 2.4147 | 5.0154 | 1.3 | 13.2 | 14.7 | 23.5 |  | 4346 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 904 | 952 | 1375 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3296 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.92309 | 1.0942 | 1.8493 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.36943 | 0.43843 | 0.73955 | 0.5 | 13.2 | 14.7 | 23.5 |  | 4120 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.9394 | 1.1131 | 1.879 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.37682 | 0.447 | 0.75301 | 0.7 | 13.2 | 14.7 | 23.5 |  | 4850 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4296 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.95571 | 1.132 | 1.9088 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.38422 | 0.45558 | 0.76648 | 0.9 | 13.2 | 14.7 | 23.5 |  | 5370 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3382.4 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.486 | 2.758 | 5.7307 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.0964 | 1.2187 | 2.5291 | 0.9 | 13.2 | 14.7 | 23.5 |  | 4228 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.5441 | 2.8216 | 5.8504 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.125 | 1.2501 | 2.5881 | 1.3 | 13.2 | 14.7 | 23.5 |  | 5164 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4848 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.6023 | 2.8853 | 5.9701 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 875.7193 | 922.7225 | 1331.6485 | 1 | 1 | 1 | 986 | 1039 | 1500 | 424 | 447 | 645 | 0.99052 | 1.0995 | 2.2706 | 1.7 | 13.2 | 14.7 | 23.5 |  | 6060 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 986 | 1039 | 1500 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1939.5 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.44768 | 0.53277 | 0.9236 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.22703 | 0.27016 | 0.46626 | 0.2 | 13.4 | 14.8 | 24 |  | 2155 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2323.8 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.47596 | 0.56571 | 0.97696 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.24261 | 0.28832 | 0.49556 | 0.3 | 13.4 | 14.8 | 24 |  | 2582 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2615.4 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.50424 | 0.59865 | 1.0303 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.2582 | 0.30647 | 0.52487 | 0.4 | 13.4 | 14.8 | 24 |  | 2906 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1951.6 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.3071 | 1.561 | 2.6927 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 0.96578 | 1.1485 | 1.9869 | 0.5 | 13.4 | 14.8 | 24 |  | 2870 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2261.68 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.4031 | 1.6731 | 2.8737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 1.0393 | 1.2342 | 2.1255 | 0.7 | 13.4 | 14.8 | 24 |  | 3326 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2518.04 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.499 | 1.7852 | 3.0547 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 748.4982 | 817.8264 | 1078.1245 | 1 | 1 | 1 | 843 | 921 | 1214 | 362 | 396 | 522 | 0.95352 | 1.135 | 1.9411 | 0.9 | 13.4 | 14.8 | 24 |  | 3703 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 843 | 921 | 1214 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2822.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.77625 | 0.84212 | 1.7888 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.37931 | 0.41187 | 0.87808 | 0.4 | 15.5 | 16.8 | 27.5 |  | 3528 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3329.6 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.79556 | 0.86285 | 1.8286 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.3897 | 0.42302 | 0.89958 | 0.5 | 15.5 | 16.8 | 27.5 |  | 4162 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3690.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.81488 | 0.88358 | 1.8684 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.40009 | 0.43418 | 0.92107 | 0.7 | 15.5 | 16.8 | 27.5 |  | 4613 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2599.64 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 4.9509 | 5.3565 | 11.3896 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.044 | 3.296 | 6.9994 | 0.7 | 15.5 | 16.8 | 27.5 |  | 3823 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3097.4 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.0255 | 5.4363 | 11.5429 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.093 | 3.3484 | 7.1 | 1 | 15.5 | 16.8 | 27.5 |  | 4555 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3546.2 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.1001 | 5.5161 | 11.6961 | 0.0002083 | 1.724 | 4 | 0.0013928 | 891.1063 | 928.2293 | 1354.6625 | 1 | 1 | 1 | 1004 | 1045 | 1526 | 432 | 449 | 656 | 2.6917 | 2.9061 | 6.1706 | 1.3 | 15.5 | 16.8 | 27.5 |  | 5215 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1004 | 1045 | 1526 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3955.2 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.0983 | 1.3107 | 2.2771 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.441 | 0.52449 | 0.91195 | 0.5 | 15.5 | 16.8 | 27.5 |  | 4944 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4656 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1172 | 1.3328 | 2.3127 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.44962 | 0.5345 | 0.92809 | 0.7 | 15.5 | 16.8 | 27.5 |  | 5820 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5155.2 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1362 | 1.3549 | 2.3483 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.45824 | 0.54451 | 0.94423 | 0.9 | 15.5 | 16.8 | 27.5 |  | 6444 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4059.2 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.0601 | 3.3196 | 7.0476 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3527 | 1.4661 | 3.1159 | 0.9 | 15.5 | 16.8 | 27.5 |  | 5074 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4957.6 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.1297 | 3.3942 | 7.1908 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3871 | 1.5029 | 3.1866 | 1.3 | 15.5 | 16.8 | 27.5 |  | 6197 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5817.6 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.1992 | 3.4689 | 7.3339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 972.2277 | 1012.7301 | 1477.9835 | 1 | 1 | 1 | 1095 | 1141 | 1664 | 471 | 491 | 716 | 1.2193 | 1.3238 | 2.7919 | 1.7 | 15.5 | 16.8 | 27.5 |  | 7272 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1095 | 1141 | 1664 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1939.5 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.52706 | 0.62828 | 1.1129 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.26609 | 0.31922 | 0.56178 | 0.2 | 14.8 | 16.6 | 28 |  | 2155 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.55969 | 0.66635 | 1.1757 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.284 | 0.34024 | 0.59629 | 0.3 | 14.8 | 16.6 | 28 |  | 2582 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2615.4 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.59232 | 0.70442 | 1.2385 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.30191 | 0.36126 | 0.6308 | 0.4 | 14.8 | 16.6 | 28 |  | 2906 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1951.6 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.5364 | 1.8371 | 3.2427 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.1327 | 1.3527 | 2.387 | 0.5 | 14.8 | 16.6 | 28 |  | 2870 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.647 | 1.9665 | 3.4558 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.2173 | 1.4515 | 2.5499 | 0.7 | 14.8 | 16.6 | 28 |  | 3326 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2518.04 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.7576 | 2.0958 | 3.6689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 811.225 | 888.925 | 1184.925 | 1 | 1 | 1 | 914 | 1001 | 1334 | 393 | 430 | 574 | 1.1183 | 1.3318 | 2.3348 | 0.9 | 14.8 | 16.6 | 28 |  | 3703 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 914 | 1001 | 1334 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2822.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.93968 | 1.0077 | 2.1571 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.46027 | 0.49302 | 1.0558 | 0.4 | 16.4 | 17.7 | 29.7 |  | 3528 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.96247 | 1.0319 | 2.2039 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.47256 | 0.50606 | 1.081 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4162 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3690.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.98527 | 1.0561 | 2.2507 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.48484 | 0.5191 | 1.1062 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4613 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2599.64 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 5.9764 | 6.4212 | 13.761 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.6712 | 3.9473 | 8.4672 | 0.7 | 16.4 | 17.7 | 29.7 |  | 3823 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.0642 | 6.5145 | 13.9415 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.7288 | 4.0086 | 8.5857 | 1 | 16.4 | 17.7 | 29.7 |  | 4555 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3546.2 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.152 | 6.6079 | 14.1219 | 0.0002083 | 1.724 | 4 | 0.0013928 | 979.575 | 1015.65 | 1489.25 | 1 | 1 | 1 | 1103 | 1144 | 1677 | 474 | 492 | 721 | 3.2362 | 3.4848 | 7.4448 | 1.3 | 16.4 | 17.7 | 29.7 |  | 5215 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1103 | 1144 | 1677 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3955.2 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.2931 | 1.5467 | 2.7492 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.51889 | 0.62129 | 1.1023 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4944 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3149 | 1.5722 | 2.7911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.52881 | 0.63288 | 1.1214 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5820 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5155.2 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3367 | 1.5977 | 2.833 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.53872 | 0.64447 | 1.1404 | 0.9 | 16.4 | 17.7 | 29.7 |  | 6444 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4059.2 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.6935 | 3.969 | 8.5002 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6301 | 1.7542 | 3.7637 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5074 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.7754 | 4.0561 | 8.6685 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6704 | 1.7973 | 3.8469 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6197 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5817.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.8573 | 4.1433 | 8.8369 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1068.7506 | 1107.6299 | 1624.3185 | 1 | 1 | 1 | 1204 | 1247 | 1829 | 518 | 536 | 786 | 1.4716 | 1.5744 | 3.358 | 1.7 | 16.4 | 17.7 | 29.7 |  | 7272 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1247 | 1829 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2262.6 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.61284 | 0.74506 | 1.3196 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.3104 | 0.37714 | 0.66611 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2514 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.65009 | 0.78926 | 1.3926 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.33091 | 0.40147 | 0.70618 | 0.3 | 16.2 | 18.6 | 31.4 |  | 3013 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3051.9 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.68734 | 0.83347 | 1.4655 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.35141 | 0.4258 | 0.74625 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3391 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2277.32 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.7972 | 2.1788 | 3.8433 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.3241 | 1.6044 | 2.8317 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3349 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.9241 | 2.3291 | 4.0906 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.4212 | 1.7193 | 3.0209 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3881 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2937.6 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 2.051 | 2.4794 | 4.338 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 878.2979 | 968.7109 | 1291.6145 | 1 | 1 | 1 | 989 | 1091 | 1455 | 425 | 469 | 626 | 1.3019 | 1.5764 | 2.764 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4320 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 989 | 1091 | 1455 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3292.8 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.025 | 1.1005 | 2.3574 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.46909 | 0.50521 | 1.0825 | 0.4 | 16.4 | 17.7 | 29.7 |  | 4116 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3884 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0496 | 1.1266 | 2.4079 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.48158 | 0.51852 | 1.1083 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4855 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4305.6 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0742 | 1.1528 | 2.4584 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.49407 | 0.53184 | 1.134 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5382 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3032.8 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.7265 | 7.2177 | 15.4955 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.7429 | 4.0216 | 8.5976 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4460 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3613.52 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.8237 | 7.321 | 15.6954 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.8014 | 4.0839 | 8.7177 | 1 | 16.4 | 17.7 | 29.7 |  | 5314 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4137.12 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.9209 | 7.4243 | 15.8953 | 0.0002083 | 1.724 | 4 | 0.0013928 | 988.7048 | 1024.6723 | 1502.6625 | 1 | 1 | 1 | 1113 | 1154 | 1692 | 479 | 496 | 728 | 3.3043 | 3.5413 | 7.5891 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6084 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1113 | 1154 | 1692 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4614.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4056 | 1.7098 | 3.0322 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.52449 | 0.63667 | 1.131 | 0.5 | 16.4 | 17.7 | 29.7 |  | 5768 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5432 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.429 | 1.7376 | 3.0778 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.5345 | 0.64851 | 1.1505 | 0.7 | 16.4 | 17.7 | 29.7 |  | 6790 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 6014.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4525 | 1.7654 | 3.1233 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.54451 | 0.66034 | 1.1699 | 0.9 | 16.4 | 17.7 | 29.7 |  | 7518 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4735.2 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 3.969 | 4.2636 | 9.1467 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.6651 | 1.7906 | 3.8345 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5919 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5784 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.0561 | 4.3564 | 9.326 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.7062 | 1.8343 | 3.919 | 1.3 | 16.4 | 17.7 | 29.7 |  | 7230 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6787.2 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.1433 | 4.4491 | 9.5053 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1079.9492 | 1119.2361 | 1641.3385 | 1 | 1 | 1 | 1216 | 1260 | 1848 | 523 | 542 | 795 | 1.4998 | 1.6094 | 3.4346 | 1.7 | 16.4 | 17.7 | 29.7 |  | 8484 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1216 | 1260 | 1848 |  | 0 | 0 | 0 | 1
13510 |  |  | 1 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2262.6 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.65973 | 0.80363 | 1.4155 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.32145 | 0.3893 | 0.68543 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2514 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
15010 |  |  | 1 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.69946 | 0.85087 | 1.4931 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.34259 | 0.41431 | 0.72652 | 0.3 | 16.2 | 18.6 | 31.4 |  | 3013 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
16510 |  |  | 1 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3051.9 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.7392 | 0.8981 | 1.5707 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.36374 | 0.43933 | 0.76761 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3391 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
13511 |  |  | 1 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2277.32 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 1.9939 | 2.4252 | 4.2683 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.3412 | 1.6295 | 2.8732 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3349 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
15011 |  |  | 1 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.1329 | 2.5903 | 4.5395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.4394 | 1.7459 | 3.0648 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3881 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
16511 |  |  | 1 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2937.6 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.2719 | 2.7554 | 4.8107 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 884.3 | 976.8 | 1300.55 | 1 | 1 | 1 | 996 | 1100 | 1465 | 428 | 473 | 630 | 1.3198 | 1.6027 | 2.7985 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4320 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 996 | 1100 | 1465 |  | 0 | 0 | 0 | 1
13515 |  |  | 1 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3292.8 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3082 | 1.363 | 3.004 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.63866 | 0.67004 | 1.4705 | 0.4 | 19.3 | 20.4 | 34.5 |  | 4116 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
15015 |  |  | 1 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3386 | 1.3944 | 3.0663 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.65498 | 0.68705 | 1.5041 | 0.5 | 19.3 | 20.4 | 34.5 |  | 4855 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
16515 |  |  | 1 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4305.6 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3689 | 1.4259 | 3.1286 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.67129 | 0.70405 | 1.5377 | 0.7 | 19.3 | 20.4 | 34.5 |  | 5382 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
13516 |  |  | 1 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3032.8 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.3163 | 8.6851 | 19.1422 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1011 | 5.3392 | 11.7693 | 0.7 | 19.3 | 20.4 | 34.5 |  | 4460 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
15016 |  |  | 1 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.433 | 8.8063 | 19.3822 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1776 | 5.4188 | 11.927 | 1 | 19.3 | 20.4 | 34.5 |  | 5314 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
16516 |  |  | 1 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4137.12 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.5498 | 8.9275 | 19.6222 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1156.25 | 1182.15 | 1757.5 | 1 | 1 | 1 | 1302 | 1331 | 1979 | 560 | 572 | 851 | 4.5064 | 4.7002 | 10.3498 | 1.3 | 19.3 | 20.4 | 34.5 |  | 6084 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1302 | 1331 | 1979 |  | 0 | 0 | 0 | 1
13520 |  |  | 1 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4614.4 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7711 | 2.156 | 3.819 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.70984 | 0.86445 | 1.5323 | 0.5 | 19.3 | 20.4 | 34.5 |  | 5768 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
15020 |  |  | 1 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7998 | 2.19 | 3.8746 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.72284 | 0.87987 | 1.5576 | 0.7 | 19.3 | 20.4 | 34.5 |  | 6790 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
16520 |  |  | 1 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6014.4 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.8284 | 2.2239 | 3.9302 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.73584 | 0.89528 | 1.5829 | 0.9 | 19.3 | 20.4 | 34.5 |  | 7518 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
13521 |  |  | 1 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4735.2 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.1385 | 5.3778 | 11.8278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1364.0875 | 1394.6194 | 2072.42 | 1 | 1 | 1 | 1536 | 1571 | 2334 | 660 | 676 | 1004 | 2.2688 | 2.3797 | 5.2315 | 0.9 | 19.3 | 20.4 | 34.5 |  | 5919 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1536 | 1571 | 2334 |  | 0 | 0 | 0 | 1
15021 |  |  | 1 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5784 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.2475 | 5.4911 | 12.0517 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1364.0875 | 1394.6194 | 2072.42 | 1 | 1 | 1 | 1536 | 1571 | 2334 | 660 | 676 | 1004 | 2.3226 | 2.4357 | 5.3422 | 1.3 | 19.3 | 20.4 | 34.5 |  | 7230 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1536 | 1571 | 2334 |  | 0 | 0 | 0 | 1
16521 |  |  | 1 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6787.2 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.3564 | 5.6044 | 12.2756 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 2.0399 | 2.1334 | 4.6656 | 1.7 | 19.3 | 20.4 | 34.5 |  | 8484 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 255.6 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.01394 | 0.016306 | 0.02216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0069533 | 0.0079513 | 0.011345 | 0.1 | 3.6 | 4.1 | 5.1 |  | 284 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 306.9 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.023911 | 0.026978 | 0.038029 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.011759 | 0.01394 | 0.018856 | 0.1 | 4.8 | 5.4 | 6.8 |  | 341 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 498.4 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.038024 | 0.043193 | 0.076311 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.19241 | 0.021258 | 0.037195 | 0.2 | 4.8 | 5.5 | 7.2 |  | 623 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 668.8 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.060116 | 0.069942 | 0.097754 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.023886 | 0.027597 | 0.038802 | 0.3 | 4.8 | 5.5 | 7.2 |  | 836 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 358.2 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.035814 | 0.041087 | 0.05814 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.017814 | 0.020475 | 0.029564 | 0.1 | 5.5 | 5.9 | 7.9 |  | 398 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 581.6 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.046821 | 0.054517 | 0.095052 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.019427 | 0.022524 | 0.039711 | 0.2 | 5.1 | 5.6 | 7.2 |  | 727 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 780.8 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.076193 | 0.087207 | 0.1247 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.025708 | 0.029553 | 0.0419 | 0.3 | 5.1 | 5.6 | 7.2 |  | 976 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 408.6 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.049245 | 0.056302 | 0.082487 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.025116 | 0.028906 | 0.041869 | 0.1 | 6.3 | 6.8 | 9.1 |  | 454 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 664 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.079895 | 0.092435 | 0.16533 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.038863 | 0.044989 | 0.081108 | 0.2 | 6 | 6.7 | 9 |  | 830 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 892 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.12607 | 0.14449 | 0.21079 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.050166 | 0.05824 | 0.084945 | 0.3 | 6 | 6.7 | 9 |  | 1115 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 459.9 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.064804 | 0.074948 | 0.11107 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.032962 | 0.038029 | 0.056302 | 0.1 | 6.7 | 7.4 | 10.3 |  | 511 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 747.2 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.1045 | 0.12025 | 0.22357 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.051562 | 0.058583 | 0.10869 | 0.2 | 7 | 7.7 | 10.7 |  | 934 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1004 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.16573 | 0.19178 | 0.28544 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.066916 | 0.077261 | 0.11405 | 0.3 | 7 | 7.7 | 10.7 |  | 1255 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 511.2 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.082487 | 0.09506 | 0.14387 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.041869 | 0.048396 | 0.07286 | 0.1 | 7.8 | 8.7 | 12.2 |  | 568 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 830.4 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.1324 | 0.15172 | 0.28827 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.064957 | 0.073967 | 0.14029 | 0.2 | 7 | 7.7 | 10.7 |  | 1038 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1115.2 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21079 | 0.24575 | 0.36902 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.084945 | 0.098963 | 0.14892 | 0.3 | 7 | 7.7 | 10.7 |  | 1394 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 562.5 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.10352 | 0.1202 | 0.18091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.052715 | 0.060952 | 0.091543 | 0.1 | 8.4 | 9.3 | 14 |  | 625 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 913.6 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15006 | 0.17058 | 0.32614 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.067155 | 0.076311 | 0.14513 | 0.2 | 7.9 | 8.8 | 12.5 |  | 1142 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24194 | 0.28134 | 0.42231 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.088349 | 0.10263 | 0.15341 | 0.3 | 7.9 | 8.8 | 12.5 |  | 1533 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 613.8 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.12287 | 0.14387 | 0.22216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.061904 | 0.07286 | 0.11235 | 0.1 | 8.9 | 9.9 | 14.8 |  | 682 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 996.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.2019 | 0.23172 | 0.44799 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.099047 | 0.11296 | 0.21755 | 0.2 | 8.7 | 9.8 | 14.3 |  | 1246 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1338.4 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.31715 | 0.36902 | 0.57123 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.12607 | 0.14743 | 0.22886 | 0.3 | 8.7 | 9.8 | 14.3 |  | 1673 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 715.5 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.17125 | 0.20101 | 0.31734 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.085827 | 0.10107 | 0.16032 | 0.1 | 10.1 | 11.2 | 17.5 |  | 795 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1162.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.2837 | 0.3237 | 0.6393 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.13869 | 0.15845 | 0.31166 | 0.2 | 9.6 | 10.5 | 16.1 |  | 1453 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1561.6 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.43747 | 0.51448 | 0.8174 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.17527 | 0.20552 | 0.3281 | 0.3 | 9.6 | 10.5 | 16.1 |  | 1952 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 818.1 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.22397 | 0.26566 | 0.42939 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.11364 | 0.13387 | 0.21677 | 0.1 | 11 | 12.4 | 19.2 |  | 909 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1328.8 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.37413 | 0.42541 | 0.86451 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.18316 | 0.2077 | 0.42263 | 0.2 | 11.5 | 12.8 | 19.6 |  | 1661 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1784 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.57707 | 0.68085 | 1.1075 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.2307 | 0.27121 | 0.44258 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2230 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 919.8 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.29196 | 0.34377 | 0.5583 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.14827 | 0.17284 | 0.2817 | 0.1 | 12.2 | 13.7 | 22 |  | 1022 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1494.4 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.4282 | 0.4889 | 0.99194 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19054 | 0.21755 | 0.43945 | 0.2 | 11.5 | 12.8 | 19.6 |  | 1868 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.67451 | 0.7932 | 1.2887 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24194 | 0.28338 | 0.46332 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2509 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1022.4 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.35281 | 0.41693 | 0.70406 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.17766 | 0.21145 | 0.35509 | 0.1 | 13.4 | 14.8 | 24 |  | 1136 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1660.8 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.61563 | 0.68093 | 1.4216 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.29985 | 0.33349 | 0.69509 | 0.2 | 13.2 | 14.7 | 23.5 |  | 2076 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2230.4 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.90678 | 1.0753 | 1.8196 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.36204 | 0.42986 | 0.72608 | 0.3 | 13.2 | 14.7 | 23.5 |  | 2788 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1125 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.41941 | 0.49982 | 0.87023 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.21145 | 0.25201 | 0.43695 | 0.1 | 13.4 | 14.8 | 24 |  | 1250 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1827.2 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.75693 | 0.82139 | 1.749 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.36892 | 0.40071 | 0.85659 | 0.2 | 15.5 | 16.8 | 27.5 |  | 2284 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2453.6 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.0793 | 1.2887 | 2.2415 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.43239 | 0.51448 | 0.89581 | 0.3 | 15.5 | 16.8 | 27.5 |  | 3067 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1226.7 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.49442 | 0.59021 | 1.05 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.24818 | 0.29821 | 0.52727 | 0.1 | 14.8 | 16.6 | 28 |  | 1363 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 1992.8 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.91688 | 0.98345 | 2.1103 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.44799 | 0.47998 | 1.0306 | 0.2 | 16.4 | 17.7 | 29.7 |  | 2491 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2676.8 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.2712 | 1.5213 | 2.7074 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.50897 | 0.60971 | 1.0833 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3346 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1329.3 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.5756 | 0.70085 | 1.2466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.2899 | 0.35281 | 0.62604 | 0.1 | 16.2 | 18.6 | 31.4 |  | 1477 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2159.2 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.3168 | 1.5999 | 2.8401 | 0.0002083 | 1.724 | 2 | 0.00046183 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 0.96659 | 1.1739 | 2.0855 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2699 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2899.2 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.3821 | 1.682 | 2.9867 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.51448 | 0.62484 | 1.1116 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3624 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
22010 |  |  | 2 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1431.9 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.61999 | 0.75639 | 1.338 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.3003 | 0.36428 | 0.64435 | 0.1 | 16.2 | 18.6 | 31.4 |  | 1591 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
22015 |  |  | 2 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2324.8 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.2779 | 1.3315 | 2.9416 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.62235 | 0.65303 | 1.4369 | 0.2 | 19.3 | 20.4 | 34.5 |  | 2906 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
22020 |  |  | 2 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3122.4 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7425 | 2.1221 | 3.7634 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.69684 | 0.84904 | 1.507 | 0.3 | 19.3 | 20.4 | 34.5 |  | 3903 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 30.9 | 353.7 | 531.0839 | 593.5851 | 603.7501 | N/A | 1 | 1 | 1 | #VALUE! | 292 | 327 | 332 | #VALUE! | 50 | 56 | 57 | #VALUE! | 0.010419 | 0.013016 | 0.013477 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 165.2042 | 176.5749 | 177.9165 | 1 | 1 | 1 | 186 | 199 | 200 | 80 | 86 | 86 | 0.026246 | 0.03026 | 0.03026 | 0.2 | 3.968 | 4.5178 | 4.5714 |  | 393 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 186 | 199 | 200 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 34.1 | 373.32 | 935.3255 | 1110.0611 | 1207.5001 | N/A | 1 | 1 | 1 | #VALUE! | 515 | 611 | 665 | #VALUE! | 89 | 105 | 114 | #VALUE! | 0.052293 | 0.072324 | 0.084992 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 300.2905 | 340.1672 | 355.8334 | 1 | 1 | 1 | 338 | 383 | 401 | 145 | 165 | 172 | 0.13632 | 0.17573 | 0.19069 | 0.5 | 5.978 | 7.4234 | 9.1429 |  | 549 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 338 | 383 | 401 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 35.7 | 423.9 | 1207.0335 | 1516.5744 | 1725.0001 | N/A | 1 | 1 | 1 | #VALUE! | 664 | 835 | 949 | #VALUE! | 114 | 144 | 163 | #VALUE! | 0.052711 | 0.083535 | 0.10667 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 394.3977 | 471.8389 | 508.3335 | 1 | 1 | 1 | 444 | 531 | 572 | 191 | 228 | 246 | 0.14584 | 0.20686 | 0.24035 | 0.2 | 6.7572 | 9.1627 | 12.5714 |  | 471 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 444 | 531 | 572 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 33.0902 | 406.6873 | 501.6873 | 555.7763 | 594.3332 | N/A | 1 | 1 | 1 | #VALUE! | 276 | 306 | 327 | #VALUE! | 47 | 53 | 56 | #VALUE! | 0.014981 | 0.018948 | 0.021103 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 155.2032 | 166.9571 | 173.6668 | 1 | 1 | 1 | 175 | 188 | 196 | 75 | 81 | 84 | 0.03739 | 0.043476 | 0.046689 | 0.5 | 7.3986 | 8.7271 | 8.2333 |  | 659 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 175 | 188 | 196 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 37.8451 | 632 | 1342.8565 | 1479.2042 | 1783.0001 | N/A | 1 | 1 | 1 | #VALUE! | 739 | 814 | 981 | #VALUE! | 127 | 140 | 169 | #VALUE! | 0.076561 | 0.092923 | 0.1351 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 459.3348 | 520.9999 | 1 | 1 | 1 | 477 | 517 | 587 | 205 | 222 | 252 | 0.19834 | 0.23239 | 0.29902 | 0.4 | 16.5581 | 18.744 | 24.7 |  | 790 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 517 | 587 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 40.056 | 663 | 2098.7535 | 2346.2836 | 2971.6665 | N/A | 1 | 1 | 1 | #VALUE! | 1155 | 1291 | 1635 | #VALUE! | 199 | 222 | 281 | #VALUE! | 0.55598 | 0.69136 | 1.1058 | 0.0002083 | 1.724 | 4 | 0.0013928 | 666.3741 | 735.2764 | 868.3334 | 1 | 1 | 1 | 750 | 828 | 978 | 323 | 356 | 421 | 1.4596 | 1.772 | 2.4755 | 0.7 | 23.6342 | 27.4714 | 41.1667 |  | 975 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 750 | 828 | 978 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 32.3733 | 864.8 | 1000.4309 | 1061.1878 | 1097.4999 | N/A | 1 | 1 | 1 | #VALUE! | 551 | 584 | 604 | #VALUE! | 95 | 100 | 104 | #VALUE! | 0.03462 | 0.038339 | 0.041451 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 292.1672 | 314.0225 | 330.5 | 1 | 1 | 1 | 329 | 354 | 372 | 141 | 152 | 160 | 0.075963 | 0.088216 | 0.0977 | 0.5 | 9 | 9.8 | 12 |  | 1081 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 329 | 354 | 372 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 37 | 997.6 | 2118.8633 | 2307.013 | 2560.8334 | N/A | 1 | 1 | 1 | #VALUE! | 1166 | 1270 | 1409 | #VALUE! | 201 | 218 | 242 | #VALUE! | 0.21311 | 0.25044 | 0.30823 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 620.1576 | 673.0826 | 771.1667 | 1 | 1 | 1 | 698 | 758 | 868 | 300 | 326 | 373 | 0.47251 | 0.55745 | 0.72872 | 0.9 | 16.9 | 18.9 | 30 |  | 1247 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 698 | 758 | 868 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.699 | 495 | 3189.1985 | 3467.538 | 4024.1666 | N/A | 1 | 1 | 1 | #VALUE! | 1755 | 1908 | 2215 | #VALUE! | 302 | 328 | 381 | #VALUE! | 0.36044 | 0.42436 | 0.57063 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 939.7017 | 1011.3774 | 1211.8334 | 1 | 1 | 1 | 1058 | 1139 | 1365 | 455 | 490 | 587 | 0.81066 | 0.9387 | 1.3421 | 0.2 | 22.7 | 24.7 | 45 |  | 550 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 1058 | 1139 | 1365 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 522.92 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.11334 | 0.13083 | 0.18635 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.084992 | 0.097098 | 0.13632 | 0.5 | 5.5 | 5.9 | 7.9 |  | 769 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 737.6 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.048569 | 0.05651 | 0.098274 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.020245 | 0.023453 | 0.041227 | 0.4 | 5.1 | 5.6 | 7.2 |  | 922 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 773.84 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.33364 | 0.38279 | 0.67287 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.15858 | 0.1833 | 0.32082 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1138 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1008.8 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.078123 | 0.089375 | 0.12765 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.026464 | 0.030406 | 0.043052 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1261 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.18463 | 0.21311 | 0.37198 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.072733 | 0.082941 | 0.14571 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1455 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 565.2 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.053626 | 0.061225 | 0.089351 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.027552 | 0.03166 | 0.045672 | 0.2 | 6.3 | 6.8 | 9.1 |  | 628 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 597.04 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.15738 | 0.18206 | 0.26161 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.11674 | 0.13265 | 0.19287 | 0.5 | 6.3 | 6.8 | 9.1 |  | 878 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 843.2 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.082668 | 0.095579 | 0.17052 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.040351 | 0.046678 | 0.083917 | 0.4 | 6 | 6.7 | 9 |  | 1054 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 884 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.52309 | 0.6014 | 1.0824 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32082 | 0.36906 | 0.66676 | 0.7 | 6 | 6.7 | 9 |  | 1300 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1152.8 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.12905 | 0.14784 | 0.21543 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.051512 | 0.059771 | 0.087064 | 0.5 | 6 | 6.7 | 9 |  | 1441 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1329.6 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.32621 | 0.37477 | 0.67158 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14397 | 0.16552 | 0.29569 | 0.9 | 6 | 6.7 | 9 |  | 1662 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 636.3 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.070367 | 0.081263 | 0.11996 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.03605 | 0.041526 | 0.061225 | 0.2 | 6.7 | 7.4 | 10.3 |  | 707 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 671.84 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.20625 | 0.23917 | 0.35237 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.15344 | 0.17573 | 0.25907 | 0.5 | 6.7 | 7.4 | 10.3 |  | 988 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 948 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.108 | 0.1242 | 0.23031 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.053462 | 0.060704 | 0.1123 | 0.4 | 7 | 7.7 | 10.7 |  | 1185 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 994.84 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.68517 | 0.78756 | 1.4596 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.42065 | 0.48597 | 0.89706 | 0.7 | 7 | 7.7 | 10.7 |  | 1463 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1296.8 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.1695 | 0.19605 | 0.29146 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.068641 | 0.079214 | 0.11678 | 0.5 | 7 | 7.7 | 10.7 |  | 1621 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1496 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.42668 | 0.4883 | 0.90539 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.18857 | 0.21735 | 0.40031 | 0.9 | 7 | 7.7 | 10.7 |  | 1870 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 706.5 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.089351 | 0.10283 | 0.15502 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.045672 | 0.052711 | 0.079022 | 0.2 | 7.8 | 8.7 | 12.2 |  | 785 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 746.64 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.26161 | 0.30395 | 0.45308 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.19287 | 0.22477 | 0.33488 | 0.5 | 7.8 | 8.7 | 12.2 |  | 1098 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1053.6 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.13669 | 0.15654 | 0.29667 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.067276 | 0.076561 | 0.1448 | 0.4 | 7 | 7.7 | 10.7 |  | 1317 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1105 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.86902 | 0.99871 | 1.8931 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.53394 | 0.61304 | 1.1614 | 0.7 | 7 | 7.7 | 10.7 |  | 1625 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1440.8 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21543 | 0.25104 | 0.37654 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.087064 | 0.10138 | 0.15235 | 0.5 | 7 | 7.7 | 10.7 |  | 1801 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1662.4 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.54057 | 0.61676 | 1.169 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.23915 | 0.27379 | 0.51738 | 0.9 | 7 | 7.7 | 10.7 |  | 2078 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 777.6 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.11189 | 0.12973 | 0.19451 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.057363 | 0.066226 | 0.09906 | 0.2 | 8.4 | 9.3 | 14 |  | 864 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 821.44 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.32914 | 0.37943 | 0.57 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.24162 | 0.27975 | 0.42027 | 0.5 | 8.4 | 9.3 | 14 |  | 1208 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1159.2 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15484 | 0.17592 | 0.33548 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.069541 | 0.078976 | 0.14978 | 0.4 | 7.9 | 8.8 | 12.5 |  | 1449 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1215.84 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0212 | 1.1694 | 2.2132 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.54491 | 0.6307 | 1.1937 | 0.7 | 7.9 | 8.8 | 12.5 |  | 1788 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1584.8 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24717 | 0.28729 | 0.43075 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.090541 | 0.10513 | 0.15694 | 0.5 | 7.9 | 8.8 | 12.5 |  | 1981 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1828.8 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.59549 | 0.68282 | 1.29 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.24589 | 0.281 | 0.53389 | 0.9 | 7.9 | 8.8 | 12.5 |  | 2286 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 847.8 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.13259 | 0.15502 | 0.23843 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.06725 | 0.079022 | 0.12133 | 0.2 | 8.9 | 9.9 | 14.8 |  | 942 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 896.24 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.38867 | 0.45308 | 0.70017 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.28771 | 0.33488 | 0.51521 | 0.5 | 8.9 | 9.9 | 14.8 |  | 1318 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1264 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.20807 | 0.23867 | 0.46027 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10238 | 0.11669 | 0.22413 | 0.4 | 8.7 | 9.8 | 14.3 |  | 1580 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1326 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3191 | 1.5142 | 2.9155 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.80755 | 0.93274 | 1.7919 | 0.7 | 8.7 | 9.8 | 14.3 |  | 1950 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1728.8 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.32375 | 0.37654 | 0.58218 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.12905 | 0.15084 | 0.23384 | 0.5 | 8.7 | 9.8 | 14.3 |  | 2161 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1995.2 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.81672 | 0.93595 | 1.8088 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.36094 | 0.41486 | 0.80035 | 0.9 | 8.7 | 9.8 | 14.3 |  | 2494 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 989.1 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.18422 | 0.21592 | 0.33952 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.092934 | 0.10926 | 0.17257 | 0.2 | 10.1 | 11.2 | 17.5 |  | 1099 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1045.16 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.5368 | 0.62753 | 0.99516 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.39489 | 0.46316 | 0.73371 | 0.5 | 10.1 | 11.2 | 17.5 |  | 1537 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1475.2 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.29198 | 0.33298 | 0.656 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14316 | 0.16346 | 0.32064 | 0.4 | 9.6 | 10.5 | 16.1 |  | 1844 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1547 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8523 | 2.1254 | 4.1724 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1374 | 1.302 | 2.5702 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2275 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1936.8 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.44617 | 0.52449 | 0.83232 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.17923 | 0.21006 | 0.33489 | 0.5 | 9.6 | 10.5 | 16.1 |  | 2421 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2327.2 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1494 | 1.316 | 2.58 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.50759 | 0.58151 | 1.1397 | 0.9 | 9.6 | 10.5 | 16.1 |  | 2909 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1130.4 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.24035 | 0.28467 | 0.45825 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.12271 | 0.14433 | 0.2327 | 0.2 | 11 | 12.4 | 19.2 |  | 1256 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1194.76 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.70432 | 0.82996 | 1.3412 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.52236 | 0.61192 | 0.98532 | 0.5 | 11 | 12.4 | 19.2 |  | 1757 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1685.6 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.38464 | 0.43716 | 0.88617 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.18883 | 0.21403 | 0.43431 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2107 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1768 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4404 | 2.7896 | 5.6357 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.4959 | 1.713 | 3.4741 | 0.7 | 11.5 | 12.8 | 19.6 |  | 2600 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2305.6 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.58812 | 0.69359 | 1.1269 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.23572 | 0.27698 | 0.45137 | 0.5 | 11.5 | 12.8 | 19.6 |  | 2882 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2660 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.516 | 1.7243 | 3.4956 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.66785 | 0.76014 | 1.5442 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3325 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1271.7 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.3126 | 0.36755 | 0.59457 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.15971 | 0.18592 | 0.3017 | 0.2 | 12.2 | 13.7 | 22 |  | 1413 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1343.68 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.9178 | 1.0756 | 1.7382 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.67552 | 0.79428 | 1.2847 | 0.5 | 12.2 | 13.7 | 22 |  | 1976 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1896.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.44001 | 0.50215 | 1.0163 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19642 | 0.22413 | 0.45153 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2371 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1989 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.941 | 3.3503 | 6.7845 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.5418 | 1.7621 | 3.572 | 0.7 | 11.5 | 12.8 | 19.6 |  | 2925 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2593.6 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.68715 | 0.80774 | 1.3107 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24717 | 0.28937 | 0.47247 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3242 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2992 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.6886 | 1.9269 | 3.9059 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.69036 | 0.78818 | 1.5954 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3740 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1413 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.37714 | 0.44506 | 0.74844 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.19105 | 0.22703 | 0.37956 | 0.2 | 13.4 | 14.8 | 24 |  | 1570 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1493.28 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1014 | 1.3015 | 2.1934 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.81202 | 0.96093 | 1.6107 | 0.5 | 13.4 | 14.8 | 24 |  | 2196 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2107.2 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.63179 | 0.69856 | 1.4549 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.30854 | 0.34302 | 0.71304 | 0.4 | 13.2 | 14.7 | 23.5 |  | 2634 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2210 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0067 | 4.4506 | 9.2646 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.4755 | 2.7278 | 5.6888 | 0.7 | 13.2 | 14.7 | 23.5 |  | 3250 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2881.6 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.92309 | 1.0942 | 1.8493 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.36943 | 0.43843 | 0.73955 | 0.5 | 13.2 | 14.7 | 23.5 |  | 3602 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3324.8 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.486 | 2.758 | 5.7307 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.0964 | 1.2187 | 2.5291 | 0.9 | 13.2 | 14.7 | 23.5 |  | 4156 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1554.3 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.44768 | 0.53277 | 0.9236 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.22703 | 0.27016 | 0.46626 | 0.2 | 13.4 | 14.8 | 24 |  | 1727 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1642.88 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.3071 | 1.561 | 2.6927 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 0.96578 | 1.1485 | 1.9869 | 0.5 | 13.4 | 14.8 | 24 |  | 2416 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2317.6 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.77625 | 0.84212 | 1.7888 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.37931 | 0.41187 | 0.87808 | 0.4 | 15.5 | 16.8 | 27.5 |  | 2897 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2431 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 4.9509 | 5.3565 | 11.3896 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.044 | 3.296 | 6.9994 | 0.7 | 15.5 | 16.8 | 27.5 |  | 3575 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3169.6 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.0983 | 1.3107 | 2.2771 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.441 | 0.52449 | 0.91195 | 0.5 | 15.5 | 16.8 | 27.5 |  | 3962 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3657.6 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.0601 | 3.3196 | 7.0476 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3527 | 1.4661 | 3.1159 | 0.9 | 15.5 | 16.8 | 27.5 |  | 4572 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1695.6 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.52706 | 0.62828 | 1.1129 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.26609 | 0.31922 | 0.56178 | 0.2 | 14.8 | 16.6 | 28 |  | 1884 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1791.8 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.5364 | 1.8371 | 3.2427 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.1327 | 1.3527 | 2.387 | 0.5 | 14.8 | 16.6 | 28 |  | 2635 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2528.8 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.93968 | 1.0077 | 2.1571 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.46027 | 0.49302 | 1.0558 | 0.4 | 16.4 | 17.7 | 29.7 |  | 3161 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2652 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 5.9764 | 6.4212 | 13.761 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.6712 | 3.9473 | 8.4672 | 0.7 | 16.4 | 17.7 | 29.7 |  | 3900 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3457.6 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.2931 | 1.5467 | 2.7492 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.51889 | 0.62129 | 1.1023 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4322 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3989.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.6935 | 3.969 | 8.5002 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6301 | 1.7542 | 3.7637 | 0.9 | 16.4 | 17.7 | 29.7 |  | 4987 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1836.9 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.61284 | 0.74506 | 1.3196 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.3104 | 0.37714 | 0.66611 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2041 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1941.4 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.7972 | 2.1788 | 3.8433 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.3241 | 1.6044 | 2.8317 | 0.5 | 16.2 | 18.6 | 31.4 |  | 2855 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2739.2 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.025 | 1.1005 | 2.3574 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.46909 | 0.50521 | 1.0825 | 0.4 | 16.4 | 17.7 | 29.7 |  | 3424 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2893.4 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.7265 | 7.2177 | 15.4955 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.7429 | 4.0216 | 8.5976 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4255 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3746.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4056 | 1.7098 | 3.0322 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.52449 | 0.63667 | 1.131 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4683 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4322.4 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 3.969 | 4.2636 | 9.1467 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.6651 | 1.7906 | 3.8345 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5403 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
23510 |  |  | 2 | 35 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1978.2 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.65973 | 0.80363 | 1.4155 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.32145 | 0.3893 | 0.68543 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2198 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
23511 |  |  | 2 | 35 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2090.32 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 1.9939 | 2.4252 | 4.2683 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.3412 | 1.6295 | 2.8732 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3074 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
23515 |  |  | 2 | 35 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2950.4 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3082 | 1.363 | 3.004 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.63866 | 0.67004 | 1.4705 | 0.4 | 19.3 | 20.4 | 34.5 |  | 3688 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
23516 |  |  | 2 | 35 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3094 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.3163 | 8.6851 | 19.1422 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1011 | 5.3392 | 11.7693 | 0.7 | 19.3 | 20.4 | 34.5 |  | 4550 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
23520 |  |  | 2 | 35 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4034.4 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7711 | 2.156 | 3.819 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.70984 | 0.86445 | 1.5323 | 0.5 | 19.3 | 20.4 | 34.5 |  | 5043 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
23521 |  |  | 2 | 35 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4654.4 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.1385 | 5.3778 | 11.8278 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 1.9458 | 2.0356 | 4.4723 | 0.9 | 19.3 | 20.4 | 34.5 |  | 5818 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.016857 | 0.01965 | 0.026529 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0085435 | 0.0097389 | 0.013782 | 0.3 | 3.6 | 4.1 | 5.1 |  | 482 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 445.4 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.050581 | 0.05791 | 0.078337 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 1 | 1 | 1 | 166 | 178 | 208 | 71 | 77 | 89 | 0.037378 | 0.043737 | 0.05791 | 0.7 | 3.6 | 4.1 | 5.1 |  | 655 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 208 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.02858 | 0.032164 | 0.045024 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.014274 | 0.016857 | 0.022651 | 0.3 | 4.8 | 5.4 | 6.8 |  | 578 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 533.8 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.084292 | 0.096838 | 0.1338 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 1 | 1 | 1 | 215 | 231 | 273 | 92 | 99 | 117 | 0.061755 | 0.071194 | 0.098466 | 0.7 | 4.8 | 5.4 | 6.8 |  | 785 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 215 | 231 | 273 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 736 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.040945 | 0.046453 | 0.081641 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.20426 | 0.023025 | 0.04006 | 0.5 | 4.8 | 5.5 | 7.2 |  | 920 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 796.28 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.25099 | 0.29015 | 0.50664 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 1 | 1 | 1 | 241 | 259 | 343 | 104 | 111 | 147 | 0.15636 | 0.17794 | 0.31079 | 1 | 4.8 | 5.5 | 7.2 |  | 1171 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 241 | 259 | 343 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1017.6 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.063262 | 0.073526 | 0.10254 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.025306 | 0.029205 | 0.040959 | 0.7 | 4.8 | 5.5 | 7.2 |  | 1272 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1230.4 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.15981 | 0.18276 | 0.32038 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 1 | 1 | 1 | 263 | 283 | 374 | 113 | 122 | 161 | 0.070452 | 0.081971 | 0.14185 | 1.3 | 4.8 | 5.5 | 7.2 |  | 1538 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 263 | 283 | 374 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 607.5 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.042452 | 0.048569 | 0.068264 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.021426 | 0.024553 | 0.035181 | 0.3 | 5.5 | 5.9 | 7.9 |  | 675 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 622.88 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.12447 | 0.14346 | 0.20361 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.093622 | 0.1068 | 0.14941 | 0.7 | 5.5 | 5.9 | 7.9 |  | 916 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 858.4 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.050317 | 0.058503 | 0.1015 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.021062 | 0.024382 | 0.042743 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1073 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 928.88 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.34088 | 0.39094 | 0.68614 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.16238 | 0.18761 | 0.32782 | 1 | 5.1 | 5.6 | 7.2 |  | 1366 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1187.2 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.080053 | 0.091543 | 0.1306 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027221 | 0.031259 | 0.044205 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1484 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1436 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19075 | 0.22005 | 0.38322 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.075464 | 0.086002 | 0.1507 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1795 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693.9 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.058006 | 0.066147 | 0.096216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.029989 | 0.034414 | 0.049475 | 0.3 | 6.3 | 6.8 | 9.1 |  | 771 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 711.96 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.17225 | 0.19897 | 0.28489 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.12816 | 0.14543 | 0.21066 | 0.7 | 6.3 | 6.8 | 9.1 |  | 1047 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.08544 | 0.098724 | 0.17572 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.041839 | 0.048366 | 0.086726 | 0.5 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1061.48 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.53376 | 0.61345 | 1.1024 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32782 | 0.37695 | 0.67993 | 1 | 6 | 6.7 | 9 |  | 1561 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1356.8 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13202 | 0.15119 | 0.22007 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.052857 | 0.061301 | 0.089183 | 0.7 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1640.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.33623 | 0.38608 | 0.69032 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14891 | 0.1711 | 0.30491 | 1.3 | 6 | 6.7 | 9 |  | 2051 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 781.2 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.075931 | 0.087579 | 0.12886 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.039137 | 0.045024 | 0.066147 | 0.3 | 6.7 | 7.4 | 10.3 |  | 868 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 801.04 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.22512 | 0.26068 | 0.38263 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.16798 | 0.19212 | 0.28215 | 0.7 | 6.7 | 7.4 | 10.3 |  | 1178 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1104 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11149 | 0.12815 | 0.23705 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.055362 | 0.062825 | 0.11592 | 0.5 | 7 | 7.7 | 10.7 |  | 1380 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1194.08 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.69865 | 0.80277 | 1.4856 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.42949 | 0.49599 | 0.91409 | 1 | 7 | 7.7 | 10.7 |  | 1756 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1526.4 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17327 | 0.20033 | 0.29749 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.070366 | 0.081167 | 0.11951 | 0.7 | 7 | 7.7 | 10.7 |  | 1908 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1846.4 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.43934 | 0.50252 | 0.92966 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.19481 | 0.2244 | 0.41228 | 1.3 | 7 | 7.7 | 10.7 |  | 2308 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 867.6 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.096216 | 0.1106 | 0.16616 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.049475 | 0.057025 | 0.085184 | 0.3 | 7.8 | 8.7 | 12.2 |  | 964 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 890.12 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.28489 | 0.33052 | 0.49084 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.21066 | 0.24513 | 0.36381 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1309 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14098 | 0.16137 | 0.30506 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.069595 | 0.079155 | 0.14931 | 0.5 | 7 | 7.7 | 10.7 |  | 1533 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1326.68 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.88558 | 1.0174 | 1.9255 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.54481 | 0.62528 | 1.1827 | 1 | 7 | 7.7 | 10.7 |  | 1951 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1696 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22007 | 0.25634 | 0.38406 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.089183 | 0.1038 | 0.15579 | 0.7 | 7 | 7.7 | 10.7 |  | 2120 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2051.2 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.5561 | 0.63417 | 1.1993 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.24681 | 0.28241 | 0.53233 | 1.3 | 7 | 7.7 | 10.7 |  | 2564 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 954 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12026 | 0.13925 | 0.20811 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.062011 | 0.071501 | 0.10658 | 0.3 | 8.4 | 9.3 | 14 |  | 1060 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 979.2 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.35764 | 0.41173 | 0.61623 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.26332 | 0.30444 | 0.45561 | 0.7 | 8.4 | 9.3 | 14 |  | 1440 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1348.8 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15961 | 0.18125 | 0.34482 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.071928 | 0.081641 | 0.15442 | 0.5 | 7.9 | 8.8 | 12.5 |  | 1686 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1459.28 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0402 | 1.1908 | 2.2504 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.55597 | 0.64325 | 1.2155 | 1 | 7.9 | 8.8 | 12.5 |  | 2146 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1865.6 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25239 | 0.29324 | 0.4392 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.092734 | 0.10762 | 0.16047 | 0.7 | 7.9 | 8.8 | 12.5 |  | 2332 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2256 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.61237 | 0.70183 | 1.323 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.25374 | 0.28981 | 0.54925 | 1.3 | 7.9 | 8.8 | 12.5 |  | 2820 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1041.3 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.1423 | 0.16616 | 0.25469 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.072596 | 0.085184 | 0.13032 | 0.3 | 8.9 | 9.9 | 14.8 |  | 1157 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1068.28 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.42166 | 0.49084 | 0.75556 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.31302 | 0.36381 | 0.5575 | 0.7 | 8.9 | 9.9 | 14.8 |  | 1571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1472 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.21425 | 0.24563 | 0.47256 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10572 | 0.12043 | 0.23072 | 0.5 | 8.7 | 9.8 | 14.3 |  | 1840 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1591.88 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3428 | 1.541 | 2.9626 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.8231 | 0.95035 | 1.8229 | 1 | 8.7 | 9.8 | 14.3 |  | 2341 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33035 | 0.38406 | 0.59314 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13202 | 0.15425 | 0.23882 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2544 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2461.6 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.83892 | 0.96093 | 1.853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.37189 | 0.42721 | 0.82216 | 1.3 | 8.7 | 9.8 | 14.3 |  | 3077 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1215 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.19719 | 0.23082 | 0.36171 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10004 | 0.11746 | 0.18481 | 0.3 | 10.1 | 11.2 | 17.5 |  | 1350 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1246.44 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.58065 | 0.67784 | 1.0706 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.42835 | 0.50166 | 0.79144 | 0.7 | 10.1 | 11.2 | 17.5 |  | 1833 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1716.8 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30027 | 0.34226 | 0.6727 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14762 | 0.16846 | 0.32963 | 0.5 | 9.6 | 10.5 | 16.1 |  | 2146 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1857.08 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8841 | 2.1613 | 4.2367 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1583 | 1.3255 | 2.6125 | 1 | 9.6 | 10.5 | 16.1 |  | 2731 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.45488 | 0.5345 | 0.84723 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18319 | 0.2146 | 0.34168 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2968 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2872 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1792 | 1.3495 | 2.64 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.5223 | 0.59805 | 1.1693 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3590 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1387.8 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.25674 | 0.30367 | 0.48711 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.13179 | 0.1548 | 0.24862 | 0.3 | 11 | 12.4 | 19.2 |  | 1542 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1423.92 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.76 | 0.8943 | 1.4394 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.56517 | 0.66113 | 1.0601 | 0.7 | 11 | 12.4 | 19.2 |  | 2094 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1962.4 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.39516 | 0.44891 | 0.90784 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.19451 | 0.22035 | 0.44599 | 0.5 | 11.5 | 12.8 | 19.6 |  | 2453 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2122.96 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4809 | 2.8351 | 5.7191 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.5224 | 1.7427 | 3.529 | 1 | 11.5 | 12.8 | 19.6 |  | 3122 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.59917 | 0.70634 | 1.1463 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24073 | 0.28274 | 0.46016 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3392 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3281.6 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.554 | 1.7666 | 3.5736 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.6865 | 0.781 | 1.5827 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4102 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1561.5 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.33323 | 0.39134 | 0.63084 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.17115 | 0.19899 | 0.3217 | 0.3 | 12.2 | 13.7 | 22 |  | 1735 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1602.08 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.98809 | 1.1564 | 1.8615 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.72919 | 0.85618 | 1.3791 | 0.7 | 12.2 | 13.7 | 22 |  | 2356 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2207.2 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.45183 | 0.51539 | 1.0407 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.20229 | 0.23072 | 0.46362 | 0.5 | 11.5 | 12.8 | 19.6 |  | 2759 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.16 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.9885 | 3.4035 | 6.8824 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.569 | 1.7926 | 3.6282 | 1 | 11.5 | 12.8 | 19.6 |  | 3512 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.69979 | 0.82228 | 1.3328 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25239 | 0.29536 | 0.48161 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3816 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3692 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7303 | 1.9735 | 3.9919 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.70956 | 0.8097 | 1.6351 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4615 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1735.2 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.40147 | 0.47319 | 0.79282 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.20444 | 0.24261 | 0.40402 | 0.3 | 13.4 | 14.8 | 24 |  | 1928 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1780.24 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1839 | 1.3971 | 2.3445 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.87514 | 1.0341 | 1.7259 | 0.7 | 13.4 | 14.8 | 24 |  | 2618 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2452.8 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.64795 | 0.71619 | 1.4882 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.31723 | 0.35254 | 0.73099 | 0.5 | 13.2 | 14.7 | 23.5 |  | 3066 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2653.36 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0688 | 4.5186 | 9.3927 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.5164 | 2.7723 | 5.7729 | 1 | 13.2 | 14.7 | 23.5 |  | 3902 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3392 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.9394 | 1.1131 | 1.879 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.37682 | 0.447 | 0.75301 | 0.7 | 13.2 | 14.7 | 23.5 |  | 4240 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4102.4 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.5441 | 2.8216 | 5.8504 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.125 | 1.2501 | 2.5881 | 1.3 | 13.2 | 14.7 | 23.5 |  | 5128 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1908.9 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.47596 | 0.56571 | 0.97696 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.24261 | 0.28832 | 0.49556 | 0.3 | 13.4 | 14.8 | 24 |  | 2121 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1958.4 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.4031 | 1.6731 | 2.8737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 1.0393 | 1.2342 | 2.1255 | 0.7 | 13.4 | 14.8 | 24 |  | 2880 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2698.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.79556 | 0.86285 | 1.8286 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.3897 | 0.42302 | 0.89958 | 0.5 | 15.5 | 16.8 | 27.5 |  | 3373 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2918.56 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.0255 | 5.4363 | 11.5429 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.093 | 3.3484 | 7.1 | 1 | 15.5 | 16.8 | 27.5 |  | 4292 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1172 | 1.3328 | 2.3127 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.44962 | 0.5345 | 0.92809 | 0.7 | 15.5 | 16.8 | 27.5 |  | 4664 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4512.8 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.1297 | 3.3942 | 7.1908 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3871 | 1.5029 | 3.1866 | 1.3 | 15.5 | 16.8 | 27.5 |  | 5641 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2082.6 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.55969 | 0.66635 | 1.1757 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.284 | 0.34024 | 0.59629 | 0.3 | 14.8 | 16.6 | 28 |  | 2314 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2136.56 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.647 | 1.9665 | 3.4558 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.2173 | 1.4515 | 2.5499 | 0.7 | 14.8 | 16.6 | 28 |  | 3142 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2943.2 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.96247 | 1.0319 | 2.2039 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.47256 | 0.50606 | 1.081 | 0.5 | 16.4 | 17.7 | 29.7 |  | 3679 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3183.76 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.0642 | 6.5145 | 13.9415 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.7288 | 4.0086 | 8.5857 | 1 | 16.4 | 17.7 | 29.7 |  | 4682 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3149 | 1.5722 | 2.7911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.52881 | 0.63288 | 1.1214 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5088 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4923.2 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.7754 | 4.0561 | 8.6685 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6704 | 1.7973 | 3.8469 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6154 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2255.4 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.65009 | 0.78926 | 1.3926 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.33091 | 0.40147 | 0.70618 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2506 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2314.04 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.9241 | 2.3291 | 4.0906 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.4212 | 1.7193 | 3.0209 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3403 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3188.8 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0496 | 1.1266 | 2.4079 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.48158 | 0.51852 | 1.1083 | 0.5 | 16.4 | 17.7 | 29.7 |  | 3986 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3449.64 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.8237 | 7.321 | 15.6954 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.8014 | 4.0839 | 8.7177 | 1 | 16.4 | 17.7 | 29.7 |  | 5073 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.429 | 1.7376 | 3.0778 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.5345 | 0.64851 | 1.1505 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5512 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5332.8 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.0561 | 4.3564 | 9.326 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.7062 | 1.8343 | 3.919 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6666 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
25010 |  |  | 2 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2429.1 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.69946 | 0.85087 | 1.4931 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.34259 | 0.41431 | 0.72652 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2699 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
25011 |  |  | 2 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2492.2 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.1329 | 2.5903 | 4.5395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.4394 | 1.7459 | 3.0648 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3665 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
25015 |  |  | 2 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3433.6 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3386 | 1.3944 | 3.0663 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.65498 | 0.68705 | 1.5041 | 0.5 | 19.3 | 20.4 | 34.5 |  | 4292 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
25016 |  |  | 2 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3714.84 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.433 | 8.8063 | 19.3822 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1776 | 5.4188 | 11.927 | 1 | 19.3 | 20.4 | 34.5 |  | 5463 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
25020 |  |  | 2 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7998 | 2.19 | 3.8746 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.72284 | 0.87987 | 1.5576 | 0.7 | 19.3 | 20.4 | 34.5 |  | 5936 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
25021 |  |  | 2 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5743.2 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.2475 | 5.4911 | 12.0517 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 1.9929 | 2.0845 | 4.569 | 1.3 | 19.3 | 20.4 | 34.5 |  | 7179 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 504.9 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.018315 | 0.021321 | 0.028713 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0093387 | 0.010633 | 0.015001 | 0.4 | 3.6 | 4.1 | 5.1 |  | 561 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 504.56 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.055558 | 0.063526 | 0.085696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 136.4943 | 146.0591 | 170.792 | 1 | 1 | 1 | 154 | 164 | 192 | 66 | 71 | 83 | 0.035795 | 0.041174 | 0.055558 | 0.9 | 3.6 | 4.1 | 5.1 |  | 742 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 154 | 164 | 192 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 605.7 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.030914 | 0.034757 | 0.048521 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.015531 | 0.018315 | 0.024549 | 0.4 | 4.8 | 5.4 | 6.8 |  | 673 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 605.2 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.092148 | 0.10573 | 0.14567 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 176.675 | 189.625 | 223.85 | 1 | 1 | 1 | 199 | 214 | 252 | 86 | 92 | 108 | 0.059477 | 0.067704 | 0.092148 | 0.9 | 4.8 | 5.4 | 6.8 |  | 890 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 199 | 214 | 252 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.042405 | 0.048084 | 0.084306 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.21018 | 0.023909 | 0.041493 | 0.7 | 4.8 | 5.5 | 7.2 |  | 1029 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 908.48 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.25653 | 0.29644 | 0.51684 | 0.0002083 | 1.724 | 4 | 0.0013928 | 197.95 | 212.75 | 282.125 | 1 | 1 | 1 | 223 | 240 | 318 | 96 | 103 | 137 | 0.1366 | 0.157 | 0.27613 | 1.3 | 4.8 | 5.5 | 7.2 |  | 1336 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 223 | 240 | 318 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1148 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.064835 | 0.075319 | 0.10493 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.026015 | 0.030009 | 0.042037 | 0.9 | 4.8 | 5.5 | 7.2 |  | 1435 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1442.4 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.16506 | 0.18866 | 0.33 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 216.2921 | 232.1848 | 307.3035 | 1 | 1 | 1 | 244 | 261 | 346 | 105 | 112 | 149 | 0.063205 | 0.071759 | 0.12585 | 1.7 | 4.8 | 5.5 | 7.2 |  | 1803 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 244 | 261 | 346 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 706.5 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.045771 | 0.05231 | 0.073326 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.023232 | 0.026592 | 0.037989 | 0.4 | 5.5 | 5.9 | 7.9 |  | 785 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 705.84 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.1356 | 0.15609 | 0.22087 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216.4625 | 232.1327 | 277.537 | 1 | 1 | 1 | 244 | 261 | 313 | 105 | 112 | 135 | 0.087288 | 0.098827 | 0.1416 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1038 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 244 | 261 | 313 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 960.8 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.052065 | 0.060496 | 0.10472 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.02188 | 0.025311 | 0.044259 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1201 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1060.12 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.34811 | 0.39909 | 0.69942 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.1279 | 218.0533 | 288.6 | 1 | 1 | 1 | 229 | 246 | 325 | 98 | 106 | 140 | 0.14228 | 0.16618 | 0.28823 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1559 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 229 | 246 | 325 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1339.2 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.081982 | 0.09371 | 0.13355 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027977 | 0.032112 | 0.045357 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1674 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1683.2 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19688 | 0.22698 | 0.39446 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.2818 | 238.6146 | 315.8135 | 1 | 1 | 1 | 250 | 269 | 356 | 108 | 116 | 153 | 0.066805 | 0.076887 | 0.13259 | 1.7 | 5.1 | 5.6 | 7.2 |  | 2104 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 250 | 269 | 356 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 807.3 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.062387 | 0.071069 | 0.10308 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.032425 | 0.037168 | 0.053278 | 0.4 | 6.3 | 6.8 | 9.1 |  | 897 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 806.48 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.18712 | 0.21588 | 0.30817 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255.3 | 273.8 | 331.15 | 1 | 1 | 1 | 288 | 308 | 373 | 124 | 132 | 160 | 0.12022 | 0.1356 | 0.19648 | 0.9 | 6.3 | 6.8 | 9.1 |  | 1186 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 288 | 308 | 373 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1097.6 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.088213 | 0.10187 | 0.18091 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.043327 | 0.050055 | 0.089535 | 0.7 | 6 | 6.7 | 9 |  | 1372 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1211.76 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.54444 | 0.62549 | 1.1224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 288.6 | 309.875 | 416.25 | 1 | 1 | 1 | 325 | 349 | 469 | 140 | 150 | 202 | 0.28823 | 0.33043 | 0.5959 | 1.3 | 6 | 6.7 | 9 |  | 1782 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 325 | 349 | 469 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1530.4 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.135 | 0.15454 | 0.22471 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.054203 | 0.062832 | 0.091303 | 0.9 | 6 | 6.7 | 9 |  | 1913 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1923.2 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.34626 | 0.39739 | 0.70905 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315.2976 | 338.1017 | 453.6385 | 1 | 1 | 1 | 355 | 381 | 511 | 153 | 164 | 220 | 0.13259 | 0.15202 | 0.27123 | 1.7 | 6 | 6.7 | 9 |  | 2404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 355 | 381 | 511 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 908.1 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.081495 | 0.093894 | 0.13775 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.042225 | 0.048521 | 0.071069 | 0.4 | 6.7 | 7.4 | 10.3 |  | 1009 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 907.8 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.24399 | 0.28219 | 0.41289 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 293.3758 | 315.5893 | 384.282 | 1 | 1 | 1 | 330 | 355 | 433 | 142 | 153 | 186 | 0.15609 | 0.18024 | 0.26275 | 0.9 | 6.7 | 7.4 | 10.3 |  | 1335 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 330 | 355 | 433 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1235.2 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11499 | 0.13209 | 0.24379 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.057261 | 0.064946 | 0.11954 | 0.7 | 7 | 7.7 | 10.7 |  | 1544 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1362.72 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.71213 | 0.81798 | 1.5115 | 0.0002083 | 1.724 | 4 | 0.0013928 | 330.9459 | 354.5558 | 482.85 | 1 | 1 | 1 | 373 | 399 | 544 | 160 | 172 | 234 | 0.37549 | 0.43333 | 0.79758 | 1.3 | 7 | 7.7 | 10.7 |  | 2004 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 373 | 399 | 544 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1721.6 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17704 | 0.20461 | 0.30351 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.072092 | 0.08312 | 0.12225 | 0.9 | 7 | 7.7 | 10.7 |  | 2152 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2164 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.45199 | 0.51674 | 0.95392 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 361.0734 | 386.8326 | 526.806 | 1 | 1 | 1 | 407 | 436 | 593 | 175 | 187 | 255 | 0.17276 | 0.19688 | 0.36292 | 1.7 | 7 | 7.7 | 10.7 |  | 2705 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 407 | 436 | 593 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1008.9 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.10308 | 0.11836 | 0.1773 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.053278 | 0.06134 | 0.091346 | 0.4 | 7.8 | 8.7 | 12.2 |  | 1121 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1008.44 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.30817 | 0.35709 | 0.52861 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 331.15 | 356.125 | 437.525 | 1 | 1 | 1 | 373 | 401 | 493 | 160 | 172 | 212 | 0.19648 | 0.22591 | 0.33833 | 0.9 | 7.8 | 8.7 | 12.2 |  | 1483 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 373 | 401 | 493 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1372 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14527 | 0.16619 | 0.31346 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.071914 | 0.08175 | 0.15382 | 0.7 | 7 | 7.7 | 10.7 |  | 1715 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1514.36 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.90215 | 1.0361 | 1.958 | 0.0002083 | 1.724 | 4 | 0.0013928 | 372.775 | 398.675 | 550.375 | 1 | 1 | 1 | 420 | 449 | 620 | 181 | 193 | 267 | 0.47941 | 0.54444 | 1.0361 | 1.3 | 7 | 7.7 | 10.7 |  | 2227 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 420 | 449 | 620 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1912.8 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22471 | 0.26163 | 0.39158 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.091303 | 0.10622 | 0.15923 | 0.9 | 7 | 7.7 | 10.7 |  | 2391 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2404 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.57163 | 0.65158 | 1.2295 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 406.4601 | 435.2289 | 599.9735 | 1 | 1 | 1 | 458 | 490 | 676 | 197 | 211 | 291 | 0.21817 | 0.24979 | 0.47097 | 1.7 | 7 | 7.7 | 10.7 |  | 3005 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 458 | 490 | 676 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.7 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12862 | 0.14878 | 0.22171 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.066659 | 0.076776 | 0.11409 | 0.4 | 8.4 | 9.3 | 14 |  | 1233 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.08 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.38614 | 0.44403 | 0.66245 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 371.314 | 400.0249 | 491.027 | 1 | 1 | 1 | 418 | 451 | 553 | 180 | 194 | 238 | 0.24663 | 0.28502 | 0.42315 | 0.9 | 8.4 | 9.3 | 14 |  | 1631 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 418 | 451 | 553 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1509.6 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.16439 | 0.18659 | 0.35416 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.074314 | 0.084306 | 0.15906 | 0.7 | 7.9 | 8.8 | 12.5 |  | 1887 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1666 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0593 | 1.2122 | 2.2875 | 0.0002083 | 1.724 | 4 | 0.0013928 | 377.2455 | 403.9466 | 556.85 | 1 | 1 | 1 | 425 | 455 | 627 | 183 | 196 | 270 | 0.48996 | 0.56134 | 1.0593 | 1.3 | 7.9 | 8.8 | 12.5 |  | 2450 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 425 | 455 | 627 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2104 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25762 | 0.29919 | 0.44764 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.094926 | 0.11012 | 0.16399 | 0.9 | 7.9 | 8.8 | 12.5 |  | 2630 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2644.8 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.62926 | 0.72084 | 1.3559 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 412.2253 | 441.4022 | 608.4835 | 1 | 1 | 1 | 464 | 497 | 685 | 200 | 214 | 295 | 0.22476 | 0.25684 | 0.48383 | 1.7 | 7.9 | 8.8 | 12.5 |  | 3306 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 464 | 497 | 685 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1210.5 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.15201 | 0.1773 | 0.27096 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.077943 | 0.091346 | 0.1393 | 0.4 | 8.9 | 9.9 | 14.8 |  | 1345 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1210.4 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.45466 | 0.52861 | 0.81096 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 404.225 | 437.525 | 544.825 | 1 | 1 | 1 | 455 | 493 | 614 | 196 | 212 | 264 | 0.29072 | 0.33833 | 0.51717 | 0.9 | 8.9 | 9.9 | 14.8 |  | 1780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 455 | 493 | 614 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1646.4 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.22042 | 0.25258 | 0.48484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10906 | 0.12417 | 0.2373 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2058 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1816.96 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3666 | 1.5677 | 3.0098 | 0.0002083 | 1.724 | 4 | 0.0013928 | 458.8 | 492.1 | 684.5 | 1 | 1 | 1 | 517 | 554 | 771 | 222 | 238 | 332 | 0.71854 | 0.82484 | 1.5962 | 1.3 | 8.7 | 9.8 | 14.3 |  | 2672 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 517 | 554 | 771 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2295.2 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33694 | 0.39158 | 0.60409 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.135 | 0.15766 | 0.2438 | 0.9 | 8.7 | 9.8 | 14.3 |  | 2869 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2884.8 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.86112 | 0.98591 | 1.8972 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 500.9437 | 536.44 | 746.3085 | 1 | 1 | 1 | 564 | 604 | 840 | 243 | 260 | 361 | 0.33 | 0.37709 | 0.72084 | 1.7 | 8.7 | 9.8 | 14.3 |  | 3606 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 564 | 604 | 840 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1412.1 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.21016 | 0.24573 | 0.38389 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10715 | 0.12565 | 0.19706 | 0.4 | 10.1 | 11.2 | 17.5 |  | 1569 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1411.68 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.62449 | 0.72814 | 1.1461 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 476.375 | 516.15 | 651.2 | 1 | 1 | 1 | 536 | 581 | 733 | 230 | 250 | 315 | 0.39607 | 0.46541 | 0.72814 | 0.9 | 10.1 | 11.2 | 17.5 |  | 2076 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 536 | 581 | 733 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1920.8 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30855 | 0.35154 | 0.6894 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.15209 | 0.17347 | 0.33861 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2401 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2120.24 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.916 | 2.1972 | 4.301 | 0.0002083 | 1.724 | 4 | 0.0013928 | 544.825 | 582.75 | 818.625 | 1 | 1 | 1 | 614 | 656 | 922 | 264 | 282 | 396 | 1.0131 | 1.1547 | 2.2648 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3118 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 614 | 656 | 922 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2677.6 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.46358 | 0.54451 | 0.86215 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18714 | 0.21913 | 0.34847 | 0.9 | 9.6 | 10.5 | 16.1 |  | 3347 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3365.6 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.2091 | 1.383 | 2.7 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 594.0588 | 636.1954 | 892.6435 | 1 | 1 | 1 | 669 | 716 | 1005 | 288 | 308 | 432 | 0.46143 | 0.52682 | 1.0278 | 1.7 | 9.6 | 10.5 | 16.1 |  | 4207 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 669 | 716 | 1005 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1614.6 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.27312 | 0.32268 | 0.51598 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.14086 | 0.16526 | 0.26454 | 0.4 | 11 | 12.4 | 19.2 |  | 1794 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1613.64 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.81569 | 0.95863 | 1.5375 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.6 | 593.85 | 757.575 | 1 | 1 | 1 | 617 | 669 | 853 | 265 | 288 | 367 | 0.52097 | 0.61208 | 0.97923 | 0.9 | 11 | 12.4 | 19.2 |  | 2373 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 617 | 669 | 853 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2195.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.40567 | 0.46065 | 0.92951 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.20018 | 0.22668 | 0.45767 | 0.7 | 11.5 | 12.8 | 19.6 |  | 2744 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2422.84 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.5213 | 2.8805 | 5.8025 | 0.0002083 | 1.724 | 4 | 0.0013928 | 625.3 | 667.85 | 952.75 | 1 | 1 | 1 | 704 | 752 | 1073 | 303 | 323 | 461 | 1.3315 | 1.5115 | 3.0623 | 1.3 | 11.5 | 12.8 | 19.6 |  | 3563 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 704 | 752 | 1073 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3060.8 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.61022 | 0.71908 | 1.1657 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24575 | 0.2885 | 0.46895 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3826 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3846.4 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.5919 | 1.809 | 3.6517 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 682.6809 | 728.8758 | 1038.9785 | 1 | 1 | 1 | 769 | 821 | 1170 | 331 | 353 | 503 | 0.60733 | 0.68963 | 1.3885 | 1.7 | 11.5 | 12.8 | 19.6 |  | 4808 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 769 | 821 | 1170 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1816.2 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.35386 | 0.41512 | 0.66711 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.18259 | 0.21206 | 0.3417 | 0.4 | 12.2 | 13.7 | 22 |  | 2018 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1814.92 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 1.0584 | 1.2372 | 1.9847 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 624.4704 | 677.8928 | 864.6345 | 1 | 1 | 1 | 703 | 763 | 974 | 302 | 328 | 419 | 0.67104 | 0.78752 | 1.2664 | 0.9 | 12.2 | 13.7 | 22 |  | 2669 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 703 | 763 | 974 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2469.6 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.46364 | 0.52864 | 1.0651 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.20816 | 0.2373 | 0.4757 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3087 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2726.12 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 3.036 | 3.4567 | 6.9804 | 0.0002083 | 1.724 | 4 | 0.0013928 | 634.8357 | 677.7931 | 966.1625 | 1 | 1 | 1 | 715 | 763 | 1088 | 307 | 328 | 468 | 1.3666 | 1.5583 | 3.1554 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4009 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 715 | 763 | 1088 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3443.2 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.71243 | 0.83681 | 1.3549 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25762 | 0.30135 | 0.49076 | 0.9 | 11.5 | 12.8 | 19.6 |  | 4304 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4327.2 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7719 | 2.0202 | 4.0778 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 693.8642 | 740.8158 | 1055.9985 | 1 | 1 | 1 | 781 | 834 | 1189 | 336 | 359 | 511 | 0.62558 | 0.71297 | 1.4325 | 1.7 | 11.5 | 12.8 | 19.6 |  | 5409 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 781 | 834 | 1189 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2017.8 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.4258 | 0.50133 | 0.8372 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.21783 | 0.2582 | 0.42849 | 0.4 | 13.4 | 14.8 | 24 |  | 2242 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2016.88 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.2664 | 1.4926 | 2.4957 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 685.425 | 746.475 | 971.25 | 1 | 1 | 1 | 772 | 841 | 1094 | 332 | 362 | 470 | 0.80625 | 0.95352 | 1.583 | 0.9 | 13.4 | 14.8 | 24 |  | 2966 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 772 | 841 | 1094 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2744 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.66412 | 0.73382 | 1.5215 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.32591 | 0.36206 | 0.74894 | 0.7 | 13.2 | 14.7 | 23.5 |  | 3430 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3028.72 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.1309 | 4.5867 | 9.5209 | 0.0002083 | 1.724 | 4 | 0.0013928 | 802.9 | 845.45 | 1221 | 1 | 1 | 1 | 904 | 952 | 1375 | 389 | 409 | 591 | 2.186 | 2.4147 | 5.0154 | 1.3 | 13.2 | 14.7 | 23.5 |  | 4454 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 904 | 952 | 1375 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3825.6 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.95571 | 1.132 | 1.9088 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.38422 | 0.45558 | 0.76648 | 0.9 | 13.2 | 14.7 | 23.5 |  | 4782 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4808 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.6023 | 2.8853 | 5.9701 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 875.7193 | 922.7225 | 1331.6485 | 1 | 1 | 1 | 986 | 1039 | 1500 | 424 | 447 | 645 | 0.99052 | 1.0995 | 2.2706 | 1.7 | 13.2 | 14.7 | 23.5 |  | 6010 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 986 | 1039 | 1500 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2219.4 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.50424 | 0.59865 | 1.0303 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.2582 | 0.30647 | 0.52487 | 0.4 | 13.4 | 14.8 | 24 |  | 2466 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2218.84 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.499 | 1.7852 | 3.0547 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 748.4982 | 817.8264 | 1078.1245 | 1 | 1 | 1 | 843 | 921 | 1214 | 362 | 396 | 522 | 0.95352 | 1.135 | 1.9411 | 0.9 | 13.4 | 14.8 | 24 |  | 3263 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 843 | 921 | 1214 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3018.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.81488 | 0.88358 | 1.8684 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.40009 | 0.43418 | 0.92107 | 0.7 | 15.5 | 16.8 | 27.5 |  | 3773 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3331.32 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.1001 | 5.5161 | 11.6961 | 0.0002083 | 1.724 | 4 | 0.0013928 | 891.1063 | 928.2293 | 1354.6625 | 1 | 1 | 1 | 1004 | 1045 | 1526 | 432 | 449 | 656 | 2.6917 | 2.9061 | 6.1706 | 1.3 | 15.5 | 16.8 | 27.5 |  | 4899 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1004 | 1045 | 1526 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4208 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1362 | 1.3549 | 2.3483 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.45824 | 0.54451 | 0.94423 | 0.9 | 15.5 | 16.8 | 27.5 |  | 5260 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5288.8 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.1992 | 3.4689 | 7.3339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 972.2277 | 1012.7301 | 1477.9835 | 1 | 1 | 1 | 1095 | 1141 | 1664 | 471 | 491 | 716 | 1.2193 | 1.3238 | 2.7919 | 1.7 | 15.5 | 16.8 | 27.5 |  | 6611 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1095 | 1141 | 1664 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2421 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.59232 | 0.70442 | 1.2385 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.30191 | 0.36126 | 0.6308 | 0.4 | 14.8 | 16.6 | 28 |  | 2690 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2420.12 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.7576 | 2.0958 | 3.6689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 811.225 | 888.925 | 1184.925 | 1 | 1 | 1 | 914 | 1001 | 1334 | 393 | 430 | 574 | 1.1183 | 1.3318 | 2.3348 | 0.9 | 14.8 | 16.6 | 28 |  | 3559 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 914 | 1001 | 1334 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3292.8 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.98527 | 1.0561 | 2.2507 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.48484 | 0.5191 | 1.1062 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4116 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3634.6 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.152 | 6.6079 | 14.1219 | 0.0002083 | 1.724 | 4 | 0.0013928 | 979.575 | 1015.65 | 1489.25 | 1 | 1 | 1 | 1103 | 1144 | 1677 | 474 | 492 | 721 | 3.2362 | 3.4848 | 7.4448 | 1.3 | 16.4 | 17.7 | 29.7 |  | 5345 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1103 | 1144 | 1677 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4590.4 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3367 | 1.5977 | 2.833 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.53872 | 0.64447 | 1.1404 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5738 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5769.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.8573 | 4.1433 | 8.8369 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1068.7506 | 1107.6299 | 1624.3185 | 1 | 1 | 1 | 1204 | 1247 | 1829 | 518 | 536 | 786 | 1.4716 | 1.5744 | 3.358 | 1.7 | 16.4 | 17.7 | 29.7 |  | 7212 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1247 | 1829 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2623.5 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.68734 | 0.83347 | 1.4655 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.35141 | 0.4258 | 0.74625 | 0.4 | 16.2 | 18.6 | 31.4 |  | 2915 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2622.08 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 2.051 | 2.4794 | 4.338 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 878.2979 | 968.7109 | 1291.6145 | 1 | 1 | 1 | 989 | 1091 | 1455 | 425 | 469 | 626 | 1.3019 | 1.5764 | 2.764 | 0.9 | 16.2 | 18.6 | 31.4 |  | 3856 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 989 | 1091 | 1455 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3567.2 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0742 | 1.1528 | 2.4584 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.49407 | 0.53184 | 1.134 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4459 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3937.2 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.9209 | 7.4243 | 15.8953 | 0.0002083 | 1.724 | 4 | 0.0013928 | 988.7048 | 1024.6723 | 1502.6625 | 1 | 1 | 1 | 1113 | 1154 | 1692 | 479 | 496 | 728 | 3.3043 | 3.5413 | 7.5891 | 1.3 | 16.4 | 17.7 | 29.7 |  | 5790 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1113 | 1154 | 1692 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4973.6 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4525 | 1.7654 | 3.1233 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.54451 | 0.66034 | 1.1699 | 0.9 | 16.4 | 17.7 | 29.7 |  | 6217 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6250.4 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.1433 | 4.4491 | 9.5053 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1079.9492 | 1119.2361 | 1641.3385 | 1 | 1 | 1 | 1216 | 1260 | 1848 | 523 | 542 | 795 | 1.4998 | 1.6094 | 3.4346 | 1.7 | 16.4 | 17.7 | 29.7 |  | 7813 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1216 | 1260 | 1848 |  | 0 | 0 | 0 | 1
26510 |  |  | 2 | 65 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2825.1 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.7392 | 0.8981 | 1.5707 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.36374 | 0.43933 | 0.76761 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3139 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
26511 |  |  | 2 | 65 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2823.36 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.2719 | 2.7554 | 4.8107 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 884.3 | 976.8 | 1300.55 | 1 | 1 | 1 | 996 | 1100 | 1465 | 428 | 473 | 630 | 1.3198 | 1.6027 | 2.7985 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4152 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 996 | 1100 | 1465 |  | 0 | 0 | 0 | 1
26515 |  |  | 2 | 65 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3841.6 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3689 | 1.4259 | 3.1286 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.67129 | 0.70405 | 1.5377 | 0.7 | 19.3 | 20.4 | 34.5 |  | 4802 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
26516 |  |  | 2 | 65 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4240.48 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.5498 | 8.9275 | 19.6222 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1156.25 | 1182.15 | 1757.5 | 1 | 1 | 1 | 1302 | 1331 | 1979 | 560 | 572 | 851 | 4.5064 | 4.7002 | 10.3498 | 1.3 | 19.3 | 20.4 | 34.5 |  | 6236 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1302 | 1331 | 1979 |  | 0 | 0 | 0 | 1
26520 |  |  | 2 | 65 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5356 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.8284 | 2.2239 | 3.9302 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.73584 | 0.89528 | 1.5829 | 0.9 | 19.3 | 20.4 | 34.5 |  | 6695 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
26521 |  |  | 2 | 65 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6731.2 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.3564 | 5.6044 | 12.2756 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.1473 | 1193.2712 | 1773.2144 | 1 | 1 | 1 | 1314 | 1344 | 1997 | 565 | 578 | 859 | 1.7473 | 1.8277 | 4.0036 | 1.7 | 19.3 | 20.4 | 34.5 |  | 8414 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1314 | 1344 | 1997 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 746.6923 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.035582 | 0.039943 | 0.055515 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.018045 | 0.021232 | 0.028344 | 0.6 | 4.8 | 5.4 | 6.8 |  | 838 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.10786 | 0.12352 | 0.16941 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 148.025 | 158.875 | 187.55 | 1 | 1 | 1 | 167 | 179 | 211 | 72 | 77 | 91 | 0.05007 | 0.056844 | 0.077971 | 1.3 | 4.8 | 5.4 | 6.8 |  | 1055 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 167 | 179 | 211 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.045326 | 0.051344 | 0.089636 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.22203 | 0.025676 | 0.044358 | 1 | 4.8 | 5.5 | 7.2 |  | 1210 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1093.44 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.26762 | 0.30902 | 0.53725 | 0.0002083 | 1.724 | 4 | 0.0013928 | 165.85 | 178.25 | 236.375 | 1 | 1 | 1 | 187 | 201 | 266 | 80 | 86 | 114 | 0.099923 | 0.11519 | 0.20053 | 1.9 | 4.8 | 5.5 | 7.2 |  | 1608 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 266 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.067981 | 0.078903 | 0.10971 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.027435 | 0.031617 | 0.044194 | 1.3 | 4.8 | 5.5 | 7.2 |  | 1706 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1707.6437 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.17556 | 0.20047 | 0.34923 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 181.2177 | 194.5332 | 257.4705 | 1 | 1 | 1 | 204 | 219 | 290 | 88 | 94 | 125 | 0.048012 | 0.054595 | 0.095186 | 2.5 | 4.8 | 5.5 | 7.2 |  | 2290 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 204 | 219 | 290 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 879.3 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.052409 | 0.059791 | 0.08345 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.026843 | 0.030669 | 0.043605 | 0.6 | 5.5 | 5.9 | 7.9 |  | 977 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.15786 | 0.18135 | 0.25538 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.3604 | 194.4896 | 232.531 | 1 | 1 | 1 | 204 | 219 | 262 | 88 | 94 | 113 | 0.073177 | 0.08291 | 0.11753 | 1.3 | 5.5 | 5.9 | 7.9 |  | 1231 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 204 | 219 | 262 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.05556 | 0.064483 | 0.11116 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.023515 | 0.027169 | 0.047291 | 1 | 5.1 | 5.6 | 7.2 |  | 1411 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1275.68 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.36258 | 0.41538 | 0.72596 | 0.0002083 | 1.724 | 4 | 0.0013928 | 170.1882 | 182.6933 | 241.8 | 1 | 1 | 1 | 192 | 206 | 272 | 83 | 89 | 117 | 0.10742 | 0.12322 | 0.21105 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1876 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 272 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.085841 | 0.098046 | 0.13946 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.029489 | 0.033817 | 0.047661 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1991 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.20913 | 0.24086 | 0.41693 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 186.2361 | 199.9203 | 264.6005 | 1 | 1 | 1 | 210 | 225 | 298 | 90 | 97 | 128 | 0.05016 | 0.058043 | 0.099696 | 2.5 | 5.1 | 5.6 | 7.2 |  | 2671 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 210 | 225 | 298 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1005.3 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.071147 | 0.080914 | 0.11681 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.037297 | 0.042675 | 0.060884 | 0.6 | 6.3 | 6.8 | 9.1 |  | 1117 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.21685 | 0.2497 | 0.35472 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 213.9 | 229.4 | 277.45 | 1 | 1 | 1 | 241 | 258 | 312 | 104 | 111 | 134 | 0.10041 | 0.11361 | 0.16243 | 1.3 | 6.3 | 6.8 | 9.1 |  | 1406 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 241 | 258 | 312 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1290.4 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.093758 | 0.10816 | 0.1913 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.046303 | 0.053432 | 0.095153 | 1 | 6 | 6.7 | 9 |  | 1613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1457.92 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.56579 | 0.64958 | 1.1625 | 0.0002083 | 1.724 | 4 | 0.0013928 | 241.8 | 259.625 | 348.75 | 1 | 1 | 1 | 272 | 292 | 393 | 117 | 126 | 169 | 0.21105 | 0.2442 | 0.43546 | 1.9 | 6 | 6.7 | 9 |  | 2144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 272 | 292 | 393 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1820 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.14096 | 0.16124 | 0.23399 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.056895 | 0.065893 | 0.095541 | 1.3 | 6 | 6.7 | 9 |  | 2275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2442.4 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.36632 | 0.42001 | 0.74653 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264.1682 | 283.2744 | 380.0755 | 1 | 1 | 1 | 298 | 319 | 428 | 128 | 137 | 184 | 0.099696 | 0.11384 | 0.20261 | 2.5 | 6 | 6.7 | 9 |  | 3053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 298 | 319 | 428 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1130.4 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.092623 | 0.10652 | 0.15554 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.0484 | 0.055515 | 0.080914 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1256 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.28174 | 0.3252 | 0.47342 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 245.8013 | 264.4127 | 321.966 | 1 | 1 | 1 | 277 | 298 | 363 | 119 | 128 | 156 | 0.12965 | 0.14889 | 0.21685 | 1.3 | 6.7 | 7.4 | 10.3 |  | 1582 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 277 | 298 | 363 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1451.2 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.12198 | 0.13999 | 0.25728 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.061061 | 0.069188 | 0.12677 | 1 | 7 | 7.7 | 10.7 |  | 1814 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1640.16 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.7391 | 0.8484 | 1.5634 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277.279 | 297.0603 | 404.55 | 1 | 1 | 1 | 312 | 335 | 456 | 134 | 144 | 196 | 0.27567 | 0.31765 | 0.58326 | 1.9 | 7 | 7.7 | 10.7 |  | 2412 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 456 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2048 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.18458 | 0.21316 | 0.31556 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.075542 | 0.087026 | 0.12771 | 1.3 | 7 | 7.7 | 10.7 |  | 2560 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2747.2 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.4773 | 0.54519 | 1.0025 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 302.521 | 324.103 | 441.378 | 1 | 1 | 1 | 341 | 365 | 497 | 147 | 157 | 214 | 0.13064 | 0.14857 | 0.27229 | 2.5 | 7 | 7.7 | 10.7 |  | 3434 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 497 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1256.4 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.11681 | 0.1339 | 0.19959 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.060884 | 0.069969 | 0.10367 | 0.6 | 7.8 | 8.7 | 12.2 |  | 1396 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.35472 | 0.41022 | 0.60414 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277.45 | 298.375 | 366.575 | 1 | 1 | 1 | 312 | 336 | 413 | 134 | 144 | 178 | 0.16243 | 0.18624 | 0.27875 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1758 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 312 | 336 | 413 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1612.8 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.15384 | 0.17584 | 0.33025 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.076552 | 0.086938 | 0.16283 | 1 | 7 | 7.7 | 10.7 |  | 2016 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1822.4 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.93527 | 1.0734 | 2.023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312.325 | 334.025 | 461.125 | 1 | 1 | 1 | 352 | 376 | 519 | 151 | 162 | 223 | 0.34879 | 0.40063 | 0.75236 | 1.9 | 7 | 7.7 | 10.7 |  | 2680 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 352 | 376 | 519 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2275.2 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.23399 | 0.27222 | 0.40661 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.095541 | 0.11105 | 0.16611 | 1.3 | 7 | 7.7 | 10.7 |  | 2844 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3052.8 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.60269 | 0.68639 | 1.2901 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.5476 | 364.6513 | 502.6805 | 1 | 1 | 1 | 384 | 411 | 566 | 165 | 177 | 243 | 0.16372 | 0.18781 | 0.34923 | 2.5 | 7 | 7.7 | 10.7 |  | 3816 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 384 | 411 | 566 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1382.4 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.14536 | 0.16784 | 0.24892 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.075955 | 0.087325 | 0.12913 | 0.6 | 8.4 | 9.3 | 14 |  | 1536 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.44314 | 0.50864 | 0.7549 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 311.1009 | 335.156 | 411.401 | 1 | 1 | 1 | 350 | 377 | 463 | 151 | 162 | 199 | 0.20383 | 0.233 | 0.34474 | 1.3 | 8.4 | 9.3 | 14 |  | 1934 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 350 | 377 | 463 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1774.4 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.17395 | 0.19727 | 0.37283 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.079087 | 0.089636 | 0.16835 | 1 | 7.9 | 8.8 | 12.5 |  | 2218 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2004.64 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0974 | 1.2551 | 2.3619 | 0.0002083 | 1.724 | 4 | 0.0013928 | 316.0705 | 338.4417 | 466.55 | 1 | 1 | 1 | 356 | 381 | 525 | 153 | 164 | 226 | 0.35795 | 0.41044 | 0.77246 | 1.9 | 7.9 | 8.8 | 12.5 |  | 2948 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 356 | 381 | 525 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2502.4 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.26806 | 0.31108 | 0.46453 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.09931 | 0.11511 | 0.17105 | 1.3 | 7.9 | 8.8 | 12.5 |  | 3128 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3356.8 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.66303 | 0.75886 | 1.4219 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345.378 | 369.8235 | 509.8105 | 1 | 1 | 1 | 389 | 416 | 574 | 167 | 179 | 247 | 0.16762 | 0.19199 | 0.36058 | 2.5 | 7.9 | 8.8 | 12.5 |  | 4196 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 389 | 416 | 574 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1507.5 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.17144 | 0.19959 | 0.30349 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.088635 | 0.10367 | 0.15727 | 0.6 | 8.9 | 9.9 | 14.8 |  | 1675 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.52065 | 0.60414 | 0.92176 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 338.675 | 366.575 | 456.475 | 1 | 1 | 1 | 381 | 413 | 514 | 164 | 178 | 221 | 0.2385 | 0.27875 | 0.42106 | 1.3 | 8.9 | 9.9 | 14.8 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 381 | 413 | 514 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1935.2 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.23277 | 0.26649 | 0.50941 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.11574 | 0.13165 | 0.25047 | 1 | 8.7 | 9.8 | 14.3 |  | 2419 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2186.88 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.4141 | 1.6213 | 3.1042 | 0.0002083 | 1.724 | 4 | 0.0013928 | 384.4 | 412.3 | 573.5 | 1 | 1 | 1 | 433 | 464 | 646 | 186 | 200 | 278 | 0.52604 | 0.60697 | 1.1625 | 1.9 | 8.7 | 9.8 | 14.3 |  | 3216 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 433 | 464 | 646 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2730.4 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.35014 | 0.40661 | 0.626 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.14096 | 0.16448 | 0.25376 | 1.3 | 8.7 | 9.8 | 14.3 |  | 3413 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3663.2 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.90551 | 1.0359 | 1.9855 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 419.7096 | 449.4497 | 625.2855 | 1 | 1 | 1 | 473 | 506 | 704 | 203 | 218 | 303 | 0.24557 | 0.28234 | 0.5382 | 2.5 | 8.7 | 9.8 | 14.3 |  | 4579 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 473 | 506 | 704 |  | 0 | 0 | 0 | 1
29510 |  |  | 2 | 95 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1758.6 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.23609 | 0.27555 | 0.42826 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.12136 | 0.14204 | 0.22154 | 0.6 | 10.1 | 11.2 | 17.5 |  | 1954 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
29511 |  |  | 2 | 95 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.71218 | 0.82876 | 1.2971 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 399.125 | 432.45 | 545.6 | 1 | 1 | 1 | 449 | 487 | 614 | 193 | 209 | 264 | 0.3252 | 0.37852 | 0.59123 | 1.3 | 10.1 | 11.2 | 17.5 |  | 2461 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 449 | 487 | 614 |  | 0 | 0 | 0 | 1
29515 |  |  | 2 | 95 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2257.6 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.32511 | 0.3701 | 0.72279 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.16101 | 0.18349 | 0.35657 | 1 | 9.6 | 10.5 | 16.1 |  | 2822 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
29516 |  |  | 2 | 95 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2551.36 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.9797 | 2.269 | 4.4296 | 0.0002083 | 1.724 | 4 | 0.0013928 | 456.475 | 488.25 | 685.875 | 1 | 1 | 1 | 514 | 550 | 772 | 221 | 237 | 332 | 0.7391 | 0.8484 | 1.6506 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3752 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 514 | 550 | 772 |  | 0 | 0 | 0 | 1
29520 |  |  | 2 | 95 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3185.6 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.48099 | 0.56453 | 0.89199 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.19506 | 0.22821 | 0.36206 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3982 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
29521 |  |  | 2 | 95 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4273.6 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.2687 | 1.4501 | 2.8201 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 497.7249 | 533.0285 | 747.8905 | 1 | 1 | 1 | 561 | 600 | 842 | 241 | 258 | 362 | 0.34362 | 0.39271 | 0.76299 | 2.5 | 9.6 | 10.5 | 16.1 |  | 5342 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 561 | 600 | 842 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 295.2 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.01394 | 0.016306 | 0.02216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0069533 | 0.0079513 | 0.011345 | 0.1 | 3.6 | 4.1 | 5.1 |  | 328 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 353.7 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.023911 | 0.026978 | 0.038029 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.011759 | 0.01394 | 0.018856 | 0.1 | 4.8 | 5.4 | 6.8 |  | 393 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 523.2 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.038024 | 0.043193 | 0.076311 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.19241 | 0.021258 | 0.037195 | 0.2 | 4.8 | 5.5 | 7.2 |  | 654 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 735.2 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.060116 | 0.069942 | 0.097754 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.023886 | 0.027597 | 0.038802 | 0.3 | 4.8 | 5.5 | 7.2 |  | 919 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 413.1 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.035814 | 0.041087 | 0.05814 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.017814 | 0.020475 | 0.029564 | 0.1 | 5.5 | 5.9 | 7.9 |  | 459 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 610.4 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.046821 | 0.054517 | 0.095052 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.019427 | 0.022524 | 0.039711 | 0.2 | 5.1 | 5.6 | 7.2 |  | 763 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 857.6 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.076193 | 0.087207 | 0.1247 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.025708 | 0.029553 | 0.0419 | 0.3 | 5.1 | 5.6 | 7.2 |  | 1072 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 471.6 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.049245 | 0.056302 | 0.082487 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.025116 | 0.028906 | 0.041869 | 0.1 | 6.3 | 6.8 | 9.1 |  | 524 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 697.6 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.079895 | 0.092435 | 0.16533 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.038863 | 0.044989 | 0.081108 | 0.2 | 6 | 6.7 | 9 |  | 872 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.12607 | 0.14449 | 0.21079 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.050166 | 0.05824 | 0.084945 | 0.3 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 531 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.064804 | 0.074948 | 0.11107 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.032962 | 0.038029 | 0.056302 | 0.1 | 6.7 | 7.4 | 10.3 |  | 590 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 784.8 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.1045 | 0.12025 | 0.22357 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.051562 | 0.058583 | 0.10869 | 0.2 | 7 | 7.7 | 10.7 |  | 981 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1103.2 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.16573 | 0.19178 | 0.28544 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.066916 | 0.077261 | 0.11405 | 0.3 | 7 | 7.7 | 10.7 |  | 1379 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 589.5 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.082487 | 0.09506 | 0.14387 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.041869 | 0.048396 | 0.07286 | 0.1 | 7.8 | 8.7 | 12.2 |  | 655 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 872 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.1324 | 0.15172 | 0.28827 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.064957 | 0.073967 | 0.14029 | 0.2 | 7 | 7.7 | 10.7 |  | 1090 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1225.6 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21079 | 0.24575 | 0.36902 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.084945 | 0.098963 | 0.14892 | 0.3 | 7 | 7.7 | 10.7 |  | 1532 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 648.9 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.10352 | 0.1202 | 0.18091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.052715 | 0.060952 | 0.091543 | 0.1 | 8.4 | 9.3 | 14 |  | 721 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 959.2 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15006 | 0.17058 | 0.32614 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.067155 | 0.076311 | 0.14513 | 0.2 | 7.9 | 8.8 | 12.5 |  | 1199 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1348 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24194 | 0.28134 | 0.42231 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.088349 | 0.10263 | 0.15341 | 0.3 | 7.9 | 8.8 | 12.5 |  | 1685 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 707.4 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.12287 | 0.14387 | 0.22216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.061904 | 0.07286 | 0.11235 | 0.1 | 8.9 | 9.9 | 14.8 |  | 786 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1046.4 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.2019 | 0.23172 | 0.44799 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.099047 | 0.11296 | 0.21755 | 0.2 | 8.7 | 9.8 | 14.3 |  | 1308 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1470.4 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.31715 | 0.36902 | 0.57123 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.12607 | 0.14743 | 0.22886 | 0.3 | 8.7 | 9.8 | 14.3 |  | 1838 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 825.3 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.17125 | 0.20101 | 0.31734 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.085827 | 0.10107 | 0.16032 | 0.1 | 10.1 | 11.2 | 17.5 |  | 917 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1220.8 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.2837 | 0.3237 | 0.6393 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.13869 | 0.15845 | 0.31166 | 0.2 | 9.6 | 10.5 | 16.1 |  | 1526 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1716 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.43747 | 0.51448 | 0.8174 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.17527 | 0.20552 | 0.3281 | 0.3 | 9.6 | 10.5 | 16.1 |  | 2145 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 943.2 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.22397 | 0.26566 | 0.42939 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.11364 | 0.13387 | 0.21677 | 0.1 | 11 | 12.4 | 19.2 |  | 1048 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1395.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.37413 | 0.42541 | 0.86451 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.18316 | 0.2077 | 0.42263 | 0.2 | 11.5 | 12.8 | 19.6 |  | 1744 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1960.8 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.57707 | 0.68085 | 1.1075 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.2307 | 0.27121 | 0.44258 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2451 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1061.1 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.29196 | 0.34377 | 0.5583 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.14827 | 0.17284 | 0.2817 | 0.1 | 12.2 | 13.7 | 22 |  | 1179 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1569.6 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.4282 | 0.4889 | 0.99194 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19054 | 0.21755 | 0.43945 | 0.2 | 11.5 | 12.8 | 19.6 |  | 1962 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2206.4 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.67451 | 0.7932 | 1.2887 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24194 | 0.28338 | 0.46332 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2758 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1179 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.35281 | 0.41693 | 0.70406 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.17766 | 0.21145 | 0.35509 | 0.1 | 13.4 | 14.8 | 24 |  | 1310 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1744 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.61563 | 0.68093 | 1.4216 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.29985 | 0.33349 | 0.69509 | 0.2 | 13.2 | 14.7 | 23.5 |  | 2180 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2451.2 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.90678 | 1.0753 | 1.8196 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.36204 | 0.42986 | 0.72608 | 0.3 | 13.2 | 14.7 | 23.5 |  | 3064 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1296.9 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.41941 | 0.49982 | 0.87023 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.21145 | 0.25201 | 0.43695 | 0.1 | 13.4 | 14.8 | 24 |  | 1441 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1918.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.75693 | 0.82139 | 1.749 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.36892 | 0.40071 | 0.85659 | 0.2 | 15.5 | 16.8 | 27.5 |  | 2398 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2696 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.0793 | 1.2887 | 2.2415 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.43239 | 0.51448 | 0.89581 | 0.3 | 15.5 | 16.8 | 27.5 |  | 3370 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1414.8 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.49442 | 0.59021 | 1.05 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.24818 | 0.29821 | 0.52727 | 0.1 | 14.8 | 16.6 | 28 |  | 1572 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2092.8 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.91688 | 0.98345 | 2.1103 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.44799 | 0.47998 | 1.0306 | 0.2 | 16.4 | 17.7 | 29.7 |  | 2616 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2941.6 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.2712 | 1.5213 | 2.7074 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.50897 | 0.60971 | 1.0833 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3677 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1532.7 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.5756 | 0.70085 | 1.2466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.2899 | 0.35281 | 0.62604 | 0.1 | 16.2 | 18.6 | 31.4 |  | 1703 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2267.2 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.3168 | 1.5999 | 2.8401 | 0.0002083 | 1.724 | 2 | 0.00046183 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 0.96659 | 1.1739 | 2.0855 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2834 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3186.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.3821 | 1.682 | 2.9867 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.51448 | 0.62484 | 1.1116 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3983 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
32010 |  |  | 3 | 20 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1650.6 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.61999 | 0.75639 | 1.338 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.3003 | 0.36428 | 0.64435 | 0.1 | 16.2 | 18.6 | 31.4 |  | 1834 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
32015 |  |  | 3 | 20 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2441.6 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.2779 | 1.3315 | 2.9416 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.62235 | 0.65303 | 1.4369 | 0.2 | 19.3 | 20.4 | 34.5 |  | 3052 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
32020 |  |  | 3 | 20 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3432 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7425 | 2.1221 | 3.7634 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.69684 | 0.84904 | 1.507 | 0.3 | 19.3 | 20.4 | 34.5 |  | 4290 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 371.7 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.014912 | 0.01742 | 0.023616 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0074833 | 0.0085472 | 0.012157 | 0.2 | 3.6 | 4.1 | 5.1 |  | 413 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 381.48 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.043947 | 0.050421 | 0.068526 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 1 | 1 | 1 | 166 | 178 | 208 | 71 | 77 | 89 | 0.032318 | 0.037912 | 0.050421 | 0.4 | 3.6 | 4.1 | 5.1 |  | 561 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 208 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 446.4 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.025468 | 0.028707 | 0.040361 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.012597 | 0.014912 | 0.020121 | 0.2 | 4.8 | 5.4 | 6.8 |  | 496 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 457.64 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.073816 | 0.08498 | 0.11798 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 1 | 1 | 1 | 215 | 231 | 273 | 92 | 99 | 117 | 0.053823 | 0.062186 | 0.08643 | 0.4 | 4.8 | 5.4 | 6.8 |  | 673 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 215 | 231 | 273 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 652 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.038998 | 0.04428 | 0.078087 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.19636 | 0.021847 | 0.03815 | 0.3 | 4.8 | 5.5 | 7.2 |  | 815 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 603.84 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.24359 | 0.28177 | 0.49304 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 1 | 1 | 1 | 241 | 259 | 343 | 104 | 111 | 147 | 0.15146 | 0.17245 | 0.30189 | 0.6 | 4.8 | 5.5 | 7.2 |  | 888 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 241 | 259 | 343 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 915.2 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.061165 | 0.071136 | 0.099349 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.024359 | 0.028133 | 0.039521 | 0.4 | 4.8 | 5.5 | 7.2 |  | 1144 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 935.2 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.15281 | 0.17489 | 0.30756 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 1 | 1 | 1 | 263 | 283 | 374 | 113 | 122 | 161 | 0.067021 | 0.078056 | 0.13554 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1169 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 263 | 283 | 374 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 520.2 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.038026 | 0.043581 | 0.061515 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.019018 | 0.021834 | 0.031436 | 0.2 | 5.5 | 5.9 | 7.9 |  | 578 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 533.8 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.10964 | 0.12662 | 0.1806 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.082116 | 0.093862 | 0.13195 | 0.4 | 5.5 | 5.9 | 7.9 |  | 785 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 760.8 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.047987 | 0.055845 | 0.0972 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.019972 | 0.023143 | 0.040721 | 0.3 | 5.1 | 5.6 | 7.2 |  | 951 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 704.48 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.33123 | 0.38008 | 0.66844 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.15732 | 0.18187 | 0.31849 | 0.6 | 5.1 | 5.6 | 7.2 |  | 1036 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1067.2 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.07748 | 0.088652 | 0.12667 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.026212 | 0.030122 | 0.042668 | 0.4 | 5.1 | 5.6 | 7.2 |  | 1334 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.18258 | 0.2108 | 0.36824 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.071822 | 0.081921 | 0.14405 | 0.8 | 5.1 | 5.6 | 7.2 |  | 1364 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 594.9 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.052166 | 0.059584 | 0.087063 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.02674 | 0.030742 | 0.044405 | 0.2 | 6.3 | 6.8 | 9.1 |  | 661 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 609.96 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.15243 | 0.17643 | 0.25385 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.11294 | 0.12838 | 0.18694 | 0.4 | 6.3 | 6.8 | 9.1 |  | 897 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 869.6 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.081743 | 0.094531 | 0.16879 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.039855 | 0.046115 | 0.08298 | 0.3 | 6 | 6.7 | 9 |  | 1087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 805.12 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.51953 | 0.59739 | 1.0757 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.31849 | 0.36642 | 0.66237 | 0.6 | 6 | 6.7 | 9 |  | 1184 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1220 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.12805 | 0.14672 | 0.21389 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.051063 | 0.05926 | 0.086358 | 0.4 | 6 | 6.7 | 9 |  | 1525 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1246.4 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.32286 | 0.371 | 0.66533 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14233 | 0.16367 | 0.29262 | 0.8 | 6 | 6.7 | 9 |  | 1558 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 668.7 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.068513 | 0.079158 | 0.117 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.035021 | 0.040361 | 0.059584 | 0.2 | 6.7 | 7.4 | 10.3 |  | 743 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 686.12 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.19996 | 0.23201 | 0.34228 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.14859 | 0.17027 | 0.25138 | 0.4 | 6.7 | 7.4 | 10.3 |  | 1009 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 978.4 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.10683 | 0.12288 | 0.22806 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.052829 | 0.059997 | 0.1111 | 0.3 | 7 | 7.7 | 10.7 |  | 1223 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 905.76 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.68067 | 0.78249 | 1.451 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.41771 | 0.48263 | 0.89139 | 0.6 | 7 | 7.7 | 10.7 |  | 1332 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1372 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.16824 | 0.19463 | 0.28946 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.068066 | 0.078563 | 0.11587 | 0.4 | 7 | 7.7 | 10.7 |  | 1715 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1402.4 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.42247 | 0.48356 | 0.8973 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.18649 | 0.215 | 0.39632 | 0.8 | 7 | 7.7 | 10.7 |  | 1753 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 743.4 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.087063 | 0.10024 | 0.1513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.044405 | 0.051273 | 0.076968 | 0.2 | 7.8 | 8.7 | 12.2 |  | 826 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 762.28 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.25385 | 0.2951 | 0.44049 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.18694 | 0.21798 | 0.32523 | 0.4 | 7.8 | 8.7 | 12.2 |  | 1121 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1087.2 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.13526 | 0.15493 | 0.29387 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.066503 | 0.075697 | 0.1433 | 0.3 | 7 | 7.7 | 10.7 |  | 1359 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1006.4 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.8635 | 0.99248 | 1.8822 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.53032 | 0.60896 | 1.1543 | 0.6 | 7 | 7.7 | 10.7 |  | 1480 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1524.8 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21389 | 0.24928 | 0.37404 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.086358 | 0.10057 | 0.15121 | 0.4 | 7 | 7.7 | 10.7 |  | 1906 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1558.4 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.53539 | 0.61096 | 1.1589 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.23659 | 0.27092 | 0.51239 | 0.8 | 7 | 7.7 | 10.7 |  | 1948 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 818.1 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.1091 | 0.12655 | 0.18997 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.055814 | 0.064468 | 0.096554 | 0.2 | 8.4 | 9.3 | 14 |  | 909 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 838.44 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.31964 | 0.36866 | 0.5546 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.23439 | 0.27152 | 0.40848 | 0.4 | 8.4 | 9.3 | 14 |  | 1233 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1196 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15324 | 0.17414 | 0.33236 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.068746 | 0.078087 | 0.14823 | 0.3 | 7.9 | 8.8 | 12.5 |  | 1495 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1107.04 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0148 | 1.1623 | 2.2008 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.54122 | 0.62651 | 1.1865 | 0.6 | 7.9 | 8.8 | 12.5 |  | 1628 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1677.6 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24543 | 0.2853 | 0.42794 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.089811 | 0.1043 | 0.15576 | 0.4 | 7.9 | 8.8 | 12.5 |  | 2097 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1714.4 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.58986 | 0.67648 | 1.279 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.24327 | 0.27806 | 0.52877 | 0.8 | 7.9 | 8.8 | 12.5 |  | 2143 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 891.9 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.12935 | 0.1513 | 0.23301 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.065468 | 0.076968 | 0.11834 | 0.2 | 8.9 | 9.9 | 14.8 |  | 991 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 914.6 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.37767 | 0.44049 | 0.6817 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.27927 | 0.32523 | 0.50112 | 0.4 | 8.9 | 9.9 | 14.8 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1304.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.20601 | 0.23636 | 0.45618 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10127 | 0.11545 | 0.22194 | 0.3 | 8.7 | 9.8 | 14.3 |  | 1631 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1207.68 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3112 | 1.5053 | 2.8997 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.80237 | 0.92687 | 1.7816 | 0.6 | 8.7 | 9.8 | 14.3 |  | 1776 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1829.6 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.32155 | 0.37404 | 0.57853 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.12805 | 0.1497 | 0.23218 | 0.4 | 8.7 | 9.8 | 14.3 |  | 2287 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1870.4 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.80932 | 0.92763 | 1.7941 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.35729 | 0.41074 | 0.79308 | 0.8 | 8.7 | 9.8 | 14.3 |  | 2338 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1040.4 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.1799 | 0.21095 | 0.33213 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.090565 | 0.10653 | 0.16848 | 0.2 | 10.1 | 11.2 | 17.5 |  | 1156 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1066.92 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.52219 | 0.61076 | 0.97 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.38374 | 0.45033 | 0.71447 | 0.4 | 10.1 | 11.2 | 17.5 |  | 1569 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1522.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.28922 | 0.32989 | 0.65043 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14167 | 0.16179 | 0.31765 | 0.3 | 9.6 | 10.5 | 16.1 |  | 1903 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1408.96 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8416 | 2.1134 | 4.1509 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1304 | 1.2942 | 2.556 | 0.6 | 9.6 | 10.5 | 16.1 |  | 2072 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2134.4 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.44327 | 0.52116 | 0.82734 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.17791 | 0.20854 | 0.33263 | 0.4 | 9.6 | 10.5 | 16.1 |  | 2668 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2181.6 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1394 | 1.3048 | 2.5599 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.50269 | 0.57599 | 1.1298 | 0.8 | 9.6 | 10.5 | 16.1 |  | 2727 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1189.8 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.23489 | 0.27833 | 0.44863 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.11969 | 0.14084 | 0.22739 | 0.2 | 11 | 12.4 | 19.2 |  | 1322 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1219.92 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.68575 | 0.80851 | 1.3085 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.50809 | 0.59552 | 0.96038 | 0.4 | 11 | 12.4 | 19.2 |  | 1794 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1739.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.38114 | 0.43324 | 0.87895 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.18694 | 0.21192 | 0.43042 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2174 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1610.24 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.427 | 2.7745 | 5.6079 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.4871 | 1.703 | 3.4558 | 0.6 | 11.5 | 12.8 | 19.6 |  | 2368 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2440 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.58444 | 0.68935 | 1.1204 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.23405 | 0.27505 | 0.44844 | 0.4 | 11.5 | 12.8 | 19.6 |  | 3050 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2493.6 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.5034 | 1.7101 | 3.4695 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.66163 | 0.75319 | 1.5313 | 0.8 | 11.5 | 12.8 | 19.6 |  | 3117 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1338.3 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.30572 | 0.35963 | 0.58248 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.1559 | 0.18156 | 0.29503 | 0.2 | 12.2 | 13.7 | 22 |  | 1487 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1372.24 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.89437 | 1.0487 | 1.6972 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.65762 | 0.77365 | 1.2532 | 0.4 | 12.2 | 13.7 | 22 |  | 2018 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1956.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.43608 | 0.49773 | 1.0082 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19446 | 0.22194 | 0.44751 | 0.3 | 11.5 | 12.8 | 19.6 |  | 2446 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1811.52 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.9251 | 3.3326 | 6.7519 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.5328 | 1.7519 | 3.5532 | 0.6 | 11.5 | 12.8 | 19.6 |  | 2664 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2744.8 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.68294 | 0.80289 | 1.3034 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24543 | 0.28738 | 0.46942 | 0.4 | 11.5 | 12.8 | 19.6 |  | 3431 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2804.8 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.6748 | 1.9113 | 3.8773 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.68397 | 0.781 | 1.5822 | 0.8 | 11.5 | 12.8 | 19.6 |  | 3506 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1486.8 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.36903 | 0.43568 | 0.73365 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.18658 | 0.22184 | 0.3714 | 0.2 | 13.4 | 14.8 | 24 |  | 1652 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1524.56 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.0739 | 1.2697 | 2.143 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.79098 | 0.93653 | 1.5723 | 0.4 | 13.4 | 14.8 | 24 |  | 2242 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2174.4 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.6264 | 0.69268 | 1.4438 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.30564 | 0.33984 | 0.70706 | 0.3 | 13.2 | 14.7 | 23.5 |  | 2718 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2012.8 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 3.986 | 4.428 | 9.2218 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.4618 | 2.7129 | 5.6608 | 0.6 | 13.2 | 14.7 | 23.5 |  | 2960 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3049.6 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.91765 | 1.0879 | 1.8394 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.36697 | 0.43557 | 0.73506 | 0.4 | 13.2 | 14.7 | 23.5 |  | 3812 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3116.8 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.4666 | 2.7368 | 5.6908 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.0868 | 1.2082 | 2.5095 | 0.8 | 13.2 | 14.7 | 23.5 |  | 3896 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1635.3 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.43826 | 0.52179 | 0.90581 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.22184 | 0.26411 | 0.45649 | 0.2 | 13.4 | 14.8 | 24 |  | 1817 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1676.88 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.2752 | 1.5236 | 2.6324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 0.94128 | 1.12 | 1.9407 | 0.4 | 13.4 | 14.8 | 24 |  | 2466 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2392 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.76981 | 0.83521 | 1.7756 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.37585 | 0.40815 | 0.87092 | 0.3 | 15.5 | 16.8 | 27.5 |  | 2990 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2214.08 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 4.926 | 5.3298 | 11.3386 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.0277 | 3.2785 | 6.9659 | 0.6 | 15.5 | 16.8 | 27.5 |  | 3256 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3354.4 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.092 | 1.3034 | 2.2652 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.43813 | 0.52116 | 0.90657 | 0.4 | 15.5 | 16.8 | 27.5 |  | 4193 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3428.8 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.0369 | 3.2947 | 6.9999 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3413 | 1.4538 | 3.0924 | 0.8 | 15.5 | 16.8 | 27.5 |  | 4286 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1783.8 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.51618 | 0.61559 | 1.0919 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.26012 | 0.31222 | 0.55027 | 0.2 | 14.8 | 16.6 | 28 |  | 1982 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1829.2 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.4996 | 1.794 | 3.1717 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.1045 | 1.3197 | 2.3328 | 0.4 | 14.8 | 16.6 | 28 |  | 2690 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2609.6 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.93208 | 0.9996 | 2.1415 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.45618 | 0.48867 | 1.0474 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3262 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2415.36 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 5.9472 | 6.39 | 13.7009 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.652 | 3.9269 | 8.4276 | 0.6 | 16.4 | 17.7 | 29.7 |  | 3552 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3659.2 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.2858 | 1.5382 | 2.7353 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.51558 | 0.61743 | 1.096 | 0.4 | 16.4 | 17.7 | 29.7 |  | 4574 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3740 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.6662 | 3.9399 | 8.4441 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6166 | 1.7399 | 3.7359 | 0.8 | 16.4 | 17.7 | 29.7 |  | 4675 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1933.2 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.60043 | 0.73032 | 1.2953 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.30357 | 0.36903 | 0.65275 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2148 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1982.2 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.7549 | 2.1287 | 3.7608 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.2918 | 1.5661 | 2.7686 | 0.4 | 16.2 | 18.6 | 31.4 |  | 2915 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2826.4 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0168 | 1.0918 | 2.3405 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.46493 | 0.50077 | 1.0739 | 0.3 | 16.4 | 17.7 | 29.7 |  | 3533 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2616.64 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.6941 | 7.1833 | 15.4289 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.7234 | 4.0009 | 8.5575 | 0.6 | 16.4 | 17.7 | 29.7 |  | 3848 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3964.8 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.3977 | 1.7006 | 3.017 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.52116 | 0.63273 | 1.1245 | 0.4 | 16.4 | 17.7 | 29.7 |  | 4956 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4052 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 3.9399 | 4.2327 | 9.0869 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.6514 | 1.776 | 3.8063 | 0.8 | 16.4 | 17.7 | 29.7 |  | 5065 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2081.7 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.64648 | 0.78788 | 1.3897 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.3144 | 0.38096 | 0.67174 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2313 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2134.52 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 1.9476 | 2.3702 | 4.1779 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.3085 | 1.5907 | 2.8093 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3139 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3044 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.2981 | 1.3525 | 2.9832 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.63322 | 0.66437 | 1.4593 | 0.3 | 19.3 | 20.4 | 34.5 |  | 3805 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 2817.92 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.2773 | 8.6447 | 19.0622 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.0756 | 5.3127 | 11.7168 | 0.6 | 19.3 | 20.4 | 34.5 |  | 4144 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4269.6 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7616 | 2.1447 | 3.8005 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.7055 | 0.85932 | 1.5239 | 0.4 | 19.3 | 20.4 | 34.5 |  | 5337 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4363.2 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.1022 | 5.3401 | 11.7531 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 1.9302 | 2.0193 | 4.4401 | 0.8 | 19.3 | 20.4 | 34.5 |  | 5454 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
33010 |  |  | 3 | 30 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2230.2 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.69423 | 0.84404 | 1.4874 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.32099 | 0.39308 | 0.69423 | 0.2 | 16.2 | 18.6 | 31.4 |  | 2478 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
33011 |  |  | 3 | 30 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2286.84 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.1501 | 2.6166 | 4.6168 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 1 | 1 | 1 | 1085 | 1197 | 1595 | 467 | 515 | 686 | 1.331 | 1.6154 | 2.8504 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3363 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1085 | 1197 | 1595 |  | 0 | 0 | 0 | 1
33015 |  |  | 3 | 30 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3261.6 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.3978 | 1.4593 | 3.2172 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.64697 | 0.67492 | 1.4906 | 0.3 | 19.3 | 20.4 | 34.5 |  | 4077 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
33016 |  |  | 3 | 30 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3019.2 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.1543 | 9.5633 | 21.1249 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 1 | 1 | 1 | 1419 | 1451 | 2157 | 610 | 624 | 928 | 5.1597 | 5.3987 | 11.921 | 0.6 | 19.3 | 20.4 | 34.5 |  | 4440 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1419 | 1451 | 2157 |  | 0 | 0 | 0 | 1
33020 |  |  | 3 | 30 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4574.4 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 1.9189 | 2.3356 | 4.1391 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.72185 | 0.88097 | 1.5623 | 0.4 | 19.3 | 20.4 | 34.5 |  | 5718 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
33021 |  |  | 3 | 30 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4675.2 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.4346 | 5.6692 | 12.5091 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 1 | 1 | 1 | 1653 | 1690 | 2513 | 711 | 727 | 1081 | 2.6109 | 2.7293 | 6.0193 | 0.8 | 19.3 | 20.4 | 34.5 |  | 5844 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1653 | 1690 | 2513 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.015885 | 0.018535 | 0.025072 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0080134 | 0.009143 | 0.01297 | 0.3 | 3.6 | 4.1 | 5.1 |  | 482 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 429.76 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.047264 | 0.054165 | 0.073432 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 1 | 1 | 1 | 166 | 178 | 208 | 71 | 77 | 89 | 0.034848 | 0.040825 | 0.054165 | 0.5 | 3.6 | 4.1 | 5.1 |  | 632 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 208 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.027024 | 0.030435 | 0.042692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.013435 | 0.015885 | 0.021386 | 0.3 | 4.8 | 5.4 | 6.8 |  | 578 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 515.44 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.079054 | 0.090909 | 0.12589 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 1 | 1 | 1 | 215 | 231 | 273 | 92 | 99 | 117 | 0.057789 | 0.06669 | 0.092448 | 0.5 | 4.8 | 5.4 | 6.8 |  | 758 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 215 | 231 | 273 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 752.8 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.039971 | 0.045367 | 0.079864 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.20031 | 0.022436 | 0.039105 | 0.4 | 4.8 | 5.5 | 7.2 |  | 941 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 693.6 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.24729 | 0.28596 | 0.49984 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 1 | 1 | 1 | 241 | 259 | 343 | 104 | 111 | 147 | 0.15391 | 0.17519 | 0.30634 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1020 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 241 | 259 | 343 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1054.4 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.062213 | 0.072331 | 0.10094 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.024832 | 0.028669 | 0.04024 | 0.5 | 4.8 | 5.5 | 7.2 |  | 1318 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.15631 | 0.17883 | 0.31397 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 1 | 1 | 1 | 263 | 283 | 374 | 113 | 122 | 161 | 0.068736 | 0.080013 | 0.1387 | 1.1 | 4.8 | 5.5 | 7.2 |  | 1364 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 263 | 283 | 374 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 606.6 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.040239 | 0.046075 | 0.064889 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.020222 | 0.023193 | 0.033308 | 0.3 | 5.5 | 5.9 | 7.9 |  | 674 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 601.8 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.11705 | 0.13504 | 0.1921 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.087869 | 0.10033 | 0.14068 | 0.5 | 5.5 | 5.9 | 7.9 |  | 885 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 878.4 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.049152 | 0.057174 | 0.099348 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.020517 | 0.023762 | 0.041732 | 0.4 | 5.1 | 5.6 | 7.2 |  | 1098 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 809.2 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.33605 | 0.38551 | 0.67729 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.15985 | 0.18474 | 0.32315 | 0.8 | 5.1 | 5.6 | 7.2 |  | 1190 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1229.6 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.078766 | 0.090097 | 0.12864 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.026716 | 0.03069 | 0.043436 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1537 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1273.6 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.18667 | 0.21542 | 0.37573 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.073643 | 0.083962 | 0.14737 | 1.1 | 5.1 | 5.6 | 7.2 |  | 1592 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.055086 | 0.062865 | 0.09164 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.028364 | 0.032578 | 0.04694 | 0.3 | 6.3 | 6.8 | 9.1 |  | 770 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 687.48 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.16234 | 0.1877 | 0.26937 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.12055 | 0.13691 | 0.1988 | 0.5 | 6.3 | 6.8 | 9.1 |  | 1011 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1003.2 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.083592 | 0.096628 | 0.17225 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.040847 | 0.04724 | 0.084853 | 0.4 | 6 | 6.7 | 9 |  | 1254 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 924.8 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.52665 | 0.60542 | 1.0891 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32315 | 0.37169 | 0.67115 | 0.8 | 6 | 6.7 | 9 |  | 1360 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1405.6 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13004 | 0.14895 | 0.21698 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.05196 | 0.060281 | 0.08777 | 0.5 | 6 | 6.7 | 9 |  | 1757 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1455.2 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.32955 | 0.37854 | 0.67782 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14562 | 0.16738 | 0.29877 | 1.1 | 6 | 6.7 | 9 |  | 1819 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 780.3 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.072222 | 0.083368 | 0.12293 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.037079 | 0.042692 | 0.062865 | 0.3 | 6.7 | 7.4 | 10.3 |  | 867 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 773.84 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.21254 | 0.24634 | 0.36246 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.15829 | 0.18119 | 0.26676 | 0.5 | 6.7 | 7.4 | 10.3 |  | 1138 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1128.8 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.10916 | 0.12551 | 0.23256 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.054095 | 0.061411 | 0.11351 | 0.4 | 7 | 7.7 | 10.7 |  | 1411 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1040.4 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.68966 | 0.79263 | 1.4683 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.4236 | 0.48931 | 0.90274 | 0.8 | 7 | 7.7 | 10.7 |  | 1530 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1580.8 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17075 | 0.19748 | 0.29347 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.069216 | 0.079865 | 0.11769 | 0.5 | 7 | 7.7 | 10.7 |  | 1976 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1637.6 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.4309 | 0.49304 | 0.91348 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.19065 | 0.2197 | 0.4043 | 1.1 | 7 | 7.7 | 10.7 |  | 2047 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 866.7 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.09164 | 0.10542 | 0.15873 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.04694 | 0.054149 | 0.081076 | 0.3 | 7.8 | 8.7 | 12.2 |  | 963 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 859.52 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.26937 | 0.31281 | 0.46567 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.1988 | 0.23156 | 0.34452 | 0.5 | 7.8 | 8.7 | 12.2 |  | 1264 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1254.4 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.13812 | 0.15815 | 0.29947 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.068049 | 0.077426 | 0.1463 | 0.4 | 7 | 7.7 | 10.7 |  | 1568 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1156 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.87454 | 1.0049 | 1.9039 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.53756 | 0.61712 | 1.1685 | 0.8 | 7 | 7.7 | 10.7 |  | 1700 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1756.8 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.21698 | 0.25281 | 0.37905 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.08777 | 0.10219 | 0.1535 | 0.5 | 7 | 7.7 | 10.7 |  | 2196 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1819.2 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.54575 | 0.62256 | 1.1791 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.2417 | 0.27666 | 0.52236 | 1.1 | 7 | 7.7 | 10.7 |  | 2274 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 953.1 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.11468 | 0.1329 | 0.19904 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.058912 | 0.067985 | 0.10157 | 0.3 | 8.4 | 9.3 | 14 |  | 1059 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 945.2 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.33864 | 0.3902 | 0.58541 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.24885 | 0.28798 | 0.43205 | 0.5 | 8.4 | 9.3 | 14 |  | 1390 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1380 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15643 | 0.1777 | 0.33859 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.070337 | 0.079864 | 0.15132 | 0.4 | 7.9 | 8.8 | 12.5 |  | 1725 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1271.6 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0275 | 1.1766 | 2.2256 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.54859 | 0.63488 | 1.201 | 0.8 | 7.9 | 8.8 | 12.5 |  | 1870 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1932.8 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.24891 | 0.28927 | 0.43357 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.091272 | 0.10596 | 0.15811 | 0.5 | 7.9 | 8.8 | 12.5 |  | 2416 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2000.8 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.60111 | 0.68915 | 1.301 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.24851 | 0.28394 | 0.53901 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2501 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1040.4 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.13582 | 0.15873 | 0.24385 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.069032 | 0.081076 | 0.12433 | 0.3 | 8.9 | 9.9 | 14.8 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1031.56 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.39967 | 0.46567 | 0.71863 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.29614 | 0.34452 | 0.52931 | 0.5 | 8.9 | 9.9 | 14.8 |  | 1517 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1505.6 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.21013 | 0.24099 | 0.46437 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.1035 | 0.11794 | 0.22633 | 0.4 | 8.7 | 9.8 | 14.3 |  | 1882 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1387.2 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.327 | 1.5231 | 2.9312 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.81273 | 0.93861 | 1.8022 | 0.8 | 8.7 | 9.8 | 14.3 |  | 2040 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2108 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.32595 | 0.37905 | 0.58584 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13004 | 0.15198 | 0.2355 | 0.5 | 8.7 | 9.8 | 14.3 |  | 2635 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2183.2 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.82412 | 0.94428 | 1.8236 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.36459 | 0.41897 | 0.80762 | 1.1 | 8.7 | 9.8 | 14.3 |  | 2729 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1213.2 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.18854 | 0.22088 | 0.34692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.095303 | 0.11199 | 0.17665 | 0.3 | 10.1 | 11.2 | 17.5 |  | 1348 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1203.6 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.55142 | 0.6443 | 1.0203 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.40605 | 0.476 | 0.75295 | 0.5 | 10.1 | 11.2 | 17.5 |  | 1770 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1756 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.29474 | 0.33607 | 0.66157 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14465 | 0.16513 | 0.32364 | 0.4 | 9.6 | 10.5 | 16.1 |  | 2195 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1618.4 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8629 | 2.1373 | 4.1938 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1443 | 1.3098 | 2.5843 | 0.8 | 9.6 | 10.5 | 16.1 |  | 2380 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2459.2 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.44907 | 0.52783 | 0.83729 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18055 | 0.21157 | 0.33715 | 0.5 | 9.6 | 10.5 | 16.1 |  | 3074 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2547.2 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1593 | 1.3271 | 2.6 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.51249 | 0.58702 | 1.1495 | 1.1 | 9.6 | 10.5 | 16.1 |  | 3184 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1386.9 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.24581 | 0.291 | 0.46787 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.12574 | 0.14782 | 0.238 | 0.3 | 11 | 12.4 | 19.2 |  | 1541 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1374.96 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.72288 | 0.8514 | 1.3739 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.53663 | 0.62832 | 1.0103 | 0.5 | 11 | 12.4 | 19.2 |  | 2022 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.38815 | 0.44107 | 0.8934 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.19072 | 0.21613 | 0.4382 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2509 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1849.6 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4539 | 2.8048 | 5.6635 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.5047 | 1.7229 | 3.4924 | 0.8 | 11.5 | 12.8 | 19.6 |  | 2720 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2811.2 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.5918 | 0.69784 | 1.1334 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.23739 | 0.2789 | 0.4543 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3514 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2910.4 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.5287 | 1.7384 | 3.5216 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.67407 | 0.76709 | 1.557 | 1.1 | 11.5 | 12.8 | 19.6 |  | 3638 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1559.7 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.31947 | 0.37548 | 0.60666 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.16352 | 0.19027 | 0.30837 | 0.3 | 12.2 | 13.7 | 22 |  | 1733 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1547 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.94123 | 1.1025 | 1.7793 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.69341 | 0.81491 | 1.3162 | 0.5 | 12.2 | 13.7 | 22 |  | 2275 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2257.6 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.44395 | 0.50656 | 1.0245 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.19837 | 0.22633 | 0.45556 | 0.4 | 11.5 | 12.8 | 19.6 |  | 2822 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2080.8 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.9568 | 3.368 | 6.8172 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.5509 | 1.7723 | 3.5907 | 0.8 | 11.5 | 12.8 | 19.6 |  | 3060 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3162.4 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.69136 | 0.81258 | 1.3181 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.24891 | 0.29137 | 0.47551 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3953 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3274.4 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7025 | 1.9424 | 3.9346 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.69676 | 0.79535 | 1.6086 | 1.1 | 11.5 | 12.8 | 19.6 |  | 4093 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1733.4 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.38525 | 0.45444 | 0.76323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.19551 | 0.23223 | 0.38771 | 0.3 | 13.4 | 14.8 | 24 |  | 1926 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1719.04 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1289 | 1.3334 | 2.2438 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.83306 | 0.98533 | 1.6491 | 0.5 | 13.4 | 14.8 | 24 |  | 2528 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2508.8 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.63718 | 0.70444 | 1.466 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.31144 | 0.34619 | 0.71903 | 0.4 | 13.2 | 14.7 | 23.5 |  | 3136 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2312 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0274 | 4.4733 | 9.3073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.4891 | 2.7426 | 5.7169 | 0.8 | 13.2 | 14.7 | 23.5 |  | 3400 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3513.6 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.92853 | 1.1005 | 1.8592 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.3719 | 0.44129 | 0.74403 | 0.5 | 13.2 | 14.7 | 23.5 |  | 4392 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3638.4 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.5053 | 2.7792 | 5.7706 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.1059 | 1.2291 | 2.5488 | 1.1 | 13.2 | 14.7 | 23.5 |  | 4548 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1907.1 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.45711 | 0.54375 | 0.94138 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.23223 | 0.27622 | 0.47602 | 0.3 | 13.4 | 14.8 | 24 |  | 2119 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1891.08 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.3391 | 1.5984 | 2.7531 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 0.99029 | 1.1771 | 2.0331 | 0.5 | 13.4 | 14.8 | 24 |  | 2781 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2760 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.78269 | 0.84903 | 1.8021 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.38277 | 0.41558 | 0.88525 | 0.4 | 15.5 | 16.8 | 27.5 |  | 3450 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2543.2 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 4.9758 | 5.3831 | 11.4407 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.0604 | 3.3135 | 7.033 | 0.8 | 15.5 | 16.8 | 27.5 |  | 3740 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3864.8 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1046 | 1.3181 | 2.289 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.44387 | 0.52783 | 0.91733 | 0.5 | 15.5 | 16.8 | 27.5 |  | 4831 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4002.4 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.0833 | 3.3444 | 7.0953 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3642 | 1.4784 | 3.1395 | 1.1 | 15.5 | 16.8 | 27.5 |  | 5003 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2079.9 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.53793 | 0.64097 | 1.1338 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.27206 | 0.32623 | 0.57328 | 0.3 | 14.8 | 16.6 | 28 |  | 2311 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2063.12 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.5733 | 1.8802 | 3.3137 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.1609 | 1.3856 | 2.4413 | 0.5 | 14.8 | 16.6 | 28 |  | 3034 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3010.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.94727 | 1.0157 | 2.1727 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.46437 | 0.49737 | 1.0642 | 0.4 | 16.4 | 17.7 | 29.7 |  | 3763 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2774.4 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.0057 | 6.4523 | 13.8212 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.6904 | 3.9677 | 8.5067 | 0.8 | 16.4 | 17.7 | 29.7 |  | 4080 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4216 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3003 | 1.5552 | 2.7632 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.52219 | 0.62516 | 1.1087 | 0.5 | 16.4 | 17.7 | 29.7 |  | 5270 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4366.4 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.7208 | 3.998 | 8.5563 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6435 | 1.7686 | 3.7914 | 1.1 | 16.4 | 17.7 | 29.7 |  | 5458 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2253.6 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.62526 | 0.75979 | 1.3439 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.31724 | 0.38525 | 0.67947 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2504 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2234.48 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.8395 | 2.2289 | 3.9257 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.3565 | 1.6427 | 2.8947 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3286 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3261.6 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0332 | 1.1092 | 2.3742 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.47325 | 0.50964 | 1.0911 | 0.4 | 16.4 | 17.7 | 29.7 |  | 4077 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3005.6 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.7589 | 7.2522 | 15.5621 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.7624 | 4.0424 | 8.6376 | 0.8 | 16.4 | 17.7 | 29.7 |  | 4420 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4568 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4134 | 1.7191 | 3.0474 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.52783 | 0.64062 | 1.1375 | 0.5 | 16.4 | 17.7 | 29.7 |  | 5710 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4729.6 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 3.998 | 4.2945 | 9.2064 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.6788 | 1.8051 | 3.8627 | 1.1 | 16.4 | 17.7 | 29.7 |  | 5912 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2426.4 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.67297 | 0.81937 | 1.4414 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.3285 | 0.39764 | 0.69913 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2696 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2406.52 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.0402 | 2.4802 | 4.3587 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.3739 | 1.6683 | 2.9371 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3539 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3512 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3184 | 1.3734 | 3.0248 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.6441 | 0.67571 | 1.4817 | 0.4 | 19.3 | 20.4 | 34.5 |  | 4390 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3236.8 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.3552 | 8.7255 | 19.2222 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1266 | 5.3658 | 11.8219 | 0.8 | 19.3 | 20.4 | 34.5 |  | 4760 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4919.2 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7807 | 2.1673 | 3.8375 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.71417 | 0.86959 | 1.5407 | 0.5 | 19.3 | 20.4 | 34.5 |  | 6149 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5093.6 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.1748 | 5.4156 | 11.9024 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 1.9615 | 2.0519 | 4.5045 | 1.1 | 19.3 | 20.4 | 34.5 |  | 6367 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
34010 |  |  | 3 | 40 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2600.1 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.72242 | 0.87748 | 1.5423 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.33535 | 0.41022 | 0.72242 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2889 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
34011 |  |  | 3 | 40 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2578.56 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.2512 | 2.7366 | 4.8141 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 1 | 1 | 1 | 1085 | 1197 | 1595 | 467 | 515 | 686 | 1.3974 | 1.6941 | 2.9797 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3792 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1085 | 1197 | 1595 |  | 0 | 0 | 0 | 1
34015 |  |  | 3 | 40 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3763.2 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.4194 | 1.4817 | 3.2616 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.65805 | 0.68641 | 1.5134 | 0.4 | 19.3 | 20.4 | 34.5 |  | 4704 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
34016 |  |  | 3 | 40 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3468 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.2392 | 9.6515 | 21.2997 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 1 | 1 | 1 | 1419 | 1451 | 2157 | 610 | 624 | 928 | 5.2114 | 5.4525 | 12.0277 | 0.8 | 19.3 | 20.4 | 34.5 |  | 5100 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1419 | 1451 | 2157 |  | 0 | 0 | 0 | 1
34020 |  |  | 3 | 40 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5270.4 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 1.9394 | 2.3599 | 4.179 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.73069 | 0.89147 | 1.5795 | 0.5 | 19.3 | 20.4 | 34.5 |  | 6588 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
34021 |  |  | 3 | 40 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5457.6 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.5113 | 5.7487 | 12.6666 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 1 | 1 | 1 | 1653 | 1690 | 2513 | 711 | 727 | 1081 | 2.6516 | 2.7717 | 6.103 | 1.1 | 19.3 | 20.4 | 34.5 |  | 6822 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1653 | 1690 | 2513 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 484.2 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.016857 | 0.01965 | 0.026529 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0085435 | 0.0097389 | 0.013782 | 0.3 | 3.6 | 4.1 | 5.1 |  | 538 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 471.24 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.050581 | 0.05791 | 0.078337 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 1 | 1 | 1 | 166 | 178 | 208 | 71 | 77 | 89 | 0.037378 | 0.043737 | 0.05791 | 0.7 | 3.6 | 4.1 | 5.1 |  | 693 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 208 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 581.4 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.02858 | 0.032164 | 0.045024 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.014274 | 0.016857 | 0.022651 | 0.3 | 4.8 | 5.4 | 6.8 |  | 646 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 565.76 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.084292 | 0.096838 | 0.1338 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 1 | 1 | 1 | 215 | 231 | 273 | 92 | 99 | 117 | 0.061755 | 0.071194 | 0.098466 | 0.7 | 4.8 | 5.4 | 6.8 |  | 832 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 215 | 231 | 273 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 832 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.040945 | 0.046453 | 0.081641 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.20426 | 0.023025 | 0.04006 | 0.5 | 4.8 | 5.5 | 7.2 |  | 1040 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 774.52 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.25099 | 0.29015 | 0.50664 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 1 | 1 | 1 | 241 | 259 | 343 | 104 | 111 | 147 | 0.15636 | 0.17794 | 0.31079 | 1 | 4.8 | 5.5 | 7.2 |  | 1139 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 241 | 259 | 343 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.063262 | 0.073526 | 0.10254 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.025306 | 0.029205 | 0.040959 | 0.7 | 4.8 | 5.5 | 7.2 |  | 1455 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.15981 | 0.18276 | 0.32038 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 1 | 1 | 1 | 263 | 283 | 374 | 113 | 122 | 161 | 0.070452 | 0.081971 | 0.14185 | 1.3 | 4.8 | 5.5 | 7.2 |  | 1549 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 263 | 283 | 374 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 677.7 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.042452 | 0.048569 | 0.068264 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.021426 | 0.024553 | 0.035181 | 0.3 | 5.5 | 5.9 | 7.9 |  | 753 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 659.6 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.12447 | 0.14346 | 0.20361 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 1 | 1 | 1 | 264 | 283 | 338 | 114 | 122 | 145 | 0.093622 | 0.1068 | 0.14941 | 0.7 | 5.5 | 5.9 | 7.9 |  | 970 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 338 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.050317 | 0.058503 | 0.1015 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.021062 | 0.024382 | 0.042743 | 0.5 | 5.1 | 5.6 | 7.2 |  | 1214 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.34088 | 0.39094 | 0.68614 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 1 | 1 | 1 | 247 | 265 | 351 | 106 | 114 | 151 | 0.16238 | 0.18761 | 0.32782 | 1 | 5.1 | 5.6 | 7.2 |  | 1329 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 247 | 265 | 351 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.080053 | 0.091543 | 0.1306 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027221 | 0.031259 | 0.044205 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1698 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19075 | 0.22005 | 0.38322 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 1 | 1 | 1 | 271 | 291 | 385 | 117 | 125 | 166 | 0.075464 | 0.086002 | 0.1507 | 1.3 | 5.1 | 5.6 | 7.2 |  | 1807 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 271 | 291 | 385 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.058006 | 0.066147 | 0.096216 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.029989 | 0.034414 | 0.049475 | 0.3 | 6.3 | 6.8 | 9.1 |  | 861 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.17225 | 0.19897 | 0.28489 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.12816 | 0.14543 | 0.21066 | 0.7 | 6.3 | 6.8 | 9.1 |  | 1109 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.08544 | 0.098724 | 0.17572 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.041839 | 0.048366 | 0.086726 | 0.5 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.53376 | 0.61345 | 1.1024 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.32782 | 0.37695 | 0.67993 | 1 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13202 | 0.15119 | 0.22007 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.052857 | 0.061301 | 0.089183 | 0.7 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.33623 | 0.38608 | 0.69032 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 1 | 1 | 1 | 384 | 412 | 552 | 165 | 177 | 237 | 0.14891 | 0.1711 | 0.30491 | 1.3 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 552 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.075931 | 0.087579 | 0.12886 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.039137 | 0.045024 | 0.066147 | 0.3 | 6.7 | 7.4 | 10.3 |  | 968 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.22512 | 0.26068 | 0.38263 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 1 | 1 | 1 | 357 | 384 | 468 | 154 | 165 | 201 | 0.16798 | 0.19212 | 0.28215 | 0.7 | 6.7 | 7.4 | 10.3 |  | 1247 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 357 | 384 | 468 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11149 | 0.12815 | 0.23705 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.055362 | 0.062825 | 0.11592 | 0.5 | 7 | 7.7 | 10.7 |  | 1561 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.69865 | 0.80277 | 1.4856 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 1 | 1 | 1 | 403 | 432 | 588 | 173 | 186 | 253 | 0.42949 | 0.49599 | 0.91409 | 1 | 7 | 7.7 | 10.7 |  | 1708 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 403 | 432 | 588 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17327 | 0.20033 | 0.29749 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.070366 | 0.081167 | 0.11951 | 0.7 | 7 | 7.7 | 10.7 |  | 2183 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.43934 | 0.50252 | 0.92966 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 1 | 1 | 1 | 440 | 471 | 641 | 189 | 203 | 276 | 0.19481 | 0.2244 | 0.41228 | 1.3 | 7 | 7.7 | 10.7 |  | 2324 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 440 | 471 | 641 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.096216 | 0.1106 | 0.16616 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.049475 | 0.057025 | 0.085184 | 0.3 | 7.8 | 8.7 | 12.2 |  | 1076 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.28489 | 0.33052 | 0.49084 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.21066 | 0.24513 | 0.36381 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1386 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14098 | 0.16137 | 0.30506 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.069595 | 0.079155 | 0.14931 | 0.5 | 7 | 7.7 | 10.7 |  | 1734 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.88558 | 1.0174 | 1.9255 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.54481 | 0.62528 | 1.1827 | 1 | 7 | 7.7 | 10.7 |  | 1898 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22007 | 0.25634 | 0.38406 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.089183 | 0.1038 | 0.15579 | 0.7 | 7 | 7.7 | 10.7 |  | 2425 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.5561 | 0.63417 | 1.1993 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 1 | 1 | 1 | 495 | 530 | 730 | 213 | 228 | 314 | 0.24681 | 0.28241 | 0.53233 | 1.3 | 7 | 7.7 | 10.7 |  | 2582 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 495 | 530 | 730 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12026 | 0.13925 | 0.20811 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.062011 | 0.071501 | 0.10658 | 0.3 | 8.4 | 9.3 | 14 |  | 1184 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.35764 | 0.41173 | 0.61623 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 1 | 1 | 1 | 452 | 487 | 598 | 194 | 209 | 257 | 0.26332 | 0.30444 | 0.45561 | 0.7 | 8.4 | 9.3 | 14 |  | 1525 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 452 | 487 | 598 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.15961 | 0.18125 | 0.34482 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.071928 | 0.081641 | 0.15442 | 0.5 | 7.9 | 8.8 | 12.5 |  | 1907 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0402 | 1.1908 | 2.2504 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 1 | 1 | 1 | 459 | 492 | 678 | 197 | 212 | 292 | 0.55597 | 0.64325 | 1.2155 | 1 | 7.9 | 8.8 | 12.5 |  | 2088 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 678 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25239 | 0.29324 | 0.4392 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.092734 | 0.10762 | 0.16047 | 0.7 | 7.9 | 8.8 | 12.5 |  | 2668 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.61237 | 0.70183 | 1.323 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 1 | 1 | 1 | 502 | 537 | 741 | 216 | 231 | 319 | 0.25374 | 0.28981 | 0.54925 | 1.3 | 7.9 | 8.8 | 12.5 |  | 2840 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 502 | 537 | 741 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.1423 | 0.16616 | 0.25469 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.072596 | 0.085184 | 0.13032 | 0.3 | 8.9 | 9.9 | 14.8 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.42166 | 0.49084 | 0.75556 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.31302 | 0.36381 | 0.5575 | 0.7 | 8.9 | 9.9 | 14.8 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.21425 | 0.24563 | 0.47256 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10572 | 0.12043 | 0.23072 | 0.5 | 8.7 | 9.8 | 14.3 |  | 2081 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3428 | 1.541 | 2.9626 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.8231 | 0.95035 | 1.8229 | 1 | 8.7 | 9.8 | 14.3 |  | 2278 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33035 | 0.38406 | 0.59314 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13202 | 0.15425 | 0.23882 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2910 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.83892 | 0.96093 | 1.853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 1 | 1 | 1 | 610 | 653 | 909 | 262 | 281 | 391 | 0.37189 | 0.42721 | 0.82216 | 1.3 | 8.7 | 9.8 | 14.3 |  | 3098 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 909 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.19719 | 0.23082 | 0.36171 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10004 | 0.11746 | 0.18481 | 0.3 | 10.1 | 11.2 | 17.5 |  | 1506 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.58065 | 0.67784 | 1.0706 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.42835 | 0.50166 | 0.79144 | 0.7 | 10.1 | 11.2 | 17.5 |  | 1940 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30027 | 0.34226 | 0.6727 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.14762 | 0.16846 | 0.32963 | 0.5 | 9.6 | 10.5 | 16.1 |  | 2428 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8841 | 2.1613 | 4.2367 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1583 | 1.3255 | 2.6125 | 1 | 9.6 | 10.5 | 16.1 |  | 2657 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.45488 | 0.5345 | 0.84723 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18319 | 0.2146 | 0.34168 | 0.7 | 9.6 | 10.5 | 16.1 |  | 3395 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1792 | 1.3495 | 2.64 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 1 | 1 | 1 | 723 | 775 | 1087 | 311 | 333 | 467 | 0.5223 | 0.59805 | 1.1693 | 1.3 | 9.6 | 10.5 | 16.1 |  | 3615 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 723 | 775 | 1087 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.25674 | 0.30367 | 0.48711 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.13179 | 0.1548 | 0.24862 | 0.3 | 11 | 12.4 | 19.2 |  | 1722 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.76 | 0.8943 | 1.4394 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 1 | 1 | 1 | 667 | 723 | 922 | 287 | 311 | 396 | 0.56517 | 0.66113 | 1.0601 | 0.7 | 11 | 12.4 | 19.2 |  | 2218 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 667 | 723 | 922 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.39516 | 0.44891 | 0.90784 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.19451 | 0.22035 | 0.44599 | 0.5 | 11.5 | 12.8 | 19.6 |  | 2774 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.4809 | 2.8351 | 5.7191 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 1 | 1 | 1 | 761 | 813 | 1160 | 327 | 350 | 499 | 1.5224 | 1.7427 | 3.529 | 1 | 11.5 | 12.8 | 19.6 |  | 3037 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 761 | 813 | 1160 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.59917 | 0.70634 | 1.1463 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24073 | 0.28274 | 0.46016 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3880 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.554 | 1.7666 | 3.5736 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 1 | 1 | 1 | 831 | 887 | 1265 | 357 | 381 | 544 | 0.6865 | 0.781 | 1.5827 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4131 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 831 | 887 | 1265 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.33323 | 0.39134 | 0.63084 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.17115 | 0.19899 | 0.3217 | 0.3 | 12.2 | 13.7 | 22 |  | 1937 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.98809 | 1.1564 | 1.8615 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.72919 | 0.85618 | 1.3791 | 0.7 | 12.2 | 13.7 | 22 |  | 2495 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.45183 | 0.51539 | 1.0407 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.20229 | 0.23072 | 0.46362 | 0.5 | 11.5 | 12.8 | 19.6 |  | 3121 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 2.9885 | 3.4035 | 6.8824 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 1 | 1 | 1 | 773 | 825 | 1176 | 332 | 355 | 506 | 1.569 | 1.7926 | 3.6282 | 1 | 11.5 | 12.8 | 19.6 |  | 3416 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 773 | 825 | 1176 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.69979 | 0.82228 | 1.3328 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25239 | 0.29536 | 0.48161 | 0.7 | 11.5 | 12.8 | 19.6 |  | 4365 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7303 | 1.9735 | 3.9919 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 1 | 1 | 1 | 845 | 902 | 1286 | 363 | 388 | 553 | 0.70956 | 0.8097 | 1.6351 | 1.3 | 11.5 | 12.8 | 19.6 |  | 4648 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 845 | 902 | 1286 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.40147 | 0.47319 | 0.79282 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.20444 | 0.24261 | 0.40402 | 0.3 | 13.4 | 14.8 | 24 |  | 2152 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.1839 | 1.3971 | 2.3445 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 1 | 1 | 1 | 835 | 909 | 1182 | 359 | 391 | 508 | 0.87514 | 1.0341 | 1.7259 | 0.7 | 13.4 | 14.8 | 24 |  | 2772 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 835 | 909 | 1182 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.64795 | 0.71619 | 1.4882 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.31723 | 0.35254 | 0.73099 | 0.5 | 13.2 | 14.7 | 23.5 |  | 3468 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.0688 | 4.5186 | 9.3927 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 1 | 1 | 1 | 978 | 1029 | 1487 | 421 | 442 | 639 | 2.5164 | 2.7723 | 5.7729 | 1 | 13.2 | 14.7 | 23.5 |  | 3796 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 978 | 1029 | 1487 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.9394 | 1.1131 | 1.879 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.37682 | 0.447 | 0.75301 | 0.7 | 13.2 | 14.7 | 23.5 |  | 4850 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.5441 | 2.8216 | 5.8504 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 1 | 1 | 1 | 1066 | 1123 | 1621 | 458 | 483 | 697 | 1.125 | 1.2501 | 2.5881 | 1.3 | 13.2 | 14.7 | 23.5 |  | 5164 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1066 | 1123 | 1621 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2130.3 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.47596 | 0.56571 | 0.97696 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.24261 | 0.28832 | 0.49556 | 0.3 | 13.4 | 14.8 | 24 |  | 2367 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2073.32 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.4031 | 1.6731 | 2.8737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 1 | 1 | 1 | 911 | 996 | 1313 | 392 | 428 | 565 | 1.0393 | 1.2342 | 2.1255 | 0.7 | 13.4 | 14.8 | 24 |  | 3049 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 911 | 996 | 1313 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3052 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.79556 | 0.86285 | 1.8286 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.3897 | 0.42302 | 0.89958 | 0.5 | 15.5 | 16.8 | 27.5 |  | 3815 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2839.68 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.0255 | 5.4363 | 11.5429 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 1 | 1 | 1 | 1085 | 1130 | 1649 | 467 | 486 | 709 | 3.093 | 3.3484 | 7.1 | 1 | 15.5 | 16.8 | 27.5 |  | 4176 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1085 | 1130 | 1649 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4268 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1172 | 1.3328 | 2.3127 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.44962 | 0.5345 | 0.92809 | 0.7 | 15.5 | 16.8 | 27.5 |  | 5335 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4544 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.1297 | 3.3942 | 7.1908 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 1 | 1 | 1 | 1184 | 1233 | 1799 | 509 | 530 | 774 | 1.3871 | 1.5029 | 3.1866 | 1.3 | 15.5 | 16.8 | 27.5 |  | 5680 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1184 | 1233 | 1799 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.55969 | 0.66635 | 1.1757 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.284 | 0.34024 | 0.59629 | 0.3 | 14.8 | 16.6 | 28 |  | 2582 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.647 | 1.9665 | 3.4558 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.2173 | 1.4515 | 2.5499 | 0.7 | 14.8 | 16.6 | 28 |  | 3326 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.96247 | 1.0319 | 2.2039 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.47256 | 0.50606 | 1.081 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4162 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.0642 | 6.5145 | 13.9415 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.7288 | 4.0086 | 8.5857 | 1 | 16.4 | 17.7 | 29.7 |  | 4555 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3149 | 1.5722 | 2.7911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.52881 | 0.63288 | 1.1214 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5820 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.7754 | 4.0561 | 8.6685 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 1 | 1 | 1 | 1301 | 1349 | 1978 | 559 | 580 | 851 | 1.6704 | 1.7973 | 3.8469 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6197 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1301 | 1349 | 1978 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2518.2 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.65009 | 0.78926 | 1.3926 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.33091 | 0.40147 | 0.70618 | 0.3 | 16.2 | 18.6 | 31.4 |  | 2798 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2450.72 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 1.9241 | 2.3291 | 4.0906 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 1 | 1 | 1 | 1069 | 1179 | 1573 | 460 | 507 | 676 | 1.4212 | 1.7193 | 3.0209 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3604 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1179 | 1573 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3606.4 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0496 | 1.1266 | 2.4079 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.48158 | 0.51852 | 1.1083 | 0.5 | 16.4 | 17.7 | 29.7 |  | 4508 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3355.8 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.8237 | 7.321 | 15.6954 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 1 | 1 | 1 | 1204 | 1248 | 1829 | 518 | 537 | 786 | 3.8014 | 4.0839 | 8.7177 | 1 | 16.4 | 17.7 | 29.7 |  | 4935 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1204 | 1248 | 1829 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5044 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.429 | 1.7376 | 3.0778 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.5345 | 0.64851 | 1.1505 | 0.7 | 16.4 | 17.7 | 29.7 |  | 6305 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5370.4 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.0561 | 4.3564 | 9.326 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 1 | 1 | 1 | 1315 | 1363 | 1998 | 565 | 586 | 859 | 1.7062 | 1.8343 | 3.919 | 1.3 | 16.4 | 17.7 | 29.7 |  | 6713 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1315 | 1363 | 1998 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.69946 | 0.85087 | 1.4931 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.34259 | 0.41431 | 0.72652 | 0.3 | 16.2 | 18.6 | 31.4 |  | 3013 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.1329 | 2.5903 | 4.5395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 1 | 1 | 1 | 1077 | 1189 | 1583 | 463 | 511 | 681 | 1.4394 | 1.7459 | 3.0648 | 0.7 | 16.2 | 18.6 | 31.4 |  | 3881 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1077 | 1189 | 1583 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3386 | 1.3944 | 3.0663 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.65498 | 0.68705 | 1.5041 | 0.5 | 19.3 | 20.4 | 34.5 |  | 4855 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.433 | 8.8063 | 19.3822 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 1 | 1 | 1 | 1408 | 1439 | 2140 | 605 | 619 | 920 | 5.1776 | 5.4188 | 11.927 | 1 | 19.3 | 20.4 | 34.5 |  | 5314 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1408 | 1439 | 2140 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.7998 | 2.19 | 3.8746 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.72284 | 0.87987 | 1.5576 | 0.7 | 19.3 | 20.4 | 34.5 |  | 6790 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5784 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.2475 | 5.4911 | 12.0517 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 1 | 1 | 1 | 1421 | 1453 | 2159 | 611 | 625 | 928 | 1.9929 | 2.0845 | 4.569 | 1.3 | 19.3 | 20.4 | 34.5 |  | 7230 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1421 | 1453 | 2159 |  | 0 | 0 | 0 | 1
35010 |  |  | 3 | 50 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2905.2 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.75062 | 0.91093 | 1.5971 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.3497 | 0.42736 | 0.75062 | 0.3 | 16.2 | 18.6 | 31.4 |  | 3228 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
35011 |  |  | 3 | 50 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2827.44 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.3523 | 2.8567 | 5.0114 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 1 | 1 | 1 | 1085 | 1197 | 1595 | 467 | 515 | 686 | 1.4638 | 1.7728 | 3.1091 | 0.7 | 16.2 | 18.6 | 31.4 |  | 4158 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1085 | 1197 | 1595 |  | 0 | 0 | 0 | 1
35015 |  |  | 3 | 50 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4161.6 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.4409 | 1.5041 | 3.306 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.66913 | 0.69791 | 1.5362 | 0.5 | 19.3 | 20.4 | 34.5 |  | 5202 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
35016 |  |  | 3 | 50 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3871.92 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.3241 | 9.7397 | 21.4745 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 1 | 1 | 1 | 1419 | 1451 | 2157 | 610 | 624 | 928 | 5.2632 | 5.5063 | 12.1344 | 1 | 19.3 | 20.4 | 34.5 |  | 5694 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1419 | 1451 | 2157 |  | 0 | 0 | 0 | 1
35020 |  |  | 3 | 50 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5820 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 1.96 | 2.3843 | 4.2189 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.73953 | 0.90197 | 1.5967 | 0.7 | 19.3 | 20.4 | 34.5 |  | 7275 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
35021 |  |  | 3 | 50 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6196.8 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.588 | 5.8283 | 12.8241 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 1 | 1 | 1 | 1653 | 1690 | 2513 | 711 | 727 | 1081 | 2.6924 | 2.814 | 6.1868 | 1.3 | 19.3 | 20.4 | 34.5 |  | 7746 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1653 | 1690 | 2513 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 526.5 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.017829 | 0.020764 | 0.027985 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0090736 | 0.010335 | 0.014595 | 0.4 | 3.6 | 4.1 | 5.1 |  | 585 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 507.96 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.053899 | 0.061654 | 0.083243 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 140.1833 | 150.0066 | 175.408 | 1 | 1 | 1 | 158 | 169 | 198 | 68 | 73 | 85 | 0.036729 | 0.042099 | 0.056428 | 0.8 | 3.6 | 4.1 | 5.1 |  | 747 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 158 | 169 | 198 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 631.8 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.030136 | 0.033893 | 0.047355 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.015112 | 0.017829 | 0.023917 | 0.4 | 4.8 | 5.4 | 6.8 |  | 702 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 609.28 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.089529 | 0.10277 | 0.14171 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.45 | 194.75 | 229.9 | 1 | 1 | 1 | 204 | 219 | 259 | 88 | 94 | 111 | 0.060326 | 0.068502 | 0.094389 | 0.8 | 4.8 | 5.4 | 6.8 |  | 896 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 204 | 219 | 259 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.041918 | 0.04754 | 0.083417 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.20821 | 0.023614 | 0.041015 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1120 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 850 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.25469 | 0.29435 | 0.51344 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.3 | 218.5 | 289.75 | 1 | 1 | 1 | 229 | 246 | 326 | 98 | 106 | 140 | 0.14118 | 0.16491 | 0.28619 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1250 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 229 | 246 | 326 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.064311 | 0.074721 | 0.10413 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.025779 | 0.029741 | 0.041677 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1565 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1383.2 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.16331 | 0.1867 | 0.32679 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.1379 | 238.4601 | 315.609 | 1 | 1 | 1 | 250 | 269 | 355 | 108 | 116 | 153 | 0.066012 | 0.07599 | 0.13114 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1729 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 250 | 269 | 355 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 737.1 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.044664 | 0.051063 | 0.071639 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.02263 | 0.025912 | 0.037053 | 0.4 | 5.5 | 5.9 | 7.9 |  | 819 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 711.28 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.13189 | 0.15188 | 0.21511 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222.3128 | 238.4066 | 285.038 | 1 | 1 | 1 | 250 | 268 | 321 | 108 | 115 | 138 | 0.089529 | 0.10106 | 0.14372 | 0.8 | 5.5 | 5.9 | 7.9 |  | 1046 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 250 | 268 | 321 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.051482 | 0.059832 | 0.10364 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.021607 | 0.025001 | 0.043753 | 0.6 | 5.1 | 5.6 | 7.2 |  | 1306 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 992.12 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.3457 | 0.39637 | 0.69499 | 0.0002083 | 1.724 | 4 | 0.0013928 | 208.6178 | 223.9466 | 296.4 | 1 | 1 | 1 | 235 | 252 | 334 | 101 | 108 | 144 | 0.14986 | 0.17113 | 0.30262 | 1.2 | 5.1 | 5.6 | 7.2 |  | 1459 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 235 | 252 | 334 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.081339 | 0.092988 | 0.13257 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.027725 | 0.031827 | 0.044973 | 0.8 | 5.1 | 5.6 | 7.2 |  | 1826 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1613.6 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19483 | 0.22467 | 0.39071 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 228.2894 | 245.0636 | 324.349 | 1 | 1 | 1 | 257 | 276 | 365 | 111 | 119 | 157 | 0.069672 | 0.07991 | 0.13799 | 1.6 | 5.1 | 5.6 | 7.2 |  | 2017 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 257 | 276 | 365 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 842.4 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.060926 | 0.069429 | 0.10079 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.031613 | 0.03625 | 0.052011 | 0.4 | 6.3 | 6.8 | 9.1 |  | 936 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 812.6 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.18216 | 0.21024 | 0.30041 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 262.2 | 281.2 | 340.1 | 1 | 1 | 1 | 295 | 317 | 383 | 127 | 136 | 165 | 0.12241 | 0.13972 | 0.20304 | 0.8 | 6.3 | 6.8 | 9.1 |  | 1195 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 295 | 317 | 383 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1194.4 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.087289 | 0.10082 | 0.17918 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.042831 | 0.049492 | 0.088599 | 0.6 | 6 | 6.7 | 9 |  | 1493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1133.56 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.54088 | 0.62148 | 1.1158 | 0.0002083 | 1.724 | 4 | 0.0013928 | 296.4 | 318.25 | 427.5 | 1 | 1 | 1 | 334 | 358 | 481 | 144 | 154 | 207 | 0.30262 | 0.3457 | 0.62148 | 1.2 | 6 | 6.7 | 9 |  | 1667 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 334 | 358 | 481 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1668.8 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13401 | 0.15342 | 0.22316 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.053755 | 0.062322 | 0.090596 | 0.8 | 6 | 6.7 | 9 |  | 2086 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1844.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.34292 | 0.39362 | 0.70281 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 323.8191 | 347.2396 | 465.899 | 1 | 1 | 1 | 365 | 391 | 525 | 157 | 168 | 226 | 0.13799 | 0.15771 | 0.28318 | 1.6 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 365 | 391 | 525 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 947.7 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.079641 | 0.091789 | 0.13479 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.041196 | 0.047355 | 0.069429 | 0.4 | 6.7 | 7.4 | 10.3 |  | 1053 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 914.6 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.2377 | 0.27502 | 0.40281 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 301.3049 | 324.1188 | 394.668 | 1 | 1 | 1 | 339 | 365 | 444 | 146 | 157 | 191 | 0.16026 | 0.18443 | 0.26953 | 0.8 | 6.7 | 7.4 | 10.3 |  | 1345 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 339 | 365 | 444 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1343.2 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11382 | 0.13078 | 0.24155 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.056628 | 0.064239 | 0.11833 | 0.6 | 7 | 7.7 | 10.7 |  | 1679 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1275.68 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.70764 | 0.81291 | 1.5029 | 0.0002083 | 1.724 | 4 | 0.0013928 | 339.8904 | 364.1384 | 495.9 | 1 | 1 | 1 | 383 | 410 | 558 | 165 | 176 | 240 | 0.39637 | 0.45049 | 0.83346 | 1.2 | 7 | 7.7 | 10.7 |  | 1876 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 383 | 410 | 558 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1877.6 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17578 | 0.20318 | 0.3015 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.071517 | 0.082469 | 0.12134 | 0.8 | 7 | 7.7 | 10.7 |  | 2347 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2075.2 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.44777 | 0.512 | 0.94584 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 370.8322 | 397.2875 | 541.044 | 1 | 1 | 1 | 418 | 447 | 609 | 180 | 192 | 262 | 0.18071 | 0.20525 | 0.37919 | 1.6 | 7 | 7.7 | 10.7 |  | 2594 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 418 | 447 | 609 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1053 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.10079 | 0.11577 | 0.17359 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.052011 | 0.059902 | 0.089292 | 0.4 | 7.8 | 8.7 | 12.2 |  | 1170 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1015.92 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.30041 | 0.34823 | 0.51602 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 340.1 | 365.75 | 449.35 | 1 | 1 | 1 | 383 | 412 | 506 | 165 | 177 | 218 | 0.20304 | 0.23259 | 0.34823 | 0.8 | 7.8 | 8.7 | 12.2 |  | 1494 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 383 | 412 | 506 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1492.8 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.14384 | 0.16458 | 0.31066 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.071141 | 0.080885 | 0.15231 | 0.6 | 7 | 7.7 | 10.7 |  | 1866 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1417.12 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.89663 | 1.0298 | 1.9472 | 0.0002083 | 1.724 | 4 | 0.0013928 | 382.85 | 409.45 | 565.25 | 1 | 1 | 1 | 431 | 461 | 637 | 185 | 198 | 274 | 0.49732 | 0.56903 | 1.0841 | 1.2 | 7 | 7.7 | 10.7 |  | 2084 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 431 | 461 | 637 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2086.4 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22316 | 0.25987 | 0.38907 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.090596 | 0.10541 | 0.15808 | 0.8 | 7 | 7.7 | 10.7 |  | 2608 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2305.6 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.56645 | 0.64577 | 1.2194 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 417.4455 | 446.9919 | 616.189 | 1 | 1 | 1 | 470 | 503 | 694 | 202 | 216 | 298 | 0.22688 | 0.25897 | 0.48904 | 1.6 | 7 | 7.7 | 10.7 |  | 2882 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 470 | 503 | 694 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1158.3 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.12584 | 0.14561 | 0.21718 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.06511 | 0.075017 | 0.11159 | 0.4 | 8.4 | 9.3 | 14 |  | 1287 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1117.24 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.37664 | 0.43327 | 0.64704 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 381.3495 | 410.8364 | 504.298 | 1 | 1 | 1 | 429 | 463 | 568 | 184 | 199 | 244 | 0.25073 | 0.29182 | 0.43327 | 0.8 | 8.4 | 9.3 | 14 |  | 1643 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 568 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1642.4 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.1628 | 0.18481 | 0.35104 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.073519 | 0.083417 | 0.15751 | 0.6 | 7.9 | 8.8 | 12.5 |  | 2053 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1558.56 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0529 | 1.2051 | 2.2751 | 0.0002083 | 1.724 | 4 | 0.0013928 | 387.4413 | 414.864 | 571.9 | 1 | 1 | 1 | 436 | 467 | 644 | 187 | 201 | 277 | 0.50804 | 0.58626 | 1.1078 | 1.2 | 7.9 | 8.8 | 12.5 |  | 2292 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 436 | 467 | 644 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2295.2 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25588 | 0.2972 | 0.44483 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.094195 | 0.10929 | 0.16282 | 0.8 | 7.9 | 8.8 | 12.5 |  | 2869 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2536 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.62363 | 0.7145 | 1.3449 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 423.3665 | 453.332 | 624.929 | 1 | 1 | 1 | 477 | 511 | 704 | 205 | 220 | 303 | 0.23358 | 0.26853 | 0.50539 | 1.6 | 7.9 | 8.8 | 12.5 |  | 3170 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 477 | 511 | 704 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1263.6 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.14877 | 0.17359 | 0.26554 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.076161 | 0.089292 | 0.13631 | 0.4 | 8.9 | 9.9 | 14.8 |  | 1404 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1219.24 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.44366 | 0.51602 | 0.79249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 415.15 | 449.35 | 559.55 | 1 | 1 | 1 | 468 | 506 | 630 | 201 | 218 | 271 | 0.29753 | 0.34823 | 0.53113 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1793 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 468 | 506 | 630 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1791.2 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.21836 | 0.25026 | 0.48074 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.10795 | 0.12293 | 0.23511 | 0.6 | 8.7 | 9.8 | 14.3 |  | 2239 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1700.68 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3587 | 1.5588 | 2.9941 | 0.0002083 | 1.724 | 4 | 0.0013928 | 471.2 | 505.4 | 703 | 1 | 1 | 1 | 531 | 569 | 792 | 228 | 245 | 341 | 0.7528 | 0.86827 | 1.6737 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2501 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 531 | 569 | 792 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2504 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33475 | 0.38907 | 0.60044 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13401 | 0.15652 | 0.24214 | 0.8 | 8.7 | 9.8 | 14.3 |  | 3130 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2766.4 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.85372 | 0.97758 | 1.8825 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 514.4827 | 550.9384 | 766.479 | 1 | 1 | 1 | 579 | 620 | 863 | 249 | 267 | 371 | 0.34292 | 0.39362 | 0.75417 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3458 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 579 | 620 | 863 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1474.2 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.20583 | 0.24076 | 0.3765 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10478 | 0.12292 | 0.19297 | 0.4 | 10.1 | 11.2 | 17.5 |  | 1638 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1422.56 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.60988 | 0.71137 | 1.121 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 489.25 | 530.1 | 668.8 | 1 | 1 | 1 | 551 | 597 | 753 | 237 | 257 | 324 | 0.40948 | 0.47917 | 0.7514 | 0.8 | 10.1 | 11.2 | 17.5 |  | 2092 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 551 | 597 | 753 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2089.6 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.30579 | 0.34845 | 0.68383 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.1506 | 0.1718 | 0.33561 | 0.6 | 9.6 | 10.5 | 16.1 |  | 2612 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1984.24 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.9054 | 2.1852 | 4.2796 | 0.0002083 | 1.724 | 4 | 0.0013928 | 559.55 | 598.5 | 840.75 | 1 | 1 | 1 | 630 | 674 | 947 | 271 | 290 | 407 | 1.0607 | 1.2134 | 2.3785 | 1.2 | 9.6 | 10.5 | 16.1 |  | 2918 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 630 | 674 | 947 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2920.8 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.46068 | 0.54118 | 0.85718 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18582 | 0.21762 | 0.34621 | 0.8 | 9.6 | 10.5 | 16.1 |  | 3651 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3228 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.1991 | 1.3719 | 2.68 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 610.1144 | 653.3898 | 916.769 | 1 | 1 | 1 | 687 | 736 | 1032 | 295 | 316 | 444 | 0.47936 | 0.54914 | 1.0759 | 1.6 | 9.6 | 10.5 | 16.1 |  | 4035 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 687 | 736 | 1032 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1684.8 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.26766 | 0.31634 | 0.50636 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.13784 | 0.16177 | 0.25923 | 0.4 | 11 | 12.4 | 19.2 |  | 1872 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1625.2 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.79713 | 0.93719 | 1.5048 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 562.4 | 609.9 | 778.05 | 1 | 1 | 1 | 633 | 687 | 876 | 272 | 295 | 377 | 0.53494 | 0.62626 | 1.0088 | 0.8 | 11 | 12.4 | 19.2 |  | 2390 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 633 | 687 | 876 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.8 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.40217 | 0.45674 | 0.92228 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.19829 | 0.22457 | 0.45378 | 0.6 | 11.5 | 12.8 | 19.6 |  | 2986 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2267.12 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.5079 | 2.8653 | 5.7747 | 0.0002083 | 1.724 | 4 | 0.0013928 | 642.2 | 685.9 | 978.5 | 1 | 1 | 1 | 723 | 772 | 1102 | 311 | 332 | 474 | 1.3941 | 1.5872 | 3.2194 | 1.2 | 11.5 | 12.8 | 19.6 |  | 3334 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 723 | 772 | 1102 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3338.4 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.60654 | 0.71483 | 1.1592 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24408 | 0.28658 | 0.46602 | 0.8 | 11.5 | 12.8 | 19.6 |  | 4173 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3688.8 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.5792 | 1.7949 | 3.6257 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 701.1317 | 748.5751 | 1067.059 | 1 | 1 | 1 | 790 | 843 | 1202 | 340 | 362 | 517 | 0.63465 | 0.71842 | 1.4542 | 1.6 | 11.5 | 12.8 | 19.6 |  | 4611 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 790 | 843 | 1202 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1895.4 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.34698 | 0.4072 | 0.65502 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.17878 | 0.2077 | 0.33503 | 0.4 | 12.2 | 13.7 | 22 |  | 2106 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1828.52 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 1.035 | 1.2103 | 1.9436 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 641.348 | 696.2143 | 888.003 | 1 | 1 | 1 | 722 | 784 | 1000 | 310 | 337 | 430 | 0.6896 | 0.8111 | 1.303 | 0.8 | 12.2 | 13.7 | 22 |  | 2689 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 722 | 784 | 1000 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2687.2 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.45971 | 0.52422 | 1.057 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.2062 | 0.23511 | 0.47167 | 0.6 | 11.5 | 12.8 | 19.6 |  | 3359 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2550.68 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 3.0202 | 3.439 | 6.9477 | 0.0002083 | 1.724 | 4 | 0.0013928 | 651.9934 | 696.1118 | 992.275 | 1 | 1 | 1 | 734 | 784 | 1117 | 316 | 337 | 480 | 1.4389 | 1.635 | 3.3009 | 1.2 | 11.5 | 12.8 | 19.6 |  | 3751 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 734 | 784 | 1117 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3755.2 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.70822 | 0.83197 | 1.3475 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25588 | 0.29935 | 0.48771 | 0.8 | 11.5 | 12.8 | 19.6 |  | 4694 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4150.4 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.758 | 2.0046 | 4.0492 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 712.6173 | 760.8379 | 1084.539 | 1 | 1 | 1 | 803 | 857 | 1221 | 345 | 369 | 525 | 0.65324 | 0.74615 | 1.4991 | 1.6 | 11.5 | 12.8 | 19.6 |  | 5188 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 803 | 857 | 1221 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2106 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.41769 | 0.49195 | 0.82241 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.21336 | 0.253 | 0.42033 | 0.4 | 13.4 | 14.8 | 24 |  | 2340 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2031.84 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.2389 | 1.4608 | 2.4453 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 703.95 | 766.65 | 997.5 | 1 | 1 | 1 | 793 | 863 | 1123 | 341 | 371 | 483 | 0.82992 | 0.97777 | 1.634 | 0.8 | 13.4 | 14.8 | 24 |  | 2988 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 793 | 863 | 1123 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2985.6 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.65873 | 0.72795 | 1.5104 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.32302 | 0.35889 | 0.74296 | 0.6 | 13.2 | 14.7 | 23.5 |  | 3732 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2834.24 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.1102 | 4.564 | 9.4782 | 0.0002083 | 1.724 | 4 | 0.0013928 | 824.6 | 868.3 | 1254 | 1 | 1 | 1 | 929 | 978 | 1412 | 399 | 421 | 607 | 2.2865 | 2.5437 | 5.2631 | 1.2 | 13.2 | 14.7 | 23.5 |  | 4168 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 929 | 978 | 1412 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4172.8 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.95028 | 1.1257 | 1.8989 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.38175 | 0.45272 | 0.76199 | 0.8 | 13.2 | 14.7 | 23.5 |  | 5216 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4611.2 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.5829 | 2.8641 | 5.9302 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 899.3873 | 947.661 | 1367.639 | 1 | 1 | 1 | 1013 | 1067 | 1540 | 436 | 459 | 662 | 1.0379 | 1.1491 | 2.3726 | 1.6 | 13.2 | 14.7 | 23.5 |  | 5764 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 1013 | 1067 | 1540 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2316.6 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.49481 | 0.58767 | 1.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.253 | 0.30042 | 0.5151 | 0.4 | 13.4 | 14.8 | 24 |  | 2574 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2235.16 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.467 | 1.7479 | 2.9944 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 768.7279 | 839.9298 | 1107.263 | 1 | 1 | 1 | 866 | 946 | 1247 | 372 | 407 | 536 | 0.98291 | 1.1708 | 2.0014 | 0.8 | 13.4 | 14.8 | 24 |  | 3287 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 866 | 946 | 1247 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3284 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.80844 | 0.87667 | 1.8552 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.39662 | 0.43046 | 0.91391 | 0.6 | 15.5 | 16.8 | 27.5 |  | 4105 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3117.8 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.0752 | 5.4895 | 11.645 | 0.0002083 | 1.724 | 4 | 0.0013928 | 915.1902 | 953.3165 | 1391.275 | 1 | 1 | 1 | 1031 | 1074 | 1567 | 443 | 462 | 674 | 2.8146 | 3.0595 | 6.4808 | 1.2 | 15.5 | 16.8 | 27.5 |  | 4585 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1031 | 1074 | 1567 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4590.4 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1299 | 1.3475 | 2.3364 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.45536 | 0.54118 | 0.93885 | 0.8 | 15.5 | 16.8 | 27.5 |  | 5738 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5072 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.176 | 3.444 | 7.2862 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 998.5041 | 1040.1012 | 1517.929 | 1 | 1 | 1 | 1125 | 1171 | 1709 | 484 | 504 | 735 | 1.2762 | 1.3827 | 2.9189 | 1.6 | 15.5 | 16.8 | 27.5 |  | 6340 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1125 | 1171 | 1709 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2527.2 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.58144 | 0.69173 | 1.2176 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.29594 | 0.35425 | 0.61929 | 0.4 | 14.8 | 16.6 | 28 |  | 2808 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2438.48 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.7207 | 2.0527 | 3.5979 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 833.15 | 912.95 | 1216.95 | 1 | 1 | 1 | 938 | 1028 | 1371 | 403 | 442 | 590 | 1.1485 | 1.3747 | 2.4133 | 0.8 | 14.8 | 16.6 | 28 |  | 3586 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 938 | 1028 | 1371 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3582.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.97767 | 1.048 | 2.2351 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.48074 | 0.51475 | 1.0978 | 0.6 | 16.4 | 17.7 | 29.7 |  | 4478 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3401.36 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.1227 | 6.5768 | 14.0618 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1006.05 | 1043.1 | 1529.5 | 1 | 1 | 1 | 1133 | 1175 | 1723 | 487 | 505 | 741 | 3.3973 | 3.6513 | 7.8246 | 1.2 | 16.4 | 17.7 | 29.7 |  | 5002 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1133 | 1175 | 1723 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5007.2 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3294 | 1.5892 | 2.819 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.53542 | 0.64061 | 1.134 | 0.8 | 16.4 | 17.7 | 29.7 |  | 6259 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5533.6 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.83 | 4.1142 | 8.7808 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1097.6357 | 1137.5659 | 1668.219 | 1 | 1 | 1 | 1236 | 1281 | 1879 | 531 | 551 | 808 | 1.5332 | 1.6496 | 3.5213 | 1.6 | 16.4 | 17.7 | 29.7 |  | 6917 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1236 | 1281 | 1879 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2737.8 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.67492 | 0.81873 | 1.4412 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.34458 | 0.41769 | 0.73289 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3042 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2641.12 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 2.0087 | 2.4293 | 4.2555 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 902.0356 | 994.8922 | 1326.523 | 1 | 1 | 1 | 1016 | 1120 | 1494 | 437 | 482 | 642 | 1.3446 | 1.6274 | 2.8455 | 0.8 | 16.2 | 18.6 | 31.4 |  | 3884 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1016 | 1120 | 1494 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3881.6 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.066 | 1.1441 | 2.4416 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.4899 | 0.5274 | 1.1255 | 0.6 | 16.4 | 17.7 | 29.7 |  | 4852 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3684.24 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.8885 | 7.3899 | 15.8287 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1015.4265 | 1052.3662 | 1543.275 | 1 | 1 | 1 | 1144 | 1185 | 1738 | 492 | 510 | 747 | 3.4669 | 3.7235 | 7.9511 | 1.2 | 16.4 | 17.7 | 29.7 |  | 5418 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1144 | 1185 | 1738 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5424.8 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4446 | 1.7561 | 3.1082 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.54118 | 0.6564 | 1.1634 | 0.8 | 16.4 | 17.7 | 29.7 |  | 6781 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5994.4 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.1142 | 4.4182 | 9.4455 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1109.137 | 1149.4857 | 1685.699 | 1 | 1 | 1 | 1249 | 1295 | 1898 | 537 | 557 | 816 | 1.5677 | 1.6853 | 3.5907 | 1.6 | 16.4 | 17.7 | 29.7 |  | 7493 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1249 | 1295 | 1898 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2948.4 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.72595 | 0.88236 | 1.5448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.35669 | 0.43099 | 0.75392 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3276 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2844.44 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.2256 | 2.7004 | 4.7203 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 908.2 | 1003.2 | 1335.7 | 1 | 1 | 1 | 1023 | 1130 | 1504 | 440 | 486 | 647 | 1.3626 | 1.6538 | 2.8889 | 0.8 | 16.2 | 18.6 | 31.4 |  | 4183 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1023 | 1130 | 1504 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4180 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3588 | 1.4154 | 3.1079 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.66585 | 0.69838 | 1.5265 | 0.6 | 19.3 | 20.4 | 34.5 |  | 5225 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3967.8 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.5109 | 8.8871 | 19.5422 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1187.5 | 1214.1 | 1805 | 1 | 1 | 1 | 1337 | 1367 | 2033 | 575 | 588 | 874 | 4.7259 | 4.9407 | 10.8651 | 1.2 | 19.3 | 20.4 | 34.5 |  | 5835 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1337 | 1367 | 2033 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5841.6 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.8189 | 2.2126 | 3.9117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.7315 | 0.89014 | 1.5744 | 0.8 | 19.3 | 20.4 | 34.5 |  | 7302 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6456 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.3201 | 5.5667 | 12.201 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1198.6919 | 1225.5218 | 1821.1391 | 1 | 1 | 1 | 1350 | 1380 | 2051 | 581 | 593 | 882 | 1.8322 | 1.9079 | 4.1892 | 1.6 | 19.3 | 20.4 | 34.5 |  | 8070 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1350 | 1380 | 2051 |  | 0 | 0 | 0 | 1
36010 |  |  | 3 | 60 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3159 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.77881 | 0.94438 | 1.652 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.36406 | 0.4445 | 0.77881 | 0.4 | 16.2 | 18.6 | 31.4 |  | 3510 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
36011 |  |  | 3 | 60 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3047.76 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.4534 | 2.9767 | 5.2087 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 914.85 | 1009.85 | 1345.2 | 1 | 1 | 1 | 1030 | 1137 | 1515 | 443 | 489 | 651 | 1.3808 | 1.6737 | 2.9239 | 0.8 | 16.2 | 18.6 | 31.4 |  | 4482 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 1030 | 1137 | 1515 |  | 0 | 0 | 0 | 1
36015 |  |  | 3 | 60 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4478.4 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.4625 | 1.5265 | 3.3503 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.68022 | 0.7094 | 1.559 | 0.6 | 19.3 | 20.4 | 34.5 |  | 5598 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
36016 |  |  | 3 | 60 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4251.36 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.409 | 9.8278 | 21.6494 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1197 | 1223.6 | 1819.25 | 1 | 1 | 1 | 1348 | 1378 | 2049 | 580 | 593 | 881 | 4.808 | 5.0245 | 11.0388 | 1.2 | 19.3 | 20.4 | 34.5 |  | 6252 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1348 | 1378 | 2049 |  | 0 | 0 | 0 | 1
36020 |  |  | 3 | 60 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6259.2 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 1.9806 | 2.4087 | 4.2588 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.74837 | 0.91246 | 1.614 | 0.8 | 19.3 | 20.4 | 34.5 |  | 7824 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
36021 |  |  | 3 | 60 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6916.8 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.6647 | 5.9078 | 12.9817 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1394.6 | 1425.95 | 2119.45 | 1 | 1 | 1 | 1571 | 1606 | 2387 | 676 | 691 | 1026 | 2.473 | 2.5829 | 5.6538 | 1.6 | 19.3 | 20.4 | 34.5 |  | 8646 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1571 | 1606 | 2387 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 554 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.018801 | 0.021879 | 0.029441 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.0096037 | 0.010931 | 0.015407 | 0.5 | 3.6 | 4.1 | 5.1 |  | 624 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 540.6 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.057216 | 0.065398 | 0.088149 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 132.8052 | 142.1115 | 166.176 | 1 | 1 | 1 | 150 | 160 | 187 | 65 | 69 | 80 | 0.035849 | 0.040183 | 0.053323 | 0.9 | 3.6 | 4.1 | 5.1 |  | 795 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 150 | 160 | 187 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 674.1 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.031692 | 0.035621 | 0.049687 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.01595 | 0.018801 | 0.025182 | 0.5 | 4.8 | 5.4 | 6.8 |  | 749 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 648.72 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.094767 | 0.1087 | 0.14963 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 171.9 | 184.5 | 217.8 | 1 | 1 | 1 | 194 | 208 | 245 | 83 | 89 | 105 | 0.057216 | 0.065398 | 0.089782 | 0.9 | 4.8 | 5.4 | 6.8 |  | 954 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 194 | 208 | 245 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.042892 | 0.048627 | 0.085194 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.21215 | 0.024203 | 0.04197 | 0.7 | 4.8 | 5.5 | 7.2 |  | 1183 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 922.08 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.25838 | 0.29854 | 0.52024 | 0.0002083 | 1.724 | 4 | 0.0013928 | 192.6 | 207 | 274.5 | 1 | 1 | 1 | 217 | 233 | 309 | 93 | 100 | 133 | 0.12929 | 0.14923 | 0.26227 | 1.4 | 4.8 | 5.5 | 7.2 |  | 1356 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 217 | 233 | 309 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.065359 | 0.075916 | 0.10573 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.026252 | 0.030277 | 0.042396 | 0.9 | 4.8 | 5.5 | 7.2 |  | 1652 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1524.8 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.16681 | 0.19063 | 0.3332 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 210.4464 | 225.9095 | 298.998 | 1 | 1 | 1 | 237 | 254 | 337 | 102 | 109 | 145 | 0.060423 | 0.068833 | 0.1206 | 1.9 | 4.8 | 5.5 | 7.2 |  | 1906 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 237 | 254 | 337 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 786.6 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.046877 | 0.053557 | 0.075013 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.023834 | 0.027271 | 0.038925 | 0.5 | 5.5 | 5.9 | 7.9 |  | 874 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 756.84 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.13931 | 0.1603 | 0.22662 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 210.6121 | 225.8589 | 270.036 | 1 | 1 | 1 | 237 | 254 | 304 | 102 | 109 | 131 | 0.084927 | 0.096458 | 0.13729 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1113 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 237 | 254 | 304 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.052647 | 0.061161 | 0.10579 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.022152 | 0.02562 | 0.044764 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1380 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1075.76 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.35052 | 0.4018 | 0.70384 | 0.0002083 | 1.724 | 4 | 0.0013928 | 197.6379 | 212.1599 | 280.8 | 1 | 1 | 1 | 223 | 239 | 316 | 96 | 103 | 136 | 0.13766 | 0.15821 | 0.2741 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1582 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 223 | 239 | 316 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.082625 | 0.094433 | 0.13454 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.028229 | 0.032396 | 0.045741 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1927 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1779.2 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.19892 | 0.2293 | 0.3982 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 216.2742 | 232.1655 | 307.278 | 1 | 1 | 1 | 244 | 261 | 346 | 105 | 112 | 149 | 0.063961 | 0.072603 | 0.12723 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2224 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 244 | 261 | 346 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 898.2 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.063847 | 0.07271 | 0.10537 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.033237 | 0.038086 | 0.054546 | 0.5 | 6.3 | 6.8 | 9.1 |  | 998 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 864.96 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.19207 | 0.22152 | 0.31592 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 248.4 | 266.4 | 322.2 | 1 | 1 | 1 | 280 | 300 | 363 | 120 | 129 | 156 | 0.116 | 0.13329 | 0.19207 | 0.9 | 6.3 | 6.8 | 9.1 |  | 1272 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 280 | 300 | 363 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1262.4 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.089137 | 0.10292 | 0.18264 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.043823 | 0.050617 | 0.090471 | 0.7 | 6 | 6.7 | 9 |  | 1578 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1229.44 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.548 | 0.62951 | 1.1291 | 0.0002083 | 1.724 | 4 | 0.0013928 | 280.8 | 301.5 | 405 | 1 | 1 | 1 | 316 | 340 | 456 | 136 | 146 | 196 | 0.2741 | 0.31541 | 0.56499 | 1.4 | 6 | 6.7 | 9 |  | 1808 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 316 | 340 | 456 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1761.6 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.136 | 0.15565 | 0.22626 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.054652 | 0.063342 | 0.092009 | 0.9 | 6 | 6.7 | 9 |  | 2202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2033.6 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.34961 | 0.40116 | 0.7153 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 306.776 | 328.9638 | 441.378 | 1 | 1 | 1 | 345 | 370 | 497 | 148 | 159 | 214 | 0.12555 | 0.14457 | 0.25941 | 1.9 | 6 | 6.7 | 9 |  | 2542 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 345 | 370 | 497 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1010.7 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.08335 | 0.095999 | 0.14072 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.043254 | 0.049687 | 0.07271 | 0.5 | 6.7 | 7.4 | 10.3 |  | 1123 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 973.08 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.25029 | 0.28936 | 0.42298 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 285.4467 | 307.0599 | 373.896 | 1 | 1 | 1 | 321 | 346 | 421 | 138 | 149 | 181 | 0.15173 | 0.17584 | 0.2557 | 0.9 | 6.7 | 7.4 | 10.3 |  | 1431 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 321 | 346 | 421 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1420 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.11615 | 0.13341 | 0.24604 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.057894 | 0.065653 | 0.12074 | 0.7 | 7 | 7.7 | 10.7 |  | 1775 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1383.12 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.71663 | 0.82305 | 1.5202 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322.0014 | 344.9732 | 469.8 | 1 | 1 | 1 | 363 | 389 | 529 | 156 | 167 | 227 | 0.35959 | 0.4115 | 0.75568 | 1.4 | 7 | 7.7 | 10.7 |  | 2034 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 363 | 389 | 529 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1982.4 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.17829 | 0.20603 | 0.30552 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.072667 | 0.083771 | 0.12316 | 0.9 | 7 | 7.7 | 10.7 |  | 2478 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2287.2 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.45621 | 0.52148 | 0.96201 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 351.3147 | 376.3777 | 512.568 | 1 | 1 | 1 | 396 | 424 | 577 | 170 | 182 | 248 | 0.1649 | 0.18859 | 0.34685 | 1.9 | 7 | 7.7 | 10.7 |  | 2859 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 396 | 424 | 577 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1123.2 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.10537 | 0.12095 | 0.18102 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.054546 | 0.062778 | 0.093399 | 0.5 | 7.8 | 8.7 | 12.2 |  | 1248 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1081.2 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.31592 | 0.36594 | 0.5412 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 322.2 | 346.5 | 425.7 | 1 | 1 | 1 | 363 | 390 | 479 | 156 | 168 | 206 | 0.19207 | 0.22152 | 0.32809 | 0.9 | 7.8 | 8.7 | 12.2 |  | 1590 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 363 | 390 | 479 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1577.6 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.1467 | 0.1678 | 0.31626 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.072687 | 0.082614 | 0.15532 | 0.7 | 7 | 7.7 | 10.7 |  | 1972 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1536.8 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.90767 | 1.0423 | 1.9688 | 0.0002083 | 1.724 | 4 | 0.0013928 | 362.7 | 387.9 | 535.5 | 1 | 1 | 1 | 408 | 437 | 603 | 175 | 188 | 259 | 0.45144 | 0.52024 | 0.98132 | 1.4 | 7 | 7.7 | 10.7 |  | 2260 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 603 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2202.4 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.22626 | 0.2634 | 0.39408 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.092009 | 0.10702 | 0.16038 | 0.9 | 7 | 7.7 | 10.7 |  | 2753 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2541.6 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.57681 | 0.65738 | 1.2396 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395.4747 | 423.466 | 583.758 | 1 | 1 | 1 | 445 | 477 | 657 | 191 | 205 | 283 | 0.20738 | 0.23837 | 0.44992 | 1.9 | 7 | 7.7 | 10.7 |  | 3177 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 445 | 477 | 657 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1235.7 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.13141 | 0.15196 | 0.22625 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.068208 | 0.078534 | 0.1166 | 0.5 | 8.4 | 9.3 | 14 |  | 1373 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1189.32 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.39564 | 0.4548 | 0.67786 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 361.2785 | 389.2135 | 477.756 | 1 | 1 | 1 | 407 | 438 | 538 | 175 | 188 | 231 | 0.23963 | 0.27509 | 0.4092 | 0.9 | 8.4 | 9.3 | 14 |  | 1749 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 407 | 438 | 538 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1735.2 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.16599 | 0.18837 | 0.35727 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.07511 | 0.085194 | 0.16061 | 0.7 | 7.9 | 8.8 | 12.5 |  | 2169 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1690.48 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.0656 | 1.2194 | 2.2999 | 0.0002083 | 1.724 | 4 | 0.0013928 | 367.0497 | 393.0291 | 541.8 | 1 | 1 | 1 | 413 | 443 | 610 | 178 | 190 | 262 | 0.46688 | 0.53126 | 1.004 | 1.4 | 7.9 | 8.8 | 12.5 |  | 2486 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 413 | 443 | 610 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2422.4 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.25936 | 0.30117 | 0.45046 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.095657 | 0.11095 | 0.16517 | 0.9 | 7.9 | 8.8 | 12.5 |  | 3028 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2796 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.63489 | 0.72718 | 1.3669 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 401.0841 | 429.4724 | 592.038 | 1 | 1 | 1 | 452 | 484 | 667 | 194 | 208 | 287 | 0.21384 | 0.24528 | 0.46254 | 1.9 | 7.9 | 8.8 | 12.5 |  | 3495 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 452 | 484 | 667 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1348.2 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.15525 | 0.18102 | 0.27638 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.079725 | 0.093399 | 0.1423 | 0.5 | 8.9 | 9.9 | 14.8 |  | 1498 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1297.44 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.46566 | 0.5412 | 0.82943 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 393.3 | 425.7 | 530.1 | 1 | 1 | 1 | 443 | 479 | 597 | 190 | 206 | 257 | 0.28075 | 0.32809 | 0.50274 | 0.9 | 8.9 | 9.9 | 14.8 |  | 1908 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 443 | 479 | 597 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1892.8 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.22248 | 0.2549 | 0.48893 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.11017 | 0.12542 | 0.2395 | 0.7 | 8.7 | 9.8 | 14.3 |  | 2366 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.16 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.3745 | 1.5767 | 3.0255 | 0.0002083 | 1.724 | 4 | 0.0013928 | 446.4 | 478.8 | 666 | 1 | 1 | 1 | 503 | 539 | 750 | 216 | 232 | 323 | 0.68487 | 0.78901 | 1.5202 | 1.4 | 8.7 | 9.8 | 14.3 |  | 2712 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 503 | 539 | 750 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2643.2 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.33914 | 0.39408 | 0.60774 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.136 | 0.15879 | 0.24546 | 0.9 | 8.7 | 9.8 | 14.3 |  | 3304 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3049.6 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.86852 | 0.99423 | 1.9119 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 487.4047 | 521.9416 | 726.138 | 1 | 1 | 1 | 549 | 588 | 818 | 236 | 253 | 352 | 0.31456 | 0.36076 | 0.69184 | 1.9 | 8.7 | 9.8 | 14.3 |  | 3812 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 549 | 588 | 818 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1572.3 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.21448 | 0.2507 | 0.39129 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.10952 | 0.12838 | 0.20114 | 0.5 | 10.1 | 11.2 | 17.5 |  | 1747 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1513.68 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.63911 | 0.74491 | 1.1713 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 463.5 | 502.2 | 633.6 | 1 | 1 | 1 | 522 | 566 | 714 | 224 | 243 | 307 | 0.38562 | 0.45121 | 0.70877 | 0.9 | 10.1 | 11.2 | 17.5 |  | 2226 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 522 | 566 | 714 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2208.8 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.31131 | 0.35463 | 0.69496 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.15357 | 0.17514 | 0.3416 | 0.7 | 9.6 | 10.5 | 16.1 |  | 2761 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2151.52 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.9266 | 2.2091 | 4.3224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 530.1 | 567 | 796.5 | 1 | 1 | 1 | 597 | 639 | 897 | 257 | 275 | 386 | 0.96636 | 1.1051 | 2.1644 | 1.4 | 9.6 | 10.5 | 16.1 |  | 3164 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 597 | 639 | 897 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3083.2 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.46648 | 0.54785 | 0.86712 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.18846 | 0.22065 | 0.35074 | 0.9 | 9.6 | 10.5 | 16.1 |  | 3854 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3558.4 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.219 | 1.3942 | 2.7201 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 578.0031 | 619.0009 | 868.518 | 1 | 1 | 1 | 651 | 697 | 978 | 280 | 300 | 421 | 0.44057 | 0.50476 | 0.98497 | 1.9 | 9.6 | 10.5 | 16.1 |  | 4448 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 651 | 697 | 978 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1797.3 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.27858 | 0.32901 | 0.5256 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.14388 | 0.16875 | 0.26985 | 0.5 | 11 | 12.4 | 19.2 |  | 1997 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1729.92 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.83425 | 0.98008 | 1.5702 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 532.8 | 577.8 | 737.1 | 1 | 1 | 1 | 600 | 651 | 830 | 258 | 280 | 357 | 0.50652 | 0.59325 | 0.94897 | 0.9 | 11 | 12.4 | 19.2 |  | 2544 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 600 | 651 | 830 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2524 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.40918 | 0.46457 | 0.93673 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.20207 | 0.22879 | 0.46157 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3155 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2458.88 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.5348 | 2.8956 | 5.8303 | 0.0002083 | 1.724 | 4 | 0.0013928 | 608.4 | 649.8 | 927 | 1 | 1 | 1 | 685 | 732 | 1044 | 295 | 315 | 449 | 1.2701 | 1.4464 | 2.9214 | 1.4 | 11.5 | 12.8 | 19.6 |  | 3616 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 685 | 732 | 1044 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3524 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.6139 | 0.72333 | 1.1721 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.24742 | 0.29043 | 0.47188 | 0.9 | 11.5 | 12.8 | 19.6 |  | 4405 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4066.4 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.6045 | 1.8231 | 3.6777 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 664.23 | 709.1764 | 1010.898 | 1 | 1 | 1 | 748 | 799 | 1138 | 322 | 344 | 489 | 0.58036 | 0.66117 | 1.3238 | 1.9 | 11.5 | 12.8 | 19.6 |  | 5083 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 748 | 799 | 1138 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2021.4 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.36074 | 0.42305 | 0.6792 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.1864 | 0.21642 | 0.34837 | 0.5 | 12.2 | 13.7 | 22 |  | 2246 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1946.16 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 1.0818 | 1.2642 | 2.0258 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 607.5928 | 659.5714 | 841.266 | 1 | 1 | 1 | 684 | 743 | 947 | 294 | 319 | 407 | 0.6519 | 0.76331 | 1.2231 | 0.9 | 12.2 | 13.7 | 22 |  | 2862 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 684 | 743 | 947 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2840 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.46758 | 0.53305 | 1.0733 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.21012 | 0.2395 | 0.47973 | 0.7 | 11.5 | 12.8 | 19.6 |  | 3550 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2766.24 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 3.0519 | 3.4744 | 7.013 | 0.0002083 | 1.724 | 4 | 0.0013928 | 617.678 | 659.4743 | 940.05 | 1 | 1 | 1 | 696 | 743 | 1059 | 299 | 319 | 455 | 1.3044 | 1.4831 | 2.9993 | 1.4 | 11.5 | 12.8 | 19.6 |  | 4068 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 696 | 743 | 1059 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3964 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.71665 | 0.84166 | 1.3623 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.25936 | 0.30334 | 0.4938 | 0.9 | 11.5 | 12.8 | 19.6 |  | 4955 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4575.2 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.7857 | 2.0357 | 4.1064 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 675.1111 | 720.7938 | 1027.458 | 1 | 1 | 1 | 760 | 812 | 1157 | 327 | 349 | 498 | 0.59826 | 0.68026 | 1.3724 | 1.9 | 11.5 | 12.8 | 19.6 |  | 5719 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 760 | 812 | 1157 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2246.4 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.43391 | 0.51071 | 0.852 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.22229 | 0.26339 | 0.43664 | 0.5 | 13.4 | 14.8 | 24 |  | 2496 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2162.4 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.2939 | 1.5245 | 2.5461 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 666.9 | 726.3 | 945 | 1 | 1 | 1 | 751 | 818 | 1064 | 323 | 352 | 458 | 0.78193 | 0.92342 | 1.5375 | 0.9 | 13.4 | 14.8 | 24 |  | 3180 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 751 | 818 | 1064 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3155.2 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.6695 | 0.7397 | 1.5326 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.32881 | 0.36523 | 0.75492 | 0.7 | 13.2 | 14.7 | 23.5 |  | 3944 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3073.6 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.1516 | 4.6093 | 9.5637 | 0.0002083 | 1.724 | 4 | 0.0013928 | 781.2 | 822.6 | 1188 | 1 | 1 | 1 | 880 | 926 | 1338 | 378 | 398 | 575 | 2.0764 | 2.2999 | 4.7727 | 1.4 | 13.2 | 14.7 | 23.5 |  | 4520 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 880 | 926 | 1338 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4404.8 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.96115 | 1.1383 | 1.9187 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.38668 | 0.45843 | 0.77097 | 0.9 | 13.2 | 14.7 | 23.5 |  | 5506 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 5083.2 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.6216 | 2.9065 | 6.01 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 852.0512 | 897.7841 | 1295.658 | 1 | 1 | 1 | 960 | 1011 | 1459 | 413 | 435 | 627 | 0.94837 | 1.0507 | 2.1634 | 1.9 | 13.2 | 14.7 | 23.5 |  | 6354 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 960 | 1011 | 1459 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2471.4 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.51367 | 0.60963 | 1.0481 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.26339 | 0.31252 | 0.53463 | 0.5 | 13.4 | 14.8 | 24 |  | 2746 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2378.64 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.531 | 1.8226 | 3.1151 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 728.2686 | 795.7229 | 1048.986 | 1 | 1 | 1 | 820 | 896 | 1181 | 353 | 385 | 508 | 0.9285 | 1.0983 | 1.8796 | 0.9 | 13.4 | 14.8 | 24 |  | 3498 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 820 | 896 | 1181 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3470.4 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.82132 | 0.89049 | 1.8817 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.40355 | 0.4379 | 0.92824 | 0.7 | 15.5 | 16.8 | 27.5 |  | 4338 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3380.96 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.1249 | 5.5427 | 11.7472 | 0.0002083 | 1.724 | 4 | 0.0013928 | 867.0223 | 903.142 | 1318.05 | 1 | 1 | 1 | 976 | 1017 | 1484 | 420 | 437 | 638 | 2.5589 | 2.7685 | 5.8668 | 1.4 | 15.5 | 16.8 | 27.5 |  | 4972 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 976 | 1017 | 1484 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4845.6 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1425 | 1.3623 | 2.3601 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.46111 | 0.54785 | 0.94961 | 0.9 | 15.5 | 16.8 | 27.5 |  | 6057 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5591.2 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.2224 | 3.4938 | 7.3816 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 945.9512 | 985.3591 | 1438.038 | 1 | 1 | 1 | 1065 | 1110 | 1619 | 458 | 477 | 696 | 1.1632 | 1.2604 | 2.6593 | 1.9 | 15.5 | 16.8 | 27.5 |  | 6989 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1065 | 1110 | 1619 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2695.5 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.6032 | 0.71711 | 1.2595 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.30788 | 0.36826 | 0.6423 | 0.5 | 14.8 | 16.6 | 28 |  | 2995 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2594.88 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.7944 | 2.139 | 3.7399 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 789.3 | 864.9 | 1152.9 | 1 | 1 | 1 | 889 | 974 | 1298 | 382 | 419 | 558 | 1.0818 | 1.2939 | 2.2551 | 0.9 | 14.8 | 16.6 | 28 |  | 3816 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 889 | 974 | 1298 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3786.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 0.99286 | 1.0642 | 2.2663 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.48893 | 0.52344 | 1.1146 | 0.7 | 16.4 | 17.7 | 29.7 |  | 4733 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3688.32 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.1812 | 6.639 | 14.182 | 0.0002083 | 1.724 | 4 | 0.0013928 | 953.1 | 988.2 | 1449 | 1 | 1 | 1 | 1073 | 1113 | 1632 | 461 | 479 | 702 | 3.0783 | 3.3214 | 7.093 | 1.4 | 16.4 | 17.7 | 29.7 |  | 5424 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1073 | 1113 | 1632 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5285.6 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.344 | 1.6062 | 2.8469 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.54203 | 0.64833 | 1.1467 | 0.9 | 16.4 | 17.7 | 29.7 |  | 6607 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6100 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.8846 | 4.1723 | 8.893 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1039.8654 | 1077.694 | 1580.418 | 1 | 1 | 1 | 1171 | 1214 | 1780 | 504 | 522 | 765 | 1.4052 | 1.5061 | 3.2058 | 1.9 | 16.4 | 17.7 | 29.7 |  | 7625 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1171 | 1214 | 1780 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2920.5 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.69975 | 0.8482 | 1.4898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.35825 | 0.43391 | 0.75961 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3245 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2811.12 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 2.0933 | 2.5295 | 4.4204 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 854.5601 | 942.5295 | 1256.706 | 1 | 1 | 1 | 962 | 1061 | 1415 | 414 | 456 | 608 | 1.2642 | 1.5245 | 2.6639 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4134 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 962 | 1061 | 1415 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4101.6 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.0824 | 1.1615 | 2.4753 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.49823 | 0.53628 | 1.1426 | 0.7 | 16.4 | 17.7 | 29.7 |  | 5127 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3995.68 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 6.9533 | 7.4588 | 15.962 | 0.0002083 | 1.724 | 4 | 0.0013928 | 961.983 | 996.9785 | 1462.05 | 1 | 1 | 1 | 1083 | 1123 | 1647 | 466 | 483 | 708 | 3.1449 | 3.3766 | 7.2139 | 1.4 | 16.4 | 17.7 | 29.7 |  | 5876 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1083 | 1123 | 1647 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5726.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4603 | 1.7746 | 3.1385 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.54785 | 0.66429 | 1.1764 | 0.9 | 16.4 | 17.7 | 29.7 |  | 7158 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6608 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.1723 | 4.48 | 9.5651 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1050.7614 | 1088.9865 | 1596.978 | 1 | 1 | 1 | 1183 | 1226 | 1798 | 509 | 527 | 773 | 1.4329 | 1.5347 | 3.2725 | 1.9 | 16.4 | 17.7 | 29.7 |  | 8260 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1183 | 1226 | 1798 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3144.6 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.75244 | 0.91385 | 1.5966 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.37079 | 0.44767 | 0.78131 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3494 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3027.36 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.3183 | 2.8105 | 4.9011 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 860.4 | 950.4 | 1265.4 | 1 | 1 | 1 | 969 | 1070 | 1425 | 417 | 460 | 613 | 1.282 | 1.5505 | 2.7066 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4452 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 969 | 1070 | 1425 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4417.6 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.3791 | 1.4364 | 3.1494 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.67673 | 0.70972 | 1.5489 | 0.7 | 19.3 | 20.4 | 34.5 |  | 5522 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4303.04 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.5887 | 8.9679 | 19.7022 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1125 | 1150.2 | 1710 | 1 | 1 | 1 | 1267 | 1295 | 1926 | 545 | 557 | 828 | 4.2911 | 4.4807 | 9.845 | 1.4 | 19.3 | 20.4 | 34.5 |  | 6328 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1267 | 1295 | 1926 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6166.4 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.838 | 2.2352 | 3.9487 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.74017 | 0.90042 | 1.5913 | 0.9 | 19.3 | 20.4 | 34.5 |  | 7708 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7116.8 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.3927 | 5.6422 | 12.3503 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1135.6028 | 1161.0206 | 1725.2897 | 1 | 1 | 1 | 1279 | 1308 | 1943 | 550 | 562 | 835 | 1.6698 | 1.7426 | 3.812 | 1.9 | 19.3 | 20.4 | 34.5 |  | 8896 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1279 | 1308 | 1943 |  | 0 | 0 | 0 | 1
37010 |  |  | 3 | 70 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3369.6 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.807 | 0.97782 | 1.7069 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.37841 | 0.46164 | 0.807 | 0.5 | 16.2 | 18.6 | 31.4 |  | 3744 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
37011 |  |  | 3 | 70 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3243.6 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.5544 | 3.0967 | 5.4061 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 866.7 | 956.7 | 1274.4 | 1 | 1 | 1 | 976 | 1077 | 1435 | 420 | 463 | 617 | 1.2999 | 1.5702 | 2.741 | 0.9 | 16.2 | 18.6 | 31.4 |  | 4770 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 976 | 1077 | 1435 |  | 0 | 0 | 0 | 1
37015 |  |  | 3 | 70 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4732.8 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.4841 | 1.5489 | 3.3947 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.6913 | 0.72089 | 1.5819 | 0.7 | 19.3 | 20.4 | 34.5 |  | 5916 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
37016 |  |  | 3 | 70 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4610.4 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.4939 | 9.916 | 21.8242 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1134 | 1159.2 | 1723.5 | 1 | 1 | 1 | 1277 | 1305 | 1941 | 549 | 561 | 835 | 4.3539 | 4.5448 | 10.0111 | 1.4 | 19.3 | 20.4 | 34.5 |  | 6780 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1277 | 1305 | 1941 |  | 0 | 0 | 0 | 1
37020 |  |  | 3 | 70 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6607.2 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 2.0011 | 2.433 | 4.2987 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.75721 | 0.92296 | 1.6312 | 0.9 | 19.3 | 20.4 | 34.5 |  | 8259 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
37021 |  |  | 3 | 70 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7624.8 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.7414 | 5.9874 | 13.1392 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1321.2 | 1350.9 | 2007.9 | 1 | 1 | 1 | 1488 | 1521 | 2261 | 640 | 654 | 972 | 2.2529 | 2.3514 | 5.1488 | 1.9 | 19.3 | 20.4 | 34.5 |  | 9531 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1488 | 1521 | 2261 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 554 | 649 | 695 | 812 | N/A | 1 | 1 | 1 | #VALUE! | 357 | 382 | 447 | #VALUE! | 61 | 66 | 77 | #VALUE! | 0.020746 | 0.024108 | 0.032354 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 1 | 1 | 1 | 101 | 108 | 127 | 43 | 46 | 55 | 0.010664 | 0.012122 | 0.017032 | 0.6 | 3.6 | 4.1 | 5.1 |  | 685 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 101 | 108 | 127 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 597.72 | 881.0208 | 942.7581 | 1102.4 | N/A | 1 | 1 | 1 | #VALUE! | 485 | 519 | 607 | #VALUE! | 83 | 89 | 104 | #VALUE! | 0.063851 | 0.072887 | 0.097961 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 118.0491 | 126.3214 | 147.712 | 1 | 1 | 1 | 133 | 142 | 166 | 57 | 61 | 71 | 0.031354 | 0.035642 | 0.047499 | 1.2 | 3.6 | 4.1 | 5.1 |  | 879 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 133 | 142 | 166 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 40 | 738.9 | 841.6923 | 901.3595 | 1066.38 | N/A | 1 | 1 | 1 | #VALUE! | 463 | 496 | 587 | #VALUE! | 80 | 85 | 101 | #VALUE! | 0.034804 | 0.039079 | 0.05435 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 1 | 1 | 1 | 131 | 141 | 166 | 56 | 61 | 71 | 0.017626 | 0.020746 | 0.027712 | 0.6 | 4.8 | 5.4 | 6.8 |  | 821 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 131 | 141 | 166 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 1142.0362 | 1222.9947 | 1446.9 | N/A | 1 | 1 | 1 | #VALUE! | 629 | 673 | 796 | #VALUE! | 108 | 116 | 137 | #VALUE! | 0.10524 | 0.12055 | 0.16545 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 152.8 | 164 | 193.6 | 1 | 1 | 1 | 172 | 185 | 218 | 74 | 80 | 94 | 0.051371 | 0.059548 | 0.080852 | 1.2 | 4.8 | 5.4 | 6.8 |  | 1055 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 172 | 185 | 218 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | N/A | 1 | 1 | 1 | #VALUE! | 527 | 565 | 748 | #VALUE! | 91 | 97 | 129 | #VALUE! | 0.044839 | 0.0508 | 0.088747 | 0.0002083 | 1.724 | 2 | 0.00046183 | 423.6582 | 140.2613 | 185.64 | 1 | 1 | 1 | 477 | 158 | 209 | 205 | 68 | 90 | 0.22005 | 0.025381 | 0.043881 | 0.9 | 4.8 | 5.5 | 7.2 |  | 1272 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 477 | 158 | 209 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1059.44 | 1399.7242 | 1502.5729 | 1988.7 | N/A | 1 | 1 | 1 | #VALUE! | 770 | 827 | 1094 | #VALUE! | 132 | 142 | 188 | #VALUE! | 0.26578 | 0.30693 | 0.53385 | 0.0002083 | 1.724 | 4 | 0.0013928 | 171.2 | 184 | 244 | 1 | 1 | 1 | 193 | 207 | 275 | 83 | 89 | 118 | 0.10659 | 0.12228 | 0.21309 | 1.8 | 4.8 | 5.5 | 7.2 |  | 1558 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 193 | 207 | 275 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | N/A | 1 | 1 | 1 | #VALUE! | 741 | 794 | 939 | #VALUE! | 127 | 137 | 162 | #VALUE! | 0.067457 | 0.078306 | 0.10892 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 1 | 1 | 1 | 187 | 201 | 237 | 80 | 86 | 102 | 0.027198 | 0.031349 | 0.043834 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1774 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 237 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1707.6437 | 1802.6437 | 1935.0981 | 2561.16 | N/A | 1 | 1 | 1 | #VALUE! | 992 | 1065 | 1410 | #VALUE! | 171 | 183 | 243 | #VALUE! | 0.17381 | 0.1985 | 0.34602 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 187.0635 | 200.8085 | 265.776 | 1 | 1 | 1 | 211 | 226 | 299 | 91 | 97 | 129 | 0.050661 | 0.057383 | 0.10015 | 2.4 | 4.8 | 5.5 | 7.2 |  | 2262 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 211 | 226 | 299 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41 | 862.2 | 1029.7404 | 1104.286 | 1320.28 | N/A | 1 | 1 | 1 | #VALUE! | 567 | 608 | 727 | #VALUE! | 98 | 105 | 125 | #VALUE! | 0.051302 | 0.058544 | 0.081763 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 1 | 1 | 1 | 161 | 172 | 206 | 69 | 74 | 89 | 0.026241 | 0.02999 | 0.042669 | 0.6 | 5.5 | 5.9 | 7.9 |  | 958 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 161 | 172 | 206 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 1397.1862 | 1498.3321 | 1791.4 | N/A | 1 | 1 | 1 | #VALUE! | 769 | 825 | 986 | #VALUE! | 132 | 142 | 170 | #VALUE! | 0.15415 | 0.17714 | 0.24963 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 187.2108 | 200.7635 | 240.032 | 1 | 1 | 1 | 211 | 226 | 270 | 91 | 97 | 116 | 0.076026 | 0.08582 | 0.12055 | 1.2 | 5.5 | 5.9 | 7.9 |  | 1231 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 211 | 226 | 270 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | N/A | 1 | 1 | 1 | #VALUE! | 589 | 633 | 837 | #VALUE! | 101 | 109 | 144 | #VALUE! | 0.054978 | 0.063818 | 0.11009 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1 | 1 | 1 | 152 | 163 | 216 | 65 | 70 | 93 | 0.023242 | 0.026859 | 0.046785 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1484 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 152 | 163 | 216 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1235.56 | 1627.6272 | 1747.2217 | 2312.5 | N/A | 1 | 1 | 1 | #VALUE! | 896 | 962 | 1273 | #VALUE! | 154 | 165 | 219 | #VALUE! | 0.36017 | 0.41267 | 0.72154 | 0.0002083 | 1.724 | 4 | 0.0013928 | 175.6782 | 188.5866 | 249.6 | 1 | 1 | 1 | 198 | 212 | 281 | 85 | 91 | 121 | 0.1117 | 0.12775 | 0.2239 | 1.8 | 5.1 | 5.6 | 7.2 |  | 1817 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 198 | 212 | 281 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | N/A | 1 | 1 | 1 | #VALUE! | 831 | 891 | 1065 | #VALUE! | 143 | 153 | 183 | #VALUE! | 0.085198 | 0.097323 | 0.13847 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 1 | 1 | 1 | 192 | 206 | 246 | 83 | 89 | 106 | 0.029237 | 0.033533 | 0.047277 | 1.2 | 5.1 | 5.6 | 7.2 |  | 2070 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 246 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | N/A | 1 | 1 | 1 | #VALUE! | 1088 | 1168 | 1546 | #VALUE! | 187 | 201 | 266 | #VALUE! | 0.20709 | 0.23854 | 0.41318 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 192.2437 | 206.3694 | 273.136 | 1 | 1 | 1 | 217 | 232 | 308 | 93 | 100 | 132 | 0.052856 | 0.060898 | 0.10475 | 2.4 | 5.1 | 5.6 | 7.2 |  | 2639 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 217 | 232 | 308 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 985.5 | 1214.227 | 1304.1434 | 1574.18 | N/A | 1 | 1 | 1 | #VALUE! | 668 | 718 | 866 | #VALUE! | 115 | 123 | 149 | #VALUE! | 0.069687 | 0.079273 | 0.11452 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 1 | 1 | 1 | 190 | 204 | 246 | 82 | 88 | 106 | 0.036485 | 0.041757 | 0.059617 | 0.6 | 6.3 | 6.8 | 9.1 |  | 1095 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 246 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1647.5037 | 1769.5053 | 2135.9 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1175 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.2119 | 0.24406 | 0.34696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 220.8 | 236.8 | 286.4 | 1 | 1 | 1 | 249 | 267 | 323 | 107 | 115 | 139 | 0.1034 | 0.11859 | 0.17008 | 1.2 | 6.3 | 6.8 | 9.1 |  | 1406 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 249 | 267 | 323 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1300.3374 | 1395.3374 | 1496.2563 | 2007.56 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 823 | 1105 | #VALUE! | 132 | 142 | 190 | #VALUE! | 0.092834 | 0.10711 | 0.18957 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1 | 1 | 1 | 215 | 230 | 309 | 92 | 99 | 133 | 0.045807 | 0.052869 | 0.094217 | 0.9 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 215 | 230 | 309 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1412.36 | 2040.4332 | 2188.0092 | 2935.7 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.56223 | 0.64557 | 1.1558 | 0.0002083 | 1.724 | 4 | 0.0013928 | 249.6 | 268 | 360 | 1 | 1 | 1 | 281 | 302 | 405 | 121 | 130 | 174 | 0.2239 | 0.2579 | 0.45825 | 1.8 | 6 | 6.7 | 9 |  | 2077 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281 | 302 | 405 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1847.5719 | 1942.5719 | 2086.4239 | 2518.44 | N/A | 1 | 1 | 1 | #VALUE! | 1069 | 1148 | 1386 | #VALUE! | 184 | 197 | 238 | #VALUE! | 0.13997 | 0.16012 | 0.23244 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 1 | 1 | 1 | 270 | 290 | 351 | 116 | 125 | 151 | 0.056446 | 0.065383 | 0.094835 | 1.2 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 270 | 290 | 351 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2412.8 | 2627.7849 | 2817.8416 | 3780.76 | N/A | 1 | 1 | 1 | #VALUE! | 1446 | 1551 | 2081 | #VALUE! | 249 | 267 | 358 | #VALUE! | 0.36298 | 0.41624 | 0.74029 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 272.6898 | 292.4123 | 392.336 | 1 | 1 | 1 | 307 | 329 | 442 | 132 | 141 | 190 | 0.10475 | 0.11917 | 0.21364 | 2.4 | 6 | 6.7 | 9 |  | 3016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 307 | 329 | 442 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1108.8 | 1395.6272 | 1501.3 | 1828.08 | N/A | 1 | 1 | 1 | #VALUE! | 768 | 826 | 1006 | #VALUE! | 132 | 142 | 173 | #VALUE! | 0.090768 | 0.10442 | 0.15257 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 1 | 1 | 1 | 218 | 234 | 285 | 94 | 101 | 123 | 0.047371 | 0.05435 | 0.079273 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1232 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 285 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1893.6336 | 2037.014 | 2480.4 | N/A | 1 | 1 | 1 | #VALUE! | 1042 | 1121 | 1365 | #VALUE! | 179 | 193 | 235 | #VALUE! | 0.27545 | 0.31804 | 0.46333 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 253.7304 | 272.9421 | 332.352 | 1 | 1 | 1 | 286 | 307 | 374 | 123 | 132 | 161 | 0.13476 | 0.15415 | 0.22503 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1582 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 286 | 307 | 374 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1502.9168 | 1597.9168 | 1711.9131 | 2331.36 | N/A | 1 | 1 | 1 | #VALUE! | 879 | 942 | 1283 | #VALUE! | 151 | 162 | 221 | #VALUE! | 0.12082 | 0.13867 | 0.25503 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1 | 1 | 1 | 246 | 263 | 358 | 106 | 113 | 154 | 0.060427 | 0.068481 | 0.12557 | 0.9 | 7 | 7.7 | 10.7 |  | 1908 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 358 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1588.48 | 2336.6695 | 2503.3688 | 3409.2 | N/A | 1 | 1 | 1 | #VALUE! | 1286 | 1378 | 1876 | #VALUE! | 221 | 237 | 323 | #VALUE! | 0.73461 | 0.84333 | 1.5548 | 0.0002083 | 1.724 | 4 | 0.0013928 | 286.2235 | 306.6429 | 417.6 | 1 | 1 | 1 | 322 | 345 | 470 | 138 | 148 | 202 | 0.29011 | 0.33302 | 0.61515 | 1.8 | 7 | 7.7 | 10.7 |  | 2336 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 322 | 345 | 470 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2128.8 | 2232.7837 | 2401.8435 | 2924.64 | N/A | 1 | 1 | 1 | #VALUE! | 1229 | 1322 | 1610 | #VALUE! | 211 | 227 | 277 | #VALUE! | 0.18332 | 0.21173 | 0.31355 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 1 | 1 | 1 | 311 | 334 | 407 | 134 | 144 | 175 | 0.074967 | 0.086375 | 0.1268 | 1.2 | 7 | 7.7 | 10.7 |  | 2661 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 311 | 334 | 407 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2714.4 | 3009.2948 | 3223.9796 | 4390.56 | N/A | 1 | 1 | 1 | #VALUE! | 1656 | 1774 | 2416 | #VALUE! | 285 | 305 | 416 | #VALUE! | 0.47308 | 0.54044 | 0.99437 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 312.2797 | 334.5579 | 455.616 | 1 | 1 | 1 | 352 | 377 | 513 | 151 | 162 | 221 | 0.13626 | 0.15636 | 0.28728 | 2.4 | 7 | 7.7 | 10.7 |  | 3393 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 352 | 377 | 513 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1232.1 | 1574.3905 | 1696.1266 | 2081.98 | N/A | 1 | 1 | 1 | #VALUE! | 866 | 933 | 1146 | #VALUE! | 149 | 160 | 197 | #VALUE! | 0.11452 | 0.13131 | 0.19587 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 1 | 1 | 1 | 246 | 265 | 325 | 106 | 114 | 140 | 0.059617 | 0.068531 | 0.10162 | 0.6 | 7.8 | 8.7 | 12.2 |  | 1369 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 246 | 265 | 325 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 2136.1857 | 2301.3612 | 2824.9 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1267 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.34696 | 0.40136 | 0.59155 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 286.4 | 308 | 378.4 | 1 | 1 | 1 | 323 | 347 | 426 | 139 | 149 | 183 | 0.17008 | 0.19415 | 0.28732 | 1.2 | 7.8 | 8.7 | 12.2 |  | 1758 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 323 | 347 | 426 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1696 | 1798.7737 | 1926.0892 | 2655.16 | N/A | 1 | 1 | 1 | #VALUE! | 990 | 1060 | 1461 | #VALUE! | 170 | 182 | 251 | #VALUE! | 0.15241 | 0.17423 | 0.32745 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1 | 1 | 1 | 277 | 296 | 408 | 119 | 127 | 175 | 0.075779 | 0.086073 | 0.16133 | 0.9 | 7 | 7.7 | 10.7 |  | 2120 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 277 | 296 | 408 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1765.28 | 2630.3871 | 2816.5634 | 3882.7 | N/A | 1 | 1 | 1 | #VALUE! | 1448 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.92975 | 1.0672 | 2.0121 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322.4 | 344.8 | 476 | 1 | 1 | 1 | 363 | 388 | 536 | 156 | 167 | 230 | 0.36945 | 0.42259 | 0.79485 | 1.8 | 7 | 7.7 | 10.7 |  | 2596 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 363 | 388 | 536 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2365.6 | 2518.7768 | 2713.5353 | 3330.84 | N/A | 1 | 1 | 1 | #VALUE! | 1386 | 1493 | 1833 | #VALUE! | 238 | 257 | 315 | #VALUE! | 0.23244 | 0.27046 | 0.4041 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 1 | 1 | 1 | 351 | 378 | 464 | 151 | 163 | 200 | 0.094835 | 0.11024 | 0.16496 | 1.2 | 7 | 7.7 | 10.7 |  | 2957 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 351 | 378 | 464 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3016 | 3387.5609 | 3627.3291 | 5000.36 | N/A | 1 | 1 | 1 | #VALUE! | 1864 | 1996 | 2752 | #VALUE! | 321 | 343 | 473 | #VALUE! | 0.59751 | 0.68059 | 1.28 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 351.533 | 376.4142 | 518.896 | 1 | 1 | 1 | 396 | 424 | 584 | 170 | 182 | 251 | 0.17183 | 0.19638 | 0.36872 | 2.4 | 7 | 7.7 | 10.7 |  | 3770 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 396 | 424 | 584 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1355.4 | 1766.3894 | 1902.9713 | 2335.88 | N/A | 1 | 1 | 1 | #VALUE! | 972 | 1047 | 1286 | #VALUE! | 167 | 180 | 221 | #VALUE! | 0.14257 | 0.16466 | 0.24438 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 1 | 1 | 1 | 276 | 297 | 365 | 119 | 128 | 157 | 0.074406 | 0.085567 | 0.12662 | 0.6 | 8.4 | 9.3 | 14 |  | 1506 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 365 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2396.6961 | 2582.015 | 3169.4 | N/A | 1 | 1 | 1 | #VALUE! | 1319 | 1421 | 1744 | #VALUE! | 227 | 244 | 300 | #VALUE! | 0.43364 | 0.49787 | 0.73949 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 321.1364 | 345.9675 | 424.672 | 1 | 1 | 1 | 362 | 390 | 478 | 156 | 168 | 206 | 0.2119 | 0.24406 | 0.3602 | 1.2 | 8.4 | 9.3 | 14 |  | 1934 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 362 | 390 | 478 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1813.1502 | 1908.1502 | 2043.2072 | 2816.61 | N/A | 1 | 1 | 1 | #VALUE! | 1050 | 1124 | 1550 | #VALUE! | 181 | 193 | 267 | #VALUE! | 0.17236 | 0.19549 | 0.36972 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1 | 1 | 1 | 281 | 301 | 415 | 121 | 129 | 178 | 0.078292 | 0.088747 | 0.1668 | 0.9 | 7.9 | 8.8 | 12.5 |  | 2332 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 281 | 301 | 415 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1942.08 | 2849.7498 | 3051.4523 | 4206.5 | N/A | 1 | 1 | 1 | #VALUE! | 1568 | 1679 | 2315 | #VALUE! | 270 | 289 | 398 | #VALUE! | 1.091 | 1.2479 | 2.3495 | 0.0002083 | 1.724 | 4 | 0.0013928 | 326.2664 | 349.3592 | 481.6 | 1 | 1 | 1 | 367 | 393 | 542 | 158 | 169 | 233 | 0.37885 | 0.43263 | 0.81545 | 1.8 | 7.9 | 8.8 | 12.5 |  | 2856 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 367 | 393 | 542 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2597.5513 | 2692.5513 | 2900.7465 | 3560.64 | N/A | 1 | 1 | 1 | #VALUE! | 1482 | 1596 | 1960 | #VALUE! | 255 | 275 | 337 | #VALUE! | 0.26632 | 0.3091 | 0.46171 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 1 | 1 | 1 | 357 | 385 | 472 | 154 | 166 | 203 | 0.09858 | 0.11428 | 0.16987 | 1.2 | 7.9 | 8.8 | 12.5 |  | 3253 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 385 | 472 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3317.6 | 3556.1815 | 3807.8846 | 5249.26 | N/A | 1 | 1 | 1 | #VALUE! | 1957 | 2096 | 2889 | #VALUE! | 337 | 361 | 497 | #VALUE! | 0.6574 | 0.75252 | 1.4109 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 356.5192 | 381.7533 | 526.256 | 1 | 1 | 1 | 402 | 430 | 593 | 173 | 185 | 255 | 0.17782 | 0.20277 | 0.38033 | 2.4 | 7.9 | 8.8 | 12.5 |  | 4147 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 402 | 430 | 593 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1478.7 | 1924.9914 | 2079.6202 | 2589.78 | N/A | 1 | 1 | 1 | #VALUE! | 1059 | 1144 | 1425 | #VALUE! | 182 | 197 | 245 | #VALUE! | 0.1682 | 0.19587 | 0.29807 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 1 | 1 | 1 | 301 | 325 | 404 | 129 | 140 | 174 | 0.086853 | 0.10162 | 0.15427 | 0.6 | 8.9 | 9.9 | 14.8 |  | 1643 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 301 | 325 | 404 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2611.8926 | 2821.6982 | 3513.9 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.50965 | 0.59155 | 0.90329 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 349.6 | 378.4 | 471.2 | 1 | 1 | 1 | 394 | 426 | 531 | 169 | 183 | 228 | 0.24684 | 0.28732 | 0.4373 | 1.2 | 8.9 | 9.9 | 14.8 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 394 | 426 | 531 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 2216.9074 | 2373.9949 | 3302.76 | N/A | 1 | 1 | 1 | #VALUE! | 1220 | 1307 | 1818 | #VALUE! | 210 | 225 | 313 | #VALUE! | 0.23071 | 0.26417 | 0.50531 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1 | 1 | 1 | 341 | 365 | 508 | 147 | 157 | 218 | 0.11462 | 0.1304 | 0.24828 | 0.9 | 8.7 | 9.8 | 14.3 |  | 2544 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 508 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2118.2 | 3241.8334 | 3471.546 | 4829.7 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.4062 | 1.6124 | 3.0885 | 0.0002083 | 1.724 | 4 | 0.0013928 | 396.8 | 425.6 | 592 | 1 | 1 | 1 | 447 | 479 | 667 | 192 | 206 | 287 | 0.55649 | 0.63943 | 1.2309 | 1.8 | 8.7 | 9.8 | 14.3 |  | 3115 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 447 | 479 | 667 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2838.4 | 3079.683 | 3327.0648 | 4143.24 | N/A | 1 | 1 | 1 | #VALUE! | 1695 | 1831 | 2280 | #VALUE! | 292 | 315 | 392 | #VALUE! | 0.34794 | 0.4041 | 0.62235 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 1 | 1 | 1 | 429 | 463 | 577 | 184 | 199 | 248 | 0.13997 | 0.16334 | 0.2521 | 1.2 | 8.7 | 9.8 | 14.3 |  | 3548 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 429 | 463 | 577 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3619.2 | 4175.0158 | 4470.8527 | 6219.96 | N/A | 1 | 1 | 1 | #VALUE! | 2298 | 2460 | 3423 | #VALUE! | 395 | 423 | 589 | #VALUE! | 0.89811 | 1.0275 | 1.9708 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 433.2486 | 463.9481 | 645.456 | 1 | 1 | 1 | 488 | 522 | 727 | 210 | 224 | 313 | 0.25992 | 0.29497 | 0.56863 | 2.4 | 8.7 | 9.8 | 14.3 |  | 4524 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 488 | 522 | 727 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1725.3 | 2267.7915 | 2456.1428 | 3097.58 | N/A | 1 | 1 | 1 | #VALUE! | 1248 | 1352 | 1705 | #VALUE! | 215 | 233 | 293 | #VALUE! | 0.23177 | 0.27058 | 0.42087 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 1 | 1 | 1 | 354 | 383 | 484 | 152 | 165 | 208 | 0.11899 | 0.13931 | 0.21746 | 0.6 | 10.1 | 11.2 | 17.5 |  | 1917 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 354 | 383 | 484 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 3077.0153 | 3332.5766 | 4202.9 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.69757 | 0.81199 | 1.2719 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 412 | 446.4 | 563.2 | 1 | 1 | 1 | 464 | 503 | 634 | 200 | 216 | 273 | 0.34043 | 0.39436 | 0.61726 | 1.2 | 10.1 | 11.2 | 17.5 |  | 2461 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 634 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 2628.9846 | 2815.4585 | 3950.36 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1549 | 2174 | #VALUE! | 249 | 266 | 374 | #VALUE! | 0.32235 | 0.36701 | 0.71723 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1 | 1 | 1 | 404 | 433 | 607 | 174 | 186 | 261 | 0.15953 | 0.18182 | 0.35357 | 0.9 | 9.6 | 10.5 | 16.1 |  | 2968 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 404 | 433 | 607 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2471.12 | 3844.4231 | 4117.108 | 5776.7 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.9691 | 2.257 | 4.4082 | 0.0002083 | 1.724 | 4 | 0.0013928 | 471.2 | 504 | 708 | 1 | 1 | 1 | 531 | 568 | 797 | 228 | 244 | 343 | 0.78126 | 0.89323 | 1.7508 | 1.8 | 9.6 | 10.5 | 16.1 |  | 3634 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 531 | 568 | 797 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3312 | 3628.1092 | 3929.4416 | 4955.64 | N/A | 1 | 1 | 1 | #VALUE! | 1997 | 2163 | 2727 | #VALUE! | 343 | 372 | 469 | #VALUE! | 0.47809 | 0.56119 | 0.88701 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 1 | 1 | 1 | 505 | 547 | 690 | 217 | 235 | 297 | 0.19374 | 0.2267 | 0.3598 | 1.2 | 9.6 | 10.5 | 16.1 |  | 4140 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 505 | 547 | 690 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4222.4 | 4951.0649 | 5302.2439 | 7439.56 | N/A | 1 | 1 | 1 | #VALUE! | 2725 | 2918 | 4094 | #VALUE! | 469 | 502 | 704 | #VALUE! | 1.2588 | 1.4389 | 2.8001 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 513.7806 | 550.223 | 772.016 | 1 | 1 | 1 | 579 | 620 | 869 | 249 | 267 | 374 | 0.36298 | 0.41624 | 0.80669 | 2.4 | 9.6 | 10.5 | 16.1 |  | 5278 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 579 | 620 | 869 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1971 | 2603.9362 | 2826.6988 | 3605.38 | N/A | 1 | 1 | 1 | #VALUE! | 1433 | 1556 | 1984 | #VALUE! | 246 | 268 | 341 | #VALUE! | 0.30042 | 0.35435 | 0.56408 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 1 | 1 | 1 | 407 | 441 | 563 | 175 | 190 | 242 | 0.15598 | 0.18271 | 0.29108 | 0.6 | 11 | 12.4 | 19.2 |  | 2190 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 407 | 441 | 563 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1912.84 | 3533.1076 | 3835.3593 | 4891.9 | N/A | 1 | 1 | 1 | #VALUE! | 1944 | 2111 | 2692 | #VALUE! | 334 | 363 | 463 | #VALUE! | 0.9085 | 1.0659 | 1.701 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 473.6 | 513.6 | 655.2 | 1 | 1 | 1 | 533 | 578 | 738 | 229 | 249 | 317 | 0.44097 | 0.51757 | 0.8219 | 1.2 | 11 | 12.4 | 19.2 |  | 2813 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 533 | 578 | 738 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 3021.1784 | 3225.612 | 4597.96 | N/A | 1 | 1 | 1 | #VALUE! | 1663 | 1775 | 2530 | #VALUE! | 286 | 305 | 435 | #VALUE! | 0.4232 | 0.48023 | 0.96562 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1 | 1 | 1 | 464 | 496 | 707 | 200 | 213 | 304 | 0.20964 | 0.23722 | 0.47714 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3392 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 464 | 496 | 707 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2824.72 | 4417.9369 | 4716.8848 | 6723.7 | N/A | 1 | 1 | 1 | #VALUE! | 2431 | 2596 | 3700 | #VALUE! | 418 | 447 | 636 | #VALUE! | 2.5888 | 2.9562 | 5.9415 | 0.0002083 | 1.724 | 4 | 0.0013928 | 540.8 | 577.6 | 824 | 1 | 1 | 1 | 609 | 650 | 928 | 262 | 280 | 399 | 1.0281 | 1.1723 | 2.3612 | 1.8 | 11.5 | 12.8 | 19.6 |  | 4154 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 609 | 650 | 928 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3784.8 | 4165.8877 | 4522.2728 | 5768.04 | N/A | 1 | 1 | 1 | #VALUE! | 2293 | 2489 | 3174 | #VALUE! | 394 | 428 | 546 | #VALUE! | 0.62864 | 0.74032 | 1.198 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 1 | 1 | 1 | 580 | 629 | 803 | 249 | 270 | 345 | 0.2541 | 0.29811 | 0.48361 | 1.2 | 11.5 | 12.8 | 19.6 |  | 4731 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 580 | 629 | 803 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4825.6 | 5689.6682 | 6074.6702 | 8659.16 | N/A | 1 | 1 | 1 | #VALUE! | 3131 | 3343 | 4765 | #VALUE! | 539 | 575 | 820 | #VALUE! | 1.655 | 1.8796 | 3.7818 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 590.4267 | 630.379 | 898.576 | 1 | 1 | 1 | 665 | 710 | 1012 | 286 | 305 | 435 | 0.47635 | 0.54044 | 1.0856 | 2.4 | 11.5 | 12.8 | 19.6 |  | 6032 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 665 | 710 | 1012 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2217.6 | 2970.6878 | 3224.8254 | 4113.18 | N/A | 1 | 1 | 1 | #VALUE! | 1635 | 1775 | 2264 | #VALUE! | 281 | 305 | 389 | #VALUE! | 0.38825 | 0.45476 | 0.72756 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 1 | 1 | 1 | 464 | 503 | 642 | 200 | 216 | 276 | 0.20165 | 0.23385 | 0.37503 | 0.6 | 12.2 | 13.7 | 22 |  | 2464 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 464 | 503 | 642 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46 | 2151.52 | 4030.7284 | 4375.5508 | 5580.9 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 1.1755 | 1.3719 | 2.1901 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 540.0825 | 586.2857 | 747.792 | 1 | 1 | 1 | 608 | 660 | 842 | 261 | 284 | 362 | 0.56636 | 0.66578 | 1.0602 | 1.2 | 12.2 | 13.7 | 22 |  | 3164 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 608 | 660 | 842 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 3233.3461 | 3452.1364 | 4920.86 | N/A | 1 | 1 | 1 | #VALUE! | 1779 | 1900 | 2708 | #VALUE! | 306 | 327 | 466 | #VALUE! | 0.48334 | 0.55072 | 1.1058 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1 | 1 | 1 | 474 | 506 | 721 | 204 | 218 | 310 | 0.21795 | 0.24828 | 0.49584 | 0.9 | 11.5 | 12.8 | 19.6 |  | 3816 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 474 | 506 | 721 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 3177.64 | 4843.455 | 5171.1964 | 7371.3 | N/A | 1 | 1 | 1 | #VALUE! | 2666 | 2846 | 4057 | #VALUE! | 459 | 490 | 698 | #VALUE! | 3.1153 | 3.5454 | 7.1436 | 0.0002083 | 1.724 | 4 | 0.0013928 | 549.0471 | 586.1994 | 835.6 | 1 | 1 | 1 | 618 | 660 | 941 | 266 | 284 | 405 | 1.0593 | 1.2056 | 2.4319 | 1.8 | 11.5 | 12.8 | 19.6 |  | 4673 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 618 | 660 | 941 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 4258.4 | 4497.8275 | 4882.6095 | 6227.64 | N/A | 1 | 1 | 1 | #VALUE! | 2475 | 2687 | 3427 | #VALUE! | 426 | 462 | 589 | #VALUE! | 0.7335 | 0.86104 | 1.3917 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 1 | 1 | 1 | 592 | 643 | 820 | 255 | 276 | 353 | 0.26632 | 0.31132 | 0.506 | 1.2 | 11.5 | 12.8 | 19.6 |  | 5323 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 592 | 643 | 820 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 5428.8 | 6016.7573 | 6423.8924 | 9156.96 | N/A | 1 | 1 | 1 | #VALUE! | 3311 | 3535 | 5039 | #VALUE! | 569 | 608 | 867 | #VALUE! | 1.8412 | 2.0979 | 4.221 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 600.0988 | 640.7056 | 913.296 | 1 | 1 | 1 | 676 | 722 | 1029 | 291 | 310 | 442 | 0.49283 | 0.55798 | 1.1202 | 2.4 | 11.5 | 12.8 | 19.6 |  | 6786 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1029 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2464.2 | 3259.5786 | 3552.8678 | 4620.98 | N/A | 1 | 1 | 1 | #VALUE! | 1794 | 1955 | 2543 | #VALUE! | 309 | 336 | 437 | #VALUE! | 0.46635 | 0.54822 | 0.91117 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 1 | 1 | 1 | 509 | 555 | 721 | 219 | 239 | 310 | 0.24014 | 0.28416 | 0.46926 | 0.6 | 13.4 | 14.8 | 24 |  | 2738 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 509 | 555 | 721 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2390.88 | 4422.7051 | 4820.6497 | 6269.9 | N/A | 1 | 1 | 1 | #VALUE! | 2434 | 2653 | 3451 | #VALUE! | 419 | 456 | 594 | #VALUE! | 1.404 | 1.6519 | 2.7477 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592.8 | 645.6 | 840 | 1 | 1 | 1 | 668 | 727 | 946 | 287 | 313 | 407 | 0.67931 | 0.80213 | 1.3277 | 1.2 | 13.4 | 14.8 | 24 |  | 3516 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 668 | 727 | 946 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3392 | 3875.4624 | 4083.4736 | 5893.16 | N/A | 1 | 1 | 1 | #VALUE! | 2133 | 2247 | 3243 | #VALUE! | 367 | 386 | 558 | #VALUE! | 0.69105 | 0.76321 | 1.577 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1 | 1 | 1 | 596 | 628 | 906 | 256 | 270 | 390 | 0.34039 | 0.37793 | 0.77885 | 0.9 | 13.2 | 14.7 | 23.5 |  | 4240 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 596 | 628 | 906 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3530.56 | 5667.1756 | 5971.3549 | 8617.7 | N/A | 1 | 1 | 1 | #VALUE! | 3119 | 3286 | 4743 | #VALUE! | 536 | 565 | 816 | #VALUE! | 4.2344 | 4.7 | 9.7346 | 0.0002083 | 1.724 | 4 | 0.0013928 | 694.4 | 731.2 | 1056 | 1 | 1 | 1 | 782 | 823 | 1189 | 336 | 354 | 511 | 1.6809 | 1.8636 | 3.8524 | 1.8 | 13.2 | 14.7 | 23.5 |  | 5192 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 782 | 823 | 1189 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4731.2 | 5214.8122 | 5684.0287 | 7392.84 | N/A | 1 | 1 | 1 | #VALUE! | 2870 | 3128 | 4069 | #VALUE! | 494 | 538 | 700 | #VALUE! | 0.9829 | 1.1635 | 1.9583 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 1 | 1 | 1 | 726 | 791 | 1029 | 312 | 340 | 442 | 0.39654 | 0.46986 | 0.78893 | 1.2 | 13.2 | 14.7 | 23.5 |  | 5914 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 726 | 791 | 1029 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 6032 | 7298.5083 | 7690.2476 | 11098.36 | N/A | 1 | 1 | 1 | #VALUE! | 4017 | 4232 | 6108 | #VALUE! | 691 | 728 | 1051 | #VALUE! | 2.6992 | 2.9913 | 6.1696 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 757.3788 | 798.0303 | 1151.696 | 1 | 1 | 1 | 853 | 899 | 1297 | 367 | 387 | 558 | 0.77729 | 0.86271 | 1.7718 | 2.4 | 13.2 | 14.7 | 23.5 |  | 7540 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 853 | 899 | 1297 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2710.8 | 3560.7045 | 3890.5075 | 5128.78 | N/A | 1 | 1 | 1 | #VALUE! | 1960 | 2141 | 2823 | #VALUE! | 337 | 368 | 486 | #VALUE! | 0.55137 | 0.65355 | 1.1193 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 1 | 1 | 1 | 556 | 607 | 801 | 239 | 261 | 344 | 0.28416 | 0.33672 | 0.57371 | 0.6 | 13.4 | 14.8 | 24 |  | 3012 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 556 | 607 | 801 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2630.24 | 4831.2828 | 5278.7706 | 6958.9 | N/A | 1 | 1 | 1 | #VALUE! | 2659 | 2905 | 3830 | #VALUE! | 457 | 500 | 659 | #VALUE! | 1.6589 | 1.9721 | 3.3564 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 647.3498 | 707.3093 | 932.432 | 1 | 1 | 1 | 729 | 797 | 1050 | 313 | 343 | 452 | 0.80213 | 0.95604 | 1.6242 | 1.2 | 13.4 | 14.8 | 24 |  | 3868 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 729 | 797 | 1050 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 4302.5567 | 4481.7989 | 6540.76 | N/A | 1 | 1 | 1 | #VALUE! | 2368 | 2467 | 3600 | #VALUE! | 407 | 424 | 619 | #VALUE! | 0.84708 | 0.91814 | 1.9348 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1 | 1 | 1 | 661 | 689 | 1006 | 284 | 296 | 433 | 0.4174 | 0.45277 | 0.9569 | 0.9 | 15.5 | 16.8 | 27.5 |  | 4664 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 661 | 689 | 1006 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3883.48 | 6291.7252 | 6553.835 | 9564.7 | N/A | 1 | 1 | 1 | #VALUE! | 3463 | 3607 | 5264 | #VALUE! | 596 | 620 | 905 | #VALUE! | 5.2243 | 5.6492 | 11.9515 | 0.0002083 | 1.724 | 4 | 0.0013928 | 770.6865 | 802.7929 | 1171.6 | 1 | 1 | 1 | 868 | 904 | 1319 | 373 | 389 | 567 | 2.0666 | 2.2456 | 4.733 | 1.8 | 15.5 | 16.8 | 27.5 |  | 5711 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 868 | 904 | 1319 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5204 | 5696.5662 | 6224.1991 | 8205.24 | N/A | 1 | 1 | 1 | #VALUE! | 3135 | 3425 | 4516 | #VALUE! | 539 | 589 | 777 | #VALUE! | 1.1678 | 1.3917 | 2.4076 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 1 | 1 | 1 | 793 | 866 | 1142 | 341 | 372 | 491 | 0.4726 | 0.56119 | 0.97114 | 1.2 | 15.5 | 16.8 | 27.5 |  | 6505 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 793 | 866 | 1142 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6635.2 | 8102.8385 | 8440.3982 | 12317.96 | N/A | 1 | 1 | 1 | #VALUE! | 4459 | 4645 | 6779 | #VALUE! | 767 | 799 | 1166 | #VALUE! | 3.3152 | 3.5933 | 7.5725 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 840.8456 | 875.8747 | 1278.256 | 1 | 1 | 1 | 947 | 986 | 1440 | 407 | 424 | 619 | 0.95253 | 1.0323 | 2.1733 | 2.4 | 15.5 | 16.8 | 27.5 |  | 8294 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 947 | 986 | 1440 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2957.4 | 3860.4189 | 4228.9856 | 5636.58 | N/A | 1 | 1 | 1 | #VALUE! | 2125 | 2327 | 3102 | #VALUE! | 366 | 400 | 534 | #VALUE! | 0.64671 | 0.76786 | 1.3433 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 1 | 1 | 1 | 603 | 660 | 880 | 259 | 284 | 378 | 0.33177 | 0.39628 | 0.68831 | 0.6 | 14.8 | 16.6 | 28 |  | 3286 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 603 | 660 | 880 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2868.92 | 5237.9453 | 5738.0289 | 7647.9 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.9419 | 2.3115 | 4.024 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 701.6 | 768.8 | 1024.8 | 1 | 1 | 1 | 790 | 866 | 1154 | 340 | 372 | 496 | 0.94006 | 1.1172 | 1.9419 | 1.2 | 14.8 | 16.6 | 28 |  | 4219 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 790 | 866 | 1154 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 4729.7153 | 4901.7743 | 7188.36 | N/A | 1 | 1 | 1 | #VALUE! | 2603 | 2698 | 3956 | #VALUE! | 448 | 464 | 680 | #VALUE! | 1.0233 | 1.0965 | 2.3287 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1 | 1 | 1 | 727 | 754 | 1105 | 313 | 324 | 475 | 0.50531 | 0.54083 | 1.1482 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5088 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 727 | 754 | 1105 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4236.4 | 6916.3687 | 7167.9745 | 10511.7 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 6.2982 | 6.7635 | 14.4226 | 0.0002083 | 1.724 | 4 | 0.0013928 | 847.2 | 878.4 | 1288 | 1 | 1 | 1 | 954 | 989 | 1451 | 410 | 425 | 624 | 2.4917 | 2.6752 | 5.7216 | 1.8 | 16.4 | 17.7 | 29.7 |  | 6230 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 954 | 989 | 1451 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5677.6 | 6176.062 | 6765.7107 | 9017.64 | N/A | 1 | 1 | 1 | #VALUE! | 3399 | 3723 | 4963 | #VALUE! | 585 | 640 | 854 | #VALUE! | 1.3731 | 1.6402 | 2.9028 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 1 | 1 | 1 | 860 | 942 | 1255 | 370 | 405 | 540 | 0.55525 | 0.66378 | 1.1721 | 1.2 | 16.4 | 17.7 | 29.7 |  | 7097 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 860 | 942 | 1255 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7238.4 | 8907.2896 | 9231.3218 | 13537.56 | N/A | 1 | 1 | 1 | #VALUE! | 4902 | 5080 | 7450 | #VALUE! | 843 | 874 | 1281 | #VALUE! | 3.9938 | 4.2885 | 9.1174 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 924.3248 | 957.9502 | 1404.816 | 1 | 1 | 1 | 1041 | 1079 | 1582 | 448 | 464 | 680 | 1.1503 | 1.2325 | 2.6152 | 2.4 | 16.4 | 17.7 | 29.7 |  | 9048 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1041 | 1079 | 1582 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3203.1 | 4178.1784 | 4608.285 | 6144.38 | N/A | 1 | 1 | 1 | #VALUE! | 2299 | 2536 | 3381 | #VALUE! | 395 | 436 | 582 | #VALUE! | 0.74941 | 0.90714 | 1.5871 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 1 | 1 | 1 | 652 | 719 | 959 | 280 | 309 | 412 | 0.38559 | 0.46635 | 0.81304 | 0.6 | 16.2 | 18.6 | 31.4 |  | 3559 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 652 | 719 | 959 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3108.28 | 5669.092 | 6252.675 | 8336.9 | N/A | 1 | 1 | 1 | #VALUE! | 3120 | 3441 | 4588 | #VALUE! | 537 | 592 | 789 | #VALUE! | 2.2625 | 2.7299 | 4.7503 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 759.609 | 837.804 | 1117.072 | 1 | 1 | 1 | 855 | 944 | 1258 | 368 | 406 | 541 | 1.0942 | 1.3215 | 2.2951 | 1.2 | 16.2 | 18.6 | 31.4 |  | 4571 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 855 | 944 | 1258 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 4942.1733 | 5121.9619 | 7511.26 | N/A | 1 | 1 | 1 | #VALUE! | 2720 | 2819 | 4134 | #VALUE! | 468 | 485 | 711 | #VALUE! | 1.1152 | 1.1963 | 2.5427 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1 | 1 | 1 | 736 | 763 | 1119 | 316 | 328 | 481 | 0.51488 | 0.55403 | 1.177 | 0.9 | 16.4 | 17.7 | 29.7 |  | 5512 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 736 | 763 | 1119 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4590 | 7342.4692 | 7609.5768 | 11159.3 | N/A | 1 | 1 | 1 | #VALUE! | 4041 | 4188 | 6141 | #VALUE! | 695 | 720 | 1056 | #VALUE! | 7.0829 | 7.5965 | 16.2286 | 0.0002083 | 1.724 | 4 | 0.0013928 | 855.096 | 886.2031 | 1299.6 | 1 | 1 | 1 | 963 | 998 | 1464 | 414 | 429 | 630 | 2.54 | 2.7253 | 5.831 | 1.8 | 16.4 | 17.7 | 29.7 |  | 6750 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 963 | 998 | 1464 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 6150.4 | 6444.5232 | 7107.93 | 9477.24 | N/A | 1 | 1 | 1 | #VALUE! | 3547 | 3912 | 5216 | #VALUE! | 610 | 673 | 897 | #VALUE! | 1.4916 | 1.8117 | 3.1993 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 1 | 1 | 1 | 865 | 954 | 1273 | 372 | 410 | 547 | 0.56119 | 0.68007 | 1.2023 | 1.2 | 16.4 | 17.7 | 29.7 |  | 7688 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 865 | 954 | 1273 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7841.6 | 9234.8264 | 9570.7751 | 14035.36 | N/A | 1 | 1 | 1 | #VALUE! | 5082 | 5267 | 7724 | #VALUE! | 874 | 906 | 1329 | #VALUE! | 4.2885 | 4.6036 | 9.8042 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 934.0101 | 967.988 | 1419.536 | 1 | 1 | 1 | 1052 | 1090 | 1599 | 452 | 469 | 688 | 1.1706 | 1.2588 | 2.6761 | 2.4 | 16.4 | 17.7 | 29.7 |  | 9802 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1052 | 1090 | 1599 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3449.7 | 4331.3824 | 4782.2249 | 6369.68 | N/A | 1 | 1 | 1 | #VALUE! | 2384 | 2632 | 3505 | #VALUE! | 410 | 453 | 603 | #VALUE! | 0.80542 | 0.97683 | 1.7 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 1 | 1 | 1 | 662 | 731 | 973 | 285 | 314 | 418 | 0.39898 | 0.48102 | 0.83609 | 0.6 | 16.2 | 18.6 | 31.4 |  | 3833 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 662 | 731 | 973 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3346.96 | 5976.86 | 6598.9761 | 8789.5 | N/A | 1 | 1 | 1 | #VALUE! | 3289 | 3632 | 4837 | #VALUE! | 566 | 625 | 832 | #VALUE! | 2.5037 | 3.0306 | 5.2627 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 764.8 | 844.8 | 1124.8 | 1 | 1 | 1 | 861 | 951 | 1267 | 370 | 409 | 545 | 1.1057 | 1.3403 | 2.3279 | 1.2 | 16.2 | 18.6 | 31.4 |  | 4922 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 861 | 951 | 1267 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 5583.9636 | 5708.9475 | 8483.56 | N/A | 1 | 1 | 1 | #VALUE! | 3073 | 3142 | 4669 | #VALUE! | 529 | 540 | 803 | #VALUE! | 1.4195 | 1.4783 | 3.2325 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1 | 1 | 1 | 858 | 878 | 1304 | 369 | 378 | 561 | 0.69848 | 0.7324 | 1.5937 | 0.9 | 19.3 | 20.4 | 34.5 |  | 5936 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 858 | 878 | 1304 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4942.92 | 8165.5551 | 8348.322 | 12405.7 | N/A | 1 | 1 | 1 | #VALUE! | 4494 | 4594 | 6827 | #VALUE! | 773 | 790 | 1174 | #VALUE! | 8.7444 | 9.1295 | 20.0221 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1000 | 1022.4 | 1520 | 1 | 1 | 1 | 1126 | 1151 | 1712 | 484 | 495 | 736 | 3.46 | 3.6173 | 7.9346 | 1.8 | 19.3 | 20.4 | 34.5 |  | 7269 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1126 | 1151 | 1712 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6624 | 7236.8592 | 7990.1254 | 10642.44 | N/A | 1 | 1 | 1 | #VALUE! | 3983 | 4397 | 5857 | #VALUE! | 685 | 756 | 1007 | #VALUE! | 1.8762 | 2.2805 | 4.0229 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 1 | 1 | 1 | 1007 | 1112 | 1481 | 433 | 478 | 637 | 0.75751 | 0.92097 | 1.625 | 1.2 | 19.3 | 20.4 | 34.5 |  | 8280 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1007 | 1112 | 1481 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 8444.8 | 10516.0623 | 10751.4398 | 15976.76 | N/A | 1 | 1 | 1 | #VALUE! | 5787 | 5917 | 8793 | #VALUE! | 995 | 1018 | 1512 | #VALUE! | 5.538 | 5.7933 | 12.6488 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1009.4247 | 1032.0183 | 1533.5908 | 1 | 1 | 1 | 1137 | 1162 | 1727 | 489 | 500 | 743 | 1.3665 | 1.4277 | 3.1139 | 2.4 | 19.3 | 20.4 | 34.5 |  | 10556 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1137 | 1162 | 1727 |  | 0 | 0 | 0 | 1
39010 |  |  | 3 | 90 | 40.5 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3696.3 | 4485 | 4951 | 6595 | N/A | 1 | 1 | 1 | #VALUE! | 2468 | 2725 | 3629 | #VALUE! | 425 | 469 | 624 | #VALUE! | 0.86339 | 1.0447 | 1.8167 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 1 | 1 | 1 | 670 | 741 | 988 | 288 | 319 | 425 | 0.40712 | 0.49592 | 0.86339 | 0.6 | 16.2 | 18.6 | 31.4 |  | 4107 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 670 | 741 | 988 |  | 0 | 0 | 0 | 1
39011 |  |  | 3 | 90 | 40.5 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3586.32 | 6285 | 6939 | 9242 | N/A | 1 | 1 | 1 | #VALUE! | 3459 | 3819 | 5086 | #VALUE! | 595 | 657 | 875 | #VALUE! | 2.7566 | 3.3368 | 5.8007 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 770.4 | 850.4 | 1132.8 | 1 | 1 | 1 | 868 | 958 | 1276 | 373 | 412 | 549 | 1.1229 | 1.3592 | 2.3609 | 1.2 | 16.2 | 18.6 | 31.4 |  | 5274 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 868 | 958 | 1276 |  | 0 | 0 | 0 | 1
39015 |  |  | 3 | 90 | 40.5 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 5088 | 5796 | 5926 | 8806 | N/A | 1 | 1 | 1 | #VALUE! | 3190 | 3261 | 4846 | #VALUE! | 549 | 561 | 834 | #VALUE! | 1.5272 | 1.5937 | 3.4834 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1 | 1 | 1 | 868 | 887 | 1319 | 373 | 381 | 567 | 0.71346 | 0.74388 | 1.6275 | 0.9 | 19.3 | 20.4 | 34.5 |  | 6360 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 868 | 887 | 1319 |  | 0 | 0 | 0 | 1
39016 |  |  | 3 | 90 | 40.5 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 5295.84 | 8592 | 8784 | 13053 | N/A | 1 | 1 | 1 | #VALUE! | 4729 | 4834 | 7184 | #VALUE! | 813 | 831 | 1236 | #VALUE! | 9.6638 | 10.0924 | 22.1738 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1008 | 1030.4 | 1532 | 1 | 1 | 1 | 1135 | 1160 | 1725 | 488 | 499 | 742 | 3.5168 | 3.6754 | 8.0632 | 1.8 | 19.3 | 20.4 | 34.5 |  | 7788 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1135 | 1160 | 1725 |  | 0 | 0 | 0 | 1
39020 |  |  | 3 | 90 | 40.5 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 7096.8 | 7549 | 8335 | 11102 | N/A | 1 | 1 | 1 | #VALUE! | 4155 | 4587 | 6110 | #VALUE! | 715 | 789 | 1051 | #VALUE! | 2.0422 | 2.4817 | 4.3785 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 1 | 1 | 1 | 1019 | 1125 | 1499 | 438 | 484 | 645 | 0.77489 | 0.94396 | 1.6656 | 1.2 | 19.3 | 20.4 | 34.5 |  | 8871 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1019 | 1125 | 1499 |  | 0 | 0 | 0 | 1
39021 |  |  | 3 | 90 | 40.5 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 9048 | 10844 | 11086 | 16475 | N/A | 1 | 1 | 1 | #VALUE! | 5968 | 6101 | 9067 | #VALUE! | 1027 | 1049 | 1560 | #VALUE! | 5.8948 | 6.1465 | 13.4543 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1174.4 | 1200.8 | 1784.8 | 1 | 1 | 1 | 1323 | 1352 | 2010 | 569 | 581 | 864 | 1.8412 | 1.9184 | 4.1923 | 2.4 | 19.3 | 20.4 | 34.5 |  | 11310 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1323 | 1352 | 2010 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 41 | 1553 | 1648 | 1770 | 2136 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1176 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.15044 | 0.17417 | 0.25075 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 106.9244 | 125.0304 | 1 | 1 | 1 | 311 | 120 | 141 | 134 | 52 | 61 | 0.11141 | 0.017223 | 0.023586 | 0.4 | 0 | 0 | 0 |  | 99999 |  | 68% | [7 empty] | 1 | 1 | 1 | 311 | 120 | 141 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 |  | 1945 | 2040 | 2188 | 2936 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.51811 | 0.59578 | 1.073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 163.7931 | 175.2709 | 204.9504 | 1 | 1 | 1 | 184 | 197 | 231 | 79 | 85 | 99 | 0.087261 | 0.10097 | 0.13684 | 0.6 | 0 | 0 | 0 |  | 99999 |  | 68% | [7 empty] | 1 | 1 | 1 | 184 | 197 | 231 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 41.8 | 592.28 | 1648 | 1770 | 2136 | N/A | 1 | 1 | 1 | #VALUE! | 907 | 974 | 1176 | #VALUE! | 156 | 168 | 202 | #VALUE! | 0.15044 | 0.17417 | 0.25075 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 1 | 1 | 1 | 311 | 333 | 403 | 134 | 143 | 173 | 0.11141 | 0.12668 | 0.18457 | 0.4 | 6.3 | 6.8 | 9.1 |  | 871 |  | 68% | [7 empty] | 1 | 1 | 1 | 311 | 333 | 403 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 42.4 | 779.28 | 2040 | 2188 | 2936 | N/A | 1 | 1 | 1 | #VALUE! | 1123 | 1204 | 1616 | #VALUE! | 193 | 207 | 278 | #VALUE! | 0.51811 | 0.59578 | 1.073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 1 | 1 | 1 | 351 | 377 | 507 | 151 | 162 | 218 | 0.31756 | 0.36537 | 0.66061 | 0.6 | 6 | 6.7 | 9 |  | 1146 |  | 68% | [7 empty] | 1 | 1 | 1 | 351 | 377 | 507 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 43 | 740.52 | 2136 | 2301 | 2825 | N/A | 1 | 1 | 1 | #VALUE! | 1176 | 1266 | 1555 | #VALUE! | 202 | 218 | 267 | #VALUE! | 0.25075 | 0.29155 | 0.43546 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 1 | 1 | 1 | 403 | 434 | 533 | 173 | 187 | 229 | 0.18457 | 0.21527 | 0.32137 | 0.4 | 7.8 | 8.7 | 12.2 |  | 1089 |  | 68% | [7 empty] | 1 | 1 | 1 | 403 | 434 | 533 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 44.1 | 974.44 | 2630 | 2817 | 3883 | N/A | 1 | 1 | 1 | #VALUE! | 1447 | 1550 | 2137 | #VALUE! | 249 | 267 | 368 | #VALUE! | 0.86129 | 0.98999 | 1.8779 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 1 | 1 | 1 | 454 | 485 | 670 | 195 | 209 | 288 | 0.52887 | 0.60732 | 1.1514 | 0.6 | 7 | 7.7 | 10.7 |  | 1433 |  | 68% | [7 empty] | 1 | 1 | 1 | 454 | 485 | 670 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 44 | 888.76 | 2612 | 2822 | 3514 | N/A | 1 | 1 | 1 | #VALUE! | 1437 | 1553 | 1934 | #VALUE! | 247 | 267 | 333 | #VALUE! | 0.37327 | 0.43546 | 0.67431 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 1 | 1 | 1 | 492 | 533 | 663 | 212 | 229 | 285 | 0.2759 | 0.32137 | 0.49548 | 0.4 | 8.9 | 9.9 | 14.8 |  | 1307 |  | 68% | [7 empty] | 1 | 1 | 1 | 492 | 533 | 663 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 44.8 | 1169.6 | 3242 | 3472 | 4830 | N/A | 1 | 1 | 1 | #VALUE! | 1784 | 1911 | 2658 | #VALUE! | 307 | 329 | 457 | #VALUE! | 1.308 | 1.5017 | 2.8934 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 1 | 1 | 1 | 559 | 599 | 833 | 240 | 258 | 358 | 0.8003 | 0.92452 | 1.7774 | 0.6 | 8.7 | 9.8 | 14.3 |  | 1720 |  | 68% | [7 empty] | 1 | 1 | 1 | 559 | 599 | 833 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 44.8 | 1037 | 3077 | 3333 | 4203 | N/A | 1 | 1 | 1 | #VALUE! | 1693 | 1834 | 2313 | #VALUE! | 291 | 315 | 398 | #VALUE! | 0.51634 | 0.60405 | 0.95993 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 1 | 1 | 1 | 580 | 628 | 793 | 249 | 270 | 341 | 0.37928 | 0.44519 | 0.70677 | 0.4 | 10.1 | 11.2 | 17.5 |  | 1525 |  | 68% | [7 empty] | 1 | 1 | 1 | 580 | 628 | 793 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 45.4 | 1364.08 | 3844 | 4117 | 5777 | N/A | 1 | 1 | 1 | #VALUE! | 2116 | 2266 | 3179 | #VALUE! | 364 | 390 | 547 | #VALUE! | 1.8374 | 2.1086 | 4.1423 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 1 | 1 | 1 | 663 | 709 | 997 | 285 | 305 | 429 | 1.1276 | 1.291 | 2.5504 | 0.6 | 9.6 | 10.5 | 14.4 |  | 2006 |  | 68% | [7 empty] | 1 | 1 | 1 | 663 | 709 | 997 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 46 | 1332.8 | 4031 | 4376 | 5581 | N/A | 1 | 1 | 1 | #VALUE! | 2218 | 2408 | 3071 | #VALUE! | 382 | 414 | 528 | #VALUE! | 0.88499 | 1.0379 | 1.6807 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675 | 733 | 935 | 1 | 1 | 1 | 760 | 825 | 1053 | 327 | 355 | 453 | 0.65047 | 0.76539 | 1.2406 | 0.4 | 12.2 | 13.7 | 22 |  | 1960 |  | 68% | [7 empty] | 1 | 1 | 1 | 760 | 825 | 1053 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 46.4 | 1753.72 | 4843 | 5171 | 7371 | N/A | 1 | 1 | 1 | #VALUE! | 2665 | 2846 | 4057 | #VALUE! | 458 | 490 | 698 | #VALUE! | 2.9061 | 3.3255 | 6.7388 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686 | 733 | 1045 | 1 | 1 | 1 | 773 | 825 | 1177 | 332 | 355 | 506 | 1.5291 | 1.7478 | 3.5457 | 0.6 | 11.5 | 12.8 | 19.6 |  | 2579 |  | 68% | [7 empty] | 1 | 1 | 1 | 773 | 825 | 1177 |  | 0 | 0 | 0 | 1
52811 |  |  | 5 | 28 | 40.5 | 11 | 13 | 0 | 26 | 30 | 47.2 | 1777.52 | 5238 | 5738 | 7648 | N/A | 1 | 1 | 1 | #VALUE! | 2883 | 3158 | 4209 | #VALUE! | 496 | 543 | 724 | #VALUE! | 1.4848 | 1.7767 | 3.1433 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 1 | 1 | 1 | 988 | 1082 | 1443 | 425 | 465 | 620 | 1.0932 | 1.3066 | 2.311 | 0.4 | 14.8 | 16.6 | 28 |  | 2614 |  | 68% | [7 empty] | 1 | 1 | 1 | 988 | 1082 | 1443 |  | 0 | 0 | 0 | 1
52816 |  |  | 5 | 28 | 40.5 | 16 | 18 | 0 | 26 | 30 | 48.1 | 2338.52 | 6916 | 7168 | 10512 | N/A | 1 | 1 | 1 | #VALUE! | 3806 | 3945 | 5785 | #VALUE! | 655 | 679 | 995 | #VALUE! | 5.9355 | 6.3776 | 13.6768 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 1 | 1 | 1 | 1193 | 1237 | 1813 | 513 | 532 | 780 | 3.6443 | 3.9187 | 8.4118 | 0.6 | 16.4 | 17.7 | 29.7 |  | 3439 |  | 68% | [7 empty] | 1 | 1 | 1 | 1193 | 1237 | 1813 |  | 0 | 0 | 0 | 1
Note on D4: Thomas Henson: Strada = 1 Linea = 2 Tempo = 3 Built_in = 4
∆𝑝= 𝑘_1∗𝑞^𝑛∗((𝐿−144)∗𝑡)/1000+𝑘_2∗𝑞^2

## NL (hidden)
Selectiontool Strada Hybrid
| Lengte |  | mm | Invulformulier | Statisch toestel | rel. vocht. | Unit | Kopieer alle data
| Hoogte |  | mm | Uitvoering | Hybrid toestel | Eenheidsstelsel | DBH set | SI-eenheden
| Type |  |  | Temperaturen | DBH rail type | Toestel |  | Imperiale-eenheden
| Diepte |  | mm | Vermogen zonder ventilatoren is verwaarloosbaar. | Waterzijdig drukverlies
Afgifte zonder ventilatoren is verwaarloosbaar
| Verwarmen: |  |  |  |  | Koelen:
| Water aanvoer |  |  | Water aanvoer |  |  |  | 0
| Water retour |  | 0 | Water retour |  |  |  | 0
| Ruimte (droge bol) |  | 0 | Ruimte (droge bol) |  |  |  | 0
|  | Verwarmen: // |  | Koelen: // |  | Watervolume | Elektrisch verbruik [W] | Geluidsdrukniveau [dB(A)]**** | Geluidsvermogen [dB(A)]****
|  | Verwarmvermogen | Waterdebiet | Koelvermogen | Waterdebiet
Statisch (indicatieve waarde)
EN16430 | Ventilatorsnelheid
Ventilatorsnelheid 2
Ventilatorsnelheid 3
Stuurspanning [v]
* | Koelvermogen is berekend volgens EN16430 met de ventilatoren naar boven blazend voor alle types.
** | Wanneer het watervolume in gallons wordt gegeven, zijn dit imperial gallons.
*** | Geluidsvermogen volgens ISO 3741:2010, Voor het geluidsdrukniveau is er een aangenomen kamerdemping van 8 dB(A).

## EN (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | Output without fans is negligible | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## FR (hidden)
Selectiontool Strada Hybrid
| Longeur |  | mm | Formulaire | Appareil statique | hum. rel. | Unité | Copier toutes des données
| Hauteur |  | mm | Version | Appareil Hybrid | Système unitaire | DBH set | Unités-SI
| Type |  |  | Températures | DBH rail type | Appareil |  | Unités-Impériales
| Profondeur |  | mm | L’émission sans ventilateurs est négligeable | Perte de charge
| Chauffer: |  |  |  |  | Refroidir:
| Entrée de l'eau |  |  | Entrée de l'eau |  |  |  | 0
| Retour de l'eau |  | 0 | Retour de l'eau |  |  |  | 0
| Ambiante (bulbe sec) |  | 0 | Ambiante (bulbe sec) |  |  |  | 0
|  | Chauffer: // |  | Refroidir: // |  | Volume d'eau | Puissance absorbée elec. [W] | Pression sonore [dB(A)]**** | Puissance sonore [dB(A)]****
|  | Puissance de chauffer | Débit d'eau | Puissance de refroidir | Débit d'eau
Ventilateur éteint (indicative)
EN16430 | Vitesse ventilateur
Vitesse du ventilateur 2
Vitesse du ventilateur 3
Tension ventilateur [V]
* | La puissance de refroidissement est calculée selon EN 16430 avec des ventilateurs qui soufflent pour toutes les hauteurs.
** | Lorsque le volume d'eau est donné en gallons, ce sont des gallons impérial.
*** | Puissance acoustique selon ISO 3741: 2010, niveau de pression acoustique avec un amortissement de la pièce supposé de 8 dB(A).

## DE (hidden)
Selectiontool Strada Hybrid
| Länge |  | mm | Eingabefelder | Statisches Gerät | rel. Luftf. | Unit | Kopieren Sie alle daten
| Höhe |  | mm | Ausführung | Hybrid Gerät | Einheiten | DBH set | SI-einheiten
| Typ |  |  | Temperaturen | DBH rail typ | Gerät |  | Imperiale-einheiten
| Tiefe |  | mm | Die Ausgabe ohne Lüfter ist vernachlässigbar. | zug. wassers. Druckverlust
| Heizen: |  |  |  |  | Kühlen:
| Vorlauf wasser |  |  | Vorlauf wasser |  |  |  | 0
| Rücklauf wasser |  | 0 | Rücklauf wasser |  |  |  | 0
| Raum (trocken) |  | 0 | Raum (trocken) |  |  |  | 0
|  | Heizen: // |  | Kühlen: // |  | Wasservolumen | Elektr. Leistung [W] | Schalldruckpegel [dB(A)]**** | Schallleistungspegel [dB(A)]****
|  | Heizleistung | Heizmittelstrom | Kühlleistung | Kühlmittelstrom
Lüfter aus (richtwert)
EN16430 | Auslegungsstufe
Auslegungsstufe 2
Auslegungsstufe 3
Lufterspannung [V]
* | Die Kühlleistung wird nach EN 16430 berechnet, wobei die Lüfter für alle Höhen hochgehen.
** | Wenn das Wasservolumen in Gallonen angegeben ist, sind dies imperiale Gallonen.
*** | Schallleistung nach ISO 3741: 2010, Schalldruckpegel bei angenommener Raumdämpfung von 8 dB(A).

## NR (hidden)
Selectiontool Strada Hybrid
| Lengde |  | mm | Inngangsskjema | Statisk modell | rel. fuktighet | Unit | Kopier alle data
| Høyde |  | mm | Versjon | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Type |  |  | Temperaturer | DBH rail type | Modell |  | Imperiale-enheter
| Bredde |  | mm | Utgang uten vifter er neglisjerbar. | Trykktap
| Varme: |  |  |  |  | Kjøling:
| Tur vann |  |  | Tur vann |  |  |  | 0
| Retur vann |  | 0 | Retur vann |  |  |  | 0
| Rom (tørr pære) |  | 0 | Rom (tørr pære) |  |  |  | 0
|  | Varme: // |  | Kjøling: // |  | Vannvolum | Elektrisk effekt [W] | Lydtrykk [dB(A)]**** | Lydeffekt [dB(A)]****
|  | Varme effekt | Vannmengde | Kjøle effekt | Vannmengde
Lüfter aus (richtwert)
EN16430 | Styresignal
Auslegungsstufe 2
Auslegungsstufe 3
Viftespenning [V]
* | Kjølekapasitet beregnes i henhold til EN16430 med viftene som blåser oppover for alle typer.
** | Når vannvolumet er gitt i gallon, er dette imperial gallons.
*** | Lydeffekt i henhold til ISO 3741: 2010. For lydtrykknivået er det en antatt romdemping på 8 dB (A).

## SP (hidden)
Selectiontool Strada Hybrid
| Longitud |  | mm | Formulary | Dispositivo estático | Hum. Relativa | Unit | Copiar todos los datos
| Altura |  | mm | Versión | Dispositivo Hybrid | Convers. de unidades | DBH set | Unidades-SI
| Tipo |  |  | Temperaturas | tipo de riel DBH | Despositivo |  | Unidades-Imperial
| Profund. |  | mm | La salida sin ventiladores es insignificante. | Pérdida de carga del agua
| Calefacción: |  |  |  |  | Enfriamiento:
| Agua impulsión |  |  | Agua impulsión |  |  |  | 0
| Agua retorno |  | 0 | Agua retorno |  |  |  | 0
| Ambiente (bulbo seco) |  | 0 | Ambiente (bulbo seco) |  |  |  | 0
|  | Calefacción: // |  | Enfriamiento: // |  | Volumen de agua | Potencia eléctrica absorbida [W] | Presión sonora [dB(A)]**** | Potencia sonora [dB(A)]****
|  | Emisión calefacción | Caudal de agua, calefacción | Emisión sensible Frío | Caudal de agua, calefacción
Fans off (indicative value)
EN16430 | Velocidad del ventilador
Fan speed selection 2
Fan speed selection 3
Voltaje control [V]
* | La potencia de enfriamiento se calcula según la norma EN 16430 con ventiladores de todas las alturas.
** | Cuando el volumen de agua se da en galones, las unidades son específicamente galones imperiales.
*** | Potencia sonora según ISO 3741: 2010, nivel de presión acústica con una amortiguación ambiental supuesta de 8 dB (A).

## SW (hidden)
Selectiontool Strada Hybrid
| Längd |  | mm | Inngangsskjema | Statisk modell | rel. Fuktighet | Unit | Kopiera all data
| Höjd |  | mm | Storlek | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Typ |  |  | Temperaturer | DBH rail typ | Modell |  | Imperiella-enheter
| Djup |  | mm | Utgång utan fläktar är försumbar. | Tryckfall, vatten
| Värme: |  |  |  |  | Kyla:
| Tillopp |  |  | Tillopp |  |  |  | 0
| Retur |  | 0 | Retur |  |  |  | 0
| Rum (torr) |  | 0 | Rum (torr) |  |  |  | 0
|  | Värme: // |  | Kyla: // |  | Vattenvolym | Effektförbrukning [W] | Ljudtryck [dB(A)]**** | Ljudeffekt [dB(A)]****
|  | Effekt | Vattenflöde | Kyleffekt | Vattenflöde
Fans off (indicative value)
EN16430 | Fläkthastighet
Fan speed selection 2
Fan speed selection 3
Spänning, Fläkt [V]
* | Kyleffekt är beräknad enligt EN16430 med fläktar blåsandes i riktning uppåt för alla höjder
** | När vattenvolymen är given i gallon avser det Imperiella gallon.
*** | Ljudeffekt enligt ISO 3741:2010 ljudtryck med antagen ljudreduktion från rummet på 8 dB(A)

## TS (hidden)
Selectiontool Strada Hybrid
| Délka |  | mm | Formulary | Statická jednotka | Relativní vlhkost | Jednotka | Kopírovat všechna data
| Výška |  | mm | Verze | Hybridní jednotka | Převod jednotek | DBH sada | Mezinárodní (Sl)
| Typ |  |  | Teploty | DBH rail type | Device |  | Imperiální
| Hloubka |  | mm | Výstup bez ventilátorů je zanedbatelný. | Tlaková ztráta
| Topení: |  |  |  |  | Chlazení:
| Voda na přívodu |  |  | Voda na přívodu |  |  |  | 0
| Voda na zpátečce |  | 0 | Voda na zpátečce |  |  |  | 0
| "Suchá" teplota vzduchu |  | 0 | "Suchá" teplota vzduchu |  |  |  | 0
|  | Topení: // |  | Chlazení: // |  | Objem vody | Elektrický výkon [W] | Akustický tlak [dB(A)]**** | Akustický výkon [dB(A)]****
|  | Výkon Topení | Průtok vody | Výkon Chlazení | Průtok vody
Fans off (indicative value)
EN16430 | Rychlost otáček ventilátoru
Fan speed selection 2
Fan speed selection 3
Napětí ventilárotu [V]
* | Chladicí výkon vypočítán podle EN 16430 s ventilátory, které u všech typů - výšek foukají nahoru.
** | Když je objem vody uveden v galonech, jednotky jsou konkrétně imperiální galony.
*** | Akustický výkon podle ISO 3741: 2010, hladina akustického tlaku s předpokládaným útlumem místnosti o 8 dB (A).

## ExtraTaal1 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal2 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal3 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).